## File Description
A description of the spreadsheets of this file is provided below.
"Load P (MW)" and "Load Q (Mvar)" spreadsheets
Column A: refers to the network bus where the load is connected to.
Columns B to Y: contain the loads' power values for each hour of the day.
"Gen Status" spreadsheet
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the generators' status (as a result of the unit commitment exercise) for each hour of the day.
"Gen P (MW)" and "Gen Q (Mvar)" spreadsheets
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the generators' power quantities (as a result of the dispatch exercises) for each hour of the day. It is important to state that the reactive power limits of the generators were artificially reduced to only 75% of their physical limits within the reactive power dispatch exercise, in order to prevent them from reaching their reactive power limits – thus, generators will be able to provide voltage control through reactive power support.
"Gen Vg (pu)" spreadsheet
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the regulated voltage magnitude setpoint (in pu) for each hour of the day.
"Transf Tap Ratio" spreadsheet
Columns A and B: refer to the network buses where the transformer is connected to. It is worth mentioning that the transformers are presented in the same order as in the network file.
Columns C to Z: contain the transformers' winding 1 off-nominal turns ratio (in pu of winding 1 bus base voltage) for each hour of the day.
"Transf Data" spreadsheet
Columns A and B: refer to the network buses where the transformer is connected to. It is worth mentioning that the transformers are presented in the same order as in the network file.
Column C: contains the transformer's manufacture year.
Column D: contains the transformer's commissioning year.
Column E: contains the transformer's annual maximum loading (MVA). These values were indirectly estimated through power flow analyses, considering the peak and valley load of each season (in 2019).
Column F: contains the transformer's voltage ratio (kV).
Column G: contains the transformer's insulation medium.
Column H: contains the transformer's cooling system: ONAN (Oil Natural Air Natural), ONAF (Oil Natural Air Forced) and ODAF (Oil Directed Air Forced).
Column I: contains the transformer type.
Column J: contains the transformer's installation site (Indoor/Outdoor).
Column K: contains the transformer's criticallity indicator (the worst within the following), which was indirectly determined through a contingency analysis (N-1) for the 2019 winter peak scenario: A (very high) when the transformer loss leads to loss of load; B (high) when at least a transformer or line/cable gets overloaded due to the transformer loss; C (medium) when at least a transformer or line/cable exceeds 50% of its load rating; and D (low) for the remainder cases.
Column L: contains the percentage of time that the power transformer was over 50% of its rating in 2019. Such values were indirectly estimated through power flow analyses considering the peak and valley load of each season.
Column M: contains the mean loading (MVA) of each transformer directly connected to the distribution network (400/220/150 kV to 63 kV), since the number of potential customers affected by its loss is very difficult to obtain. The mean loading was indirectly estimated through power flow analyses considering the peak and valley load of each season (in 2019).
Column N: contains the undelivered energy on the 2019 winter peak scenario due to the transformer loss. These values were indirectly determined through a contingency analysis (N-1).
Column O: contains the mean loading (%) of each transformer in 2019. Such values were indirectly estimated through power flow analyses considering the peak and valley load of each season.
Column P: contains an indicative range for the value of lost load (k€/MWh).
"Lines_Cables Data" spreadsheet
Columns A and B: refer to the network buses where the line/cable is connected to. It is worth mentioning that the lines/cables are presented in the same order as in the network file.
Column C: contains the length (in km) of the line/cable.
Column D: contains the type of installation (overhead, underground or submarine) of the line/cable.
Columns E to H: contain the line/cable's ratings for summer, spring, autumn and winter, respectively.
Column I: contains the conductor cross-sectional area (mm2) of the line/cable. For the majority of overhead lines only its "designation" (e.g., Bear, Zebra...) is publicly available.
Column J: contains the line/cable's rated voltage (kV).
Column K: contains the line/cable's conductor material.
Column L: contains the line/cable's criticallity indicator, which is similar to the power transformer case (see line 33 above).
Column M: contains the percentage of time that the line/cable was over 50% of its rating in 2019. This is similar to the power transformer case (see line 34 above).
Column N: contains the number of potential customers affected by the line/cable loss, for customers directly connected to the transmission network. In other cases, no information is provided since it is very difficult to obtain. The shown values were indirectly determined through a contingency analysis (N-1) for the 2019 winter peak scenario.
Column O: contains the undelivered energy on the 2019 winter peak scenario due to the line/cable loss. This is similar to the power transformer case (see line 36 above).
Column P: contains the mean loading (%) of each line/cable in 2019. This is similar to the power transformer case (see line 37 above).
Column Q: contains an indicative range for the value of lost load (k€/MWh).
"Auxiliary Data" spreadsheet
Column A : refers to the type of distribution network (urban, semi-urban, rural).
Columns B to Y: contain the typical percentages of downward and upward flexible load for each type of distribution network and for each hour of the day.
"Downward Flexibility" spreadsheet
Column A : refers to the network bus where the load is connected to.
Columns B to Y: contain the downward flexible load values for each hour of the day.
"Upward Flexibility" spreadsheet
Column A : refers to the network bus where the load is connected to.
Columns B to Y: contain the upward flexible load values for each hour of the day.

## Load P (MW)
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 3.042 | 3.213 | 3.295 | 3.387 | 3.33 | 3.323 | 3.426 | 3.477 | 3.479 | 3.422 | 3.345 | 3.363 | 3.308 | 3.354 | 0.393 | 0.361
13 | 0.797 | 0.76 | 0.737 | 0.722 | 0.714 | 0.717 | 0.729 | 0.809 | 5.476 | 5.784 | 5.931 | 6.096 | 5.994 | 5.982 | 6.166 | 6.259 | 6.262 | 6.159 | 6.021 | 6.053 | 5.955 | 6.037 | 0.983 | 0.904
26 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 3.042 | 3.213 | 3.295 | 3.387 | 3.33 | 3.323 | 3.426 | 3.477 | 3.479 | 3.422 | 3.345 | 3.363 | 3.308 | 3.354 | 0.393 | 0.361
27 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 3.042 | 3.213 | 3.295 | 3.387 | 3.33 | 3.323 | 3.426 | 3.477 | 3.479 | 3.422 | 3.345 | 3.363 | 3.308 | 3.354 | 0.393 | 0.361
28 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 2.173 | 2.295 | 2.354 | 2.419 | 2.378 | 2.374 | 2.447 | 2.484 | 2.485 | 2.444 | 2.389 | 2.402 | 2.363 | 2.395 | 0.393 | 0.361
67 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 1.739 | 1.836 | 1.883 | 1.935 | 1.903 | 1.899 | 1.957 | 1.987 | 1.988 | 1.955 | 1.911 | 1.922 | 1.89 | 1.916 | 0.393 | 0.361
108 | 26.779 | 25.541 | 24.753 | 24.257 | 23.99 | 24.083 | 24.486 | 27.166 | 31.815 | 33.601 | 34.456 | 35.414 | 34.821 | 34.752 | 35.822 | 36.364 | 36.377 | 35.783 | 34.977 | 35.166 | 34.594 | 35.07 | 33.028 | 30.363
109 | 161.952 | 154.465 | 149.698 | 146.696 | 145.084 | 145.644 | 148.082 | 164.288 | 175.676 | 185.539 | 190.261 | 195.553 | 192.278 | 191.894 | 197.801 | 200.796 | 200.869 | 197.589 | 193.137 | 194.18 | 191.022 | 193.652 | 199.741 | 183.626
110 | 117.798 | 112.352 | 108.885 | 106.701 | 105.529 | 105.936 | 107.71 | 119.497 | 138.82 | 146.614 | 150.345 | 154.527 | 151.938 | 151.635 | 156.303 | 158.669 | 158.727 | 156.135 | 152.617 | 153.442 | 150.946 | 153.024 | 145.284 | 133.562
111 | 84.323 | 80.425 | 77.943 | 76.38 | 75.541 | 75.832 | 77.102 | 85.54 | 101.79 | 107.504 | 110.24 | 113.307 | 111.409 | 111.187 | 114.609 | 116.344 | 116.387 | 114.486 | 111.907 | 112.511 | 110.681 | 112.205 | 103.999 | 95.608
112 | 225.394 | 214.973 | 208.34 | 204.161 | 201.918 | 202.697 | 206.091 | 228.645 | 210.012 | 221.802 | 227.447 | 233.773 | 229.858 | 229.4 | 236.461 | 240.041 | 240.128 | 236.207 | 230.885 | 232.132 | 228.356 | 231.501 | 277.985 | 255.558
113 | 100.264 | 95.628 | 92.677 | 90.819 | 89.821 | 90.167 | 91.677 | 101.71 | 79.971 | 84.461 | 86.611 | 89.02 | 87.529 | 87.354 | 90.043 | 91.406 | 91.439 | 89.946 | 87.92 | 88.395 | 86.957 | 88.154 | 123.658 | 113.682
114 | 124.652 | 118.889 | 115.22 | 112.91 | 111.669 | 112.1 | 113.977 | 126.45 | 136.647 | 144.318 | 147.991 | 152.108 | 149.56 | 149.262 | 153.856 | 156.186 | 156.242 | 153.691 | 150.228 | 151.04 | 148.583 | 150.629 | 153.737 | 141.334
115 | 18.331 | 17.484 | 16.944 | 16.604 | 16.422 | 16.485 | 16.761 | 18.596 | 19.732 | 20.84 | 21.37 | 21.965 | 21.597 | 21.554 | 22.217 | 22.554 | 22.562 | 22.193 | 21.693 | 21.81 | 21.456 | 21.751 | 22.608 | 20.784
116 | 208.816 | 199.162 | 193.016 | 189.145 | 187.067 | 187.789 | 190.933 | 211.828 | 228.005 | 240.806 | 246.935 | 253.803 | 249.552 | 249.054 | 256.721 | 260.607 | 260.702 | 256.445 | 250.667 | 252.021 | 247.922 | 251.335 | 257.539 | 236.761
117 | 42.72 | 40.745 | 39.487 | 38.695 | 38.27 | 38.418 | 39.061 | 43.336 | 47.027 | 49.667 | 50.931 | 52.347 | 51.471 | 51.368 | 52.949 | 53.751 | 53.77 | 52.892 | 51.701 | 51.98 | 51.134 | 51.839 | 52.687 | 48.437
118 | 71.89 | 68.567 | 66.451 | 65.118 | 64.402 | 64.651 | 65.733 | 72.927 | 76.755 | 81.064 | 83.127 | 85.44 | 84.009 | 83.841 | 86.422 | 87.73 | 87.762 | 86.329 | 84.384 | 84.84 | 83.46 | 84.609 | 88.664 | 81.511
119 | 135.491 | 129.227 | 125.239 | 122.728 | 121.379 | 121.848 | 123.888 | 137.446 | 155.336 | 164.057 | 168.232 | 172.911 | 170.015 | 169.676 | 174.899 | 177.547 | 177.611 | 174.711 | 170.775 | 171.697 | 168.904 | 171.23 | 167.106 | 153.624
120 | 185.543 | 176.965 | 171.504 | 168.065 | 166.218 | 166.86 | 169.654 | 188.22 | 203.232 | 214.642 | 220.104 | 226.226 | 222.437 | 221.993 | 228.827 | 232.291 | 232.376 | 228.581 | 223.431 | 224.638 | 220.984 | 224.027 | 228.837 | 210.374
121 | 127.202 | 121.322 | 117.578 | 115.22 | 113.954 | 114.394 | 116.309 | 129.037 | 138.298 | 146.063 | 149.78 | 153.946 | 151.368 | 151.066 | 155.716 | 158.073 | 158.131 | 155.549 | 152.044 | 152.865 | 150.379 | 152.449 | 156.883 | 144.226
122 | 165.618 | 157.961 | 153.087 | 150.017 | 148.368 | 148.941 | 151.435 | 168.007 | 176.024 | 185.906 | 190.638 | 195.94 | 192.658 | 192.274 | 198.193 | 201.193 | 201.266 | 197.98 | 193.519 | 194.564 | 191.4 | 194.035 | 204.262 | 187.783
123 | 99.467 | 94.868 | 91.941 | 90.097 | 89.107 | 89.451 | 90.948 | 100.901 | 113.525 | 119.898 | 122.95 | 126.369 | 124.253 | 124.005 | 127.822 | 129.757 | 129.804 | 127.685 | 124.808 | 125.482 | 123.441 | 125.141 | 122.675 | 112.778
124 | 85.28 | 81.337 | 78.827 | 77.246 | 76.398 | 76.692 | 77.977 | 86.51 | 95.183 | 100.527 | 103.086 | 105.953 | 104.178 | 103.97 | 107.171 | 108.793 | 108.833 | 107.056 | 104.644 | 105.209 | 103.498 | 104.923 | 105.178 | 96.693
125 | 89.743 | 85.594 | 82.953 | 81.289 | 80.396 | 80.706 | 82.058 | 91.037 | 107.614 | 113.655 | 116.548 | 119.79 | 117.783 | 117.548 | 121.167 | 123.001 | 123.046 | 121.037 | 118.31 | 118.948 | 117.014 | 118.625 | 110.683 | 101.753
126 | 92.453 | 88.179 | 85.458 | 83.744 | 82.823 | 83.143 | 84.535 | 93.786 | 80.058 | 84.553 | 86.705 | 89.116 | 87.624 | 87.449 | 90.141 | 91.506 | 91.539 | 90.044 | 88.015 | 88.491 | 87.051 | 88.25 | 114.025 | 104.826
127 | 66.311 | 63.245 | 61.294 | 60.064 | 59.404 | 59.634 | 60.632 | 67.267 | 79.102 | 83.543 | 85.669 | 88.052 | 86.577 | 86.405 | 89.064 | 90.413 | 90.446 | 88.969 | 86.964 | 87.434 | 86.012 | 87.196 | 81.784 | 75.185
128 | 159.88 | 152.488 | 147.783 | 144.819 | 143.227 | 143.78 | 146.188 | 162.186 | 227.831 | 240.623 | 246.746 | 253.609 | 249.362 | 248.864 | 256.525 | 260.409 | 260.503 | 256.25 | 250.476 | 251.829 | 247.733 | 251.144 | 197.185 | 181.276
129 | 142.664 | 136.069 | 131.87 | 129.225 | 127.805 | 128.299 | 130.447 | 144.722 | 178.197 | 188.202 | 192.991 | 198.359 | 195.037 | 194.648 | 200.64 | 203.677 | 203.751 | 200.424 | 195.908 | 196.966 | 193.763 | 196.431 | 175.953 | 161.757
130 | 157.967 | 150.664 | 146.015 | 143.086 | 141.514 | 142.06 | 144.439 | 160.245 | 197.581 | 208.674 | 213.985 | 219.937 | 216.253 | 215.822 | 222.465 | 225.833 | 225.915 | 222.226 | 217.219 | 218.392 | 214.84 | 217.798 | 194.826 | 179.107
131 | 126.087 | 120.257 | 116.546 | 114.209 | 112.954 | 113.39 | 115.289 | 127.905 | 121.782 | 128.62 | 131.893 | 135.561 | 133.291 | 133.025 | 137.12 | 139.196 | 139.246 | 136.973 | 133.887 | 134.61 | 132.42 | 134.244 | 155.507 | 142.961
132 | 20.563 | 19.612 | 19.007 | 18.626 | 18.421 | 18.492 | 18.802 | 20.859 | 57.805 | 61.051 | 62.604 | 64.346 | 63.268 | 63.142 | 65.086 | 66.071 | 66.095 | 65.016 | 63.551 | 63.894 | 62.855 | 63.72 | 25.361 | 23.315
133 | 122.739 | 117.065 | 113.452 | 111.177 | 109.955 | 110.38 | 112.228 | 124.51 | 140.037 | 147.899 | 151.663 | 155.881 | 153.27 | 152.965 | 157.673 | 160.06 | 160.118 | 157.504 | 153.955 | 154.787 | 152.269 | 154.366 | 151.378 | 139.165
134 | 106.799 | 101.862 | 98.718 | 96.738 | 95.675 | 96.045 | 97.653 | 108.339 | 124.912 | 131.925 | 135.282 | 139.045 | 136.716 | 136.443 | 140.643 | 142.773 | 142.825 | 140.492 | 137.327 | 138.069 | 135.823 | 137.693 | 131.719 | 121.092
135 | 115.566 | 110.223 | 106.822 | 104.68 | 103.529 | 103.929 | 105.669 | 117.233 | 139.254 | 147.073 | 150.816 | 155.01 | 152.414 | 152.11 | 156.793 | 159.166 | 159.224 | 156.624 | 153.095 | 153.922 | 151.418 | 153.503 | 142.531 | 131.032
136 | 131.028 | 124.97 | 121.114 | 118.685 | 117.381 | 117.834 | 119.807 | 132.918 | 159.421 | 168.372 | 172.657 | 177.459 | 174.487 | 174.139 | 179.499 | 182.217 | 182.283 | 179.306 | 175.266 | 176.213 | 173.347 | 175.733 | 161.601 | 148.563
137 | 82.889 | 79.057 | 76.617 | 75.081 | 74.256 | 74.542 | 75.79 | 84.084 | 111.004 | 117.236 | 120.219 | 123.563 | 121.494 | 121.251 | 124.984 | 126.876 | 126.922 | 124.85 | 122.037 | 122.696 | 120.7 | 122.362 | 102.229 | 93.982
138 | 72.05 | 68.719 | 66.598 | 65.262 | 64.545 | 64.794 | 65.879 | 73.089 | 103.963 | 109.8 | 112.594 | 115.726 | 113.787 | 113.56 | 117.056 | 118.828 | 118.871 | 116.93 | 114.296 | 114.913 | 113.044 | 114.6 | 88.861 | 81.692
139 | 124.971 | 119.193 | 115.515 | 113.198 | 111.954 | 112.387 | 114.268 | 126.773 | 175.242 | 185.08 | 189.79 | 195.069 | 191.802 | 191.419 | 197.312 | 200.299 | 200.372 | 197.1 | 192.659 | 193.7 | 190.549 | 193.173 | 154.13 | 141.695
140 | 55.153 | 52.603 | 50.98 | 49.957 | 49.408 | 49.599 | 50.43 | 55.948 | 60.761 | 64.172 | 65.805 | 67.636 | 66.503 | 66.37 | 68.413 | 69.449 | 69.474 | 68.34 | 66.8 | 67.161 | 66.068 | 66.978 | 68.022 | 62.534
141 | 62.167 | 59.293 | 57.463 | 56.31 | 55.692 | 55.907 | 56.843 | 63.063 | 71.192 | 75.189 | 77.102 | 79.247 | 77.92 | 77.764 | 80.158 | 81.372 | 81.401 | 80.072 | 78.268 | 78.69 | 77.411 | 78.476 | 76.672 | 70.486
142 | 74.6 | 71.151 | 68.955 | 67.573 | 66.83 | 67.088 | 68.211 | 75.676 | 96.661 | 102.088 | 104.686 | 107.598 | 105.796 | 105.585 | 108.835 | 110.482 | 110.523 | 108.718 | 106.268 | 106.842 | 105.104 | 106.552 | 92.006 | 84.583
143 | 52.124 | 49.715 | 48.18 | 47.214 | 46.695 | 46.876 | 47.66 | 52.876 | 66.498 | 70.231 | 72.019 | 74.022 | 72.782 | 72.637 | 74.873 | 76.006 | 76.034 | 74.792 | 73.107 | 73.502 | 72.307 | 73.302 | 64.287 | 59.1
144 | 40.807 | 38.92 | 37.719 | 36.963 | 36.557 | 36.698 | 37.312 | 41.395 | 53.111 | 56.093 | 57.521 | 59.121 | 58.13 | 58.015 | 59.8 | 60.706 | 60.728 | 59.736 | 58.39 | 58.706 | 57.751 | 58.546 | 50.328 | 46.268
145 | 158.286 | 150.968 | 146.309 | 143.375 | 141.8 | 142.347 | 144.73 | 160.569 | 140.993 | 148.909 | 152.698 | 156.946 | 154.317 | 154.009 | 158.75 | 161.153 | 161.212 | 158.579 | 155.007 | 155.844 | 153.309 | 155.42 | 195.219 | 179.469
146 | 6.535 | 6.233 | 6.041 | 5.92 | 5.855 | 5.877 | 5.976 | 6.63 | 8.258 | 8.722 | 8.943 | 9.192 | 9.038 | 9.02 | 9.298 | 9.439 | 9.442 | 9.288 | 9.079 | 9.128 | 8.979 | 9.103 | 8.06 | 7.41
147 | 37.938 | 36.184 | 35.067 | 34.364 | 33.986 | 34.117 | 34.689 | 38.485 | 48.331 | 51.044 | 52.343 | 53.799 | 52.898 | 52.792 | 54.417 | 55.241 | 55.261 | 54.359 | 53.134 | 53.421 | 52.552 | 53.276 | 46.79 | 43.015
149 | 130.709 | 124.666 | 120.819 | 118.396 | 117.095 | 117.547 | 119.515 | 132.595 | 148.903 | 157.263 | 161.265 | 165.751 | 162.975 | 162.65 | 167.656 | 170.195 | 170.256 | 167.476 | 163.703 | 164.587 | 161.91 | 164.139 | 161.208 | 148.202
150 | 30.605 | 29.19 | 28.289 | 27.722 | 27.417 | 27.523 | 27.984 | 31.047 | 28.425 | 30.02 | 30.784 | 31.641 | 31.111 | 31.049 | 32.004 | 32.489 | 32.501 | 31.97 | 31.25 | 31.419 | 30.908 | 31.333 | 37.746 | 34.701
151 | 119.232 | 113.72 | 110.211 | 108.001 | 106.814 | 107.226 | 109.021 | 120.952 | 157.77 | 166.627 | 170.868 | 175.62 | 172.679 | 172.335 | 177.639 | 180.329 | 180.394 | 177.449 | 173.451 | 174.387 | 171.551 | 173.913 | 147.053 | 135.189
152 | 43.198 | 41.201 | 39.929 | 39.129 | 38.699 | 38.848 | 39.498 | 43.821 | 52.677 | 55.634 | 57.05 | 58.637 | 57.655 | 57.54 | 59.311 | 60.209 | 60.231 | 59.247 | 57.912 | 58.225 | 57.278 | 58.067 | 53.277 | 48.979
153 | 6.376 | 6.081 | 5.894 | 5.775 | 5.712 | 5.734 | 5.83 | 6.468 | 6.954 | 7.344 | 7.531 | 7.741 | 7.611 | 7.596 | 7.83 | 7.948 | 7.951 | 7.821 | 7.645 | 7.686 | 7.561 | 7.666 | 7.864 | 7.229
154 | 71.093 | 67.806 | 65.714 | 64.396 | 63.688 | 63.934 | 65.005 | 72.119 | 75.017 | 79.228 | 81.245 | 83.504 | 82.106 | 81.942 | 84.464 | 85.743 | 85.774 | 84.374 | 82.473 | 82.918 | 81.569 | 82.692 | 87.681 | 80.607
155 | 30.924 | 29.494 | 28.584 | 28.011 | 27.703 | 27.81 | 28.276 | 31.37 | 33.205 | 35.07 | 35.962 | 36.963 | 36.343 | 36.271 | 37.387 | 37.954 | 37.967 | 37.347 | 36.506 | 36.703 | 36.106 | 36.603 | 38.139 | 35.062
156 | 14.824 | 14.139 | 13.703 | 13.428 | 13.28 | 13.332 | 13.555 | 15.038 | 18.515 | 19.555 | 20.052 | 20.61 | 20.265 | 20.224 | 20.847 | 21.163 | 21.17 | 20.825 | 20.355 | 20.465 | 20.132 | 20.41 | 18.283 | 16.808
157 | 70.455 | 67.198 | 65.125 | 63.818 | 63.117 | 63.361 | 64.422 | 71.472 | 84.839 | 89.602 | 91.883 | 94.438 | 92.857 | 92.671 | 95.524 | 96.97 | 97.005 | 95.421 | 93.272 | 93.775 | 92.25 | 93.52 | 86.895 | 79.884
158 | 60.573 | 57.772 | 55.989 | 54.867 | 54.264 | 54.473 | 55.385 | 61.446 | 70.41 | 74.363 | 76.255 | 78.376 | 77.063 | 76.91 | 79.277 | 80.477 | 80.507 | 79.192 | 77.408 | 77.826 | 76.56 | 77.614 | 74.706 | 68.679
159 | 72.368 | 69.023 | 66.893 | 65.551 | 64.831 | 65.081 | 66.171 | 73.412 | 81.797 | 86.389 | 88.588 | 91.052 | 89.527 | 89.348 | 92.098 | 93.493 | 93.527 | 92 | 89.927 | 90.412 | 88.942 | 90.166 | 89.254 | 82.053
160 | 58.66 | 55.948 | 54.221 | 53.134 | 52.55 | 52.753 | 53.636 | 59.506 | 76.234 | 80.514 | 82.563 | 84.859 | 83.438 | 83.271 | 85.835 | 87.134 | 87.166 | 85.742 | 83.811 | 84.263 | 82.893 | 84.034 | 72.347 | 66.51
161 | 10.68 | 10.186 | 9.872 | 9.674 | 9.568 | 9.604 | 9.765 | 10.834 | 13.387 | 14.138 | 14.498 | 14.901 | 14.652 | 14.622 | 15.072 | 15.301 | 15.306 | 15.056 | 14.717 | 14.796 | 14.556 | 14.756 | 13.172 | 12.109
162 | 47.661 | 45.458 | 44.055 | 43.171 | 42.697 | 42.862 | 43.579 | 48.349 | 53.372 | 56.369 | 57.803 | 59.411 | 58.416 | 58.299 | 60.094 | 61.004 | 61.026 | 60.029 | 58.677 | 58.994 | 58.034 | 58.833 | 58.782 | 54.039
163 | 10.361 | 9.882 | 9.577 | 9.385 | 9.282 | 9.318 | 9.474 | 10.511 | 17.994 | 19.004 | 19.487 | 20.029 | 19.694 | 19.655 | 20.26 | 20.566 | 20.574 | 20.238 | 19.782 | 19.889 | 19.565 | 19.835 | 12.779 | 11.748
164 | 57.544 | 54.884 | 53.19 | 52.123 | 51.55 | 51.749 | 52.616 | 58.374 | 48.07 | 50.769 | 52.061 | 53.509 | 52.612 | 52.507 | 54.124 | 54.943 | 54.963 | 54.066 | 52.847 | 53.133 | 52.269 | 52.988 | 70.971 | 65.245
165 | 22.635 | 21.589 | 20.922 | 20.503 | 20.277 | 20.356 | 20.697 | 22.962 | 26.251 | 27.725 | 28.431 | 29.222 | 28.732 | 28.675 | 29.558 | 30.005 | 30.016 | 29.526 | 28.861 | 29.016 | 28.545 | 28.938 | 27.916 | 25.664
166 | 59.457 | 56.708 | 54.958 | 53.856 | 53.264 | 53.47 | 54.365 | 60.314 | 69.54 | 73.445 | 75.314 | 77.408 | 76.112 | 75.96 | 78.298 | 79.484 | 79.513 | 78.214 | 76.452 | 76.865 | 75.615 | 76.656 | 73.33 | 67.414
167 | 19.925 | 19.004 | 18.418 | 18.048 | 17.85 | 17.919 | 18.219 | 20.213 | 18.863 | 19.922 | 20.429 | 20.997 | 20.645 | 20.604 | 21.238 | 21.56 | 21.568 | 21.216 | 20.738 | 20.85 | 20.51 | 20.793 | 24.574 | 22.592
168 | 81.454 | 77.688 | 75.291 | 73.781 | 72.97 | 73.252 | 74.479 | 82.629 | 101.268 | 106.954 | 109.676 | 112.726 | 110.838 | 110.617 | 114.022 | 115.748 | 115.79 | 113.9 | 111.333 | 111.935 | 110.114 | 111.63 | 100.46 | 92.355
169 | 15.94 | 15.203 | 14.734 | 14.439 | 14.28 | 14.335 | 14.575 | 16.17 | 29.555 | 31.214 | 32.008 | 32.899 | 32.348 | 32.283 | 33.277 | 33.781 | 33.793 | 33.241 | 32.492 | 32.668 | 32.136 | 32.579 | 19.659 | 18.073
170 | 16.737 | 15.963 | 15.471 | 15.16 | 14.994 | 15.052 | 15.304 | 16.979 | 20.949 | 22.125 | 22.688 | 23.319 | 22.929 | 22.883 | 23.587 | 23.944 | 23.953 | 23.562 | 23.031 | 23.156 | 22.779 | 23.093 | 20.642 | 18.977
171 | 37.619 | 35.88 | 34.772 | 34.075 | 33.701 | 33.831 | 34.397 | 38.161 | 45.723 | 48.29 | 49.519 | 50.896 | 50.044 | 49.944 | 51.481 | 52.261 | 52.28 | 51.426 | 50.267 | 50.539 | 49.717 | 50.401 | 46.396 | 42.653
172 | 18.331 | 17.484 | 16.944 | 16.604 | 16.422 | 16.485 | 16.761 | 18.596 | 20.949 | 22.125 | 22.688 | 23.319 | 22.929 | 22.883 | 23.587 | 23.944 | 23.953 | 23.562 | 23.031 | 23.156 | 22.779 | 23.093 | 22.608 | 20.784
245 | 7.97 | 7.602 | 7.367 | 7.219 | 7.14 | 7.168 | 7.288 | 8.085 | 26.078 | 27.542 | 28.243 | 29.028 | 28.542 | 28.485 | 29.362 | 29.806 | 29.817 | 29.33 | 28.67 | 28.824 | 28.356 | 28.746 | 9.83 | 9.037
246 | 3.985 | 3.801 | 3.684 | 3.61 | 3.57 | 3.584 | 3.644 | 4.043 | 16.516 | 17.443 | 17.887 | 18.384 | 18.077 | 18.041 | 18.596 | 18.877 | 18.884 | 18.576 | 18.157 | 18.255 | 17.958 | 18.206 | 4.915 | 4.518
247 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 3.042 | 3.213 | 3.295 | 3.387 | 3.33 | 3.323 | 3.426 | 3.477 | 3.479 | 3.422 | 3.345 | 3.363 | 3.308 | 3.354 | 0.393 | 0.361
248 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 1.739 | 1.836 | 1.883 | 1.935 | 1.903 | 1.899 | 1.957 | 1.987 | 1.988 | 1.955 | 1.911 | 1.922 | 1.89 | 1.916 | 0.393 | 0.361
249 | 2.391 | 2.28 | 2.21 | 2.166 | 2.142 | 2.15 | 2.186 | 2.426 | 5.216 | 5.508 | 5.649 | 5.806 | 5.708 | 5.697 | 5.872 | 5.961 | 5.963 | 5.866 | 5.734 | 5.765 | 5.671 | 5.749 | 2.949 | 2.711
250 | 1.594 | 1.52 | 1.473 | 1.444 | 1.428 | 1.434 | 1.458 | 1.617 | 10.17 | 10.741 | 11.015 | 11.321 | 11.131 | 11.109 | 11.451 | 11.625 | 11.629 | 11.439 | 11.181 | 11.241 | 11.059 | 11.211 | 1.966 | 1.807
255 | 25.504 | 24.325 | 23.574 | 23.102 | 22.848 | 22.936 | 23.32 | 25.872 | 22.601 | 23.869 | 24.477 | 25.158 | 24.736 | 24.687 | 25.447 | 25.832 | 25.842 | 25.42 | 24.847 | 24.981 | 24.575 | 24.913 | 31.455 | 28.917
256 | 78.737 | 78.725 | 78.748 | 78.759 | 78.805 | 78.758 | 78.693 | 78.234 | 73.887 | 78.035 | 80.021 | 82.246 | 80.869 | 80.708 | 83.192 | 84.452 | 84.482 | 83.103 | 81.23 | 81.669 | 80.341 | 81.447 | 78.62 | 78.524
257 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 2.608 | 2.754 | 2.824 | 2.903 | 2.854 | 2.849 | 2.936 | 2.981 | 2.982 | 2.933 | 2.867 | 2.882 | 2.836 | 2.875 | 0.393 | 0.361
258 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 2.173 | 2.295 | 2.354 | 2.419 | 2.378 | 2.374 | 2.447 | 2.484 | 2.485 | 2.444 | 2.389 | 2.402 | 2.363 | 2.395 | 0.393 | 0.361
259 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 2.173 | 2.295 | 2.354 | 2.419 | 2.378 | 2.374 | 2.447 | 2.484 | 2.485 | 2.444 | 2.389 | 2.402 | 2.363 | 2.395 | 0.393 | 0.361
260 | 86.312 | 86.299 | 86.324 | 86.336 | 86.386 | 86.334 | 86.263 | 85.761 | 91.272 | 96.396 | 98.849 | 101.599 | 99.897 | 99.698 | 102.767 | 104.322 | 104.36 | 102.656 | 100.343 | 100.885 | 99.244 | 100.611 | 86.183 | 86.078
261 | 0.319 | 0.304 | 0.295 | 0.289 | 0.286 | 0.287 | 0.292 | 0.323 | 0.869 | 0.918 | 0.941 | 0.968 | 0.951 | 0.95 | 0.979 | 0.994 | 0.994 | 0.978 | 0.956 | 0.961 | 0.945 | 0.958 | 0.393 | 0.361

## Load Q (Mvar)
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.176 | 0.186 | 0.192 | 0.197 | 0.194 | 0.194 | 0.2 | 0.203 | 0.202 | 0.198 | 0.193 | 0.193 | 0.189 | 0.192 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.229 | 1.304 | 1.341 | 1.381 | 1.36 | 1.358 | 1.399 | 1.418 | 1.415 | 1.388 | 1.351 | 1.35 | 1.324 | 1.341 | 0 | 0
26 | -0.159 | -0.152 | -0.147 | -0.144 | -0.143 | -0.143 | -0.146 | -0.162 | 0.176 | 0.186 | 0.192 | 0.197 | 0.194 | 0.194 | 0.2 | 0.203 | 0.202 | 0.198 | 0.193 | 0.193 | 0.189 | 0.192 | -0.197 | -0.181
27 | -0.159 | -0.152 | -0.147 | -0.144 | -0.143 | -0.143 | -0.146 | -0.162 | 0.088 | 0.093 | 0.096 | 0.099 | 0.097 | 0.097 | 0.1 | 0.101 | 0.101 | 0.099 | 0.096 | 0.096 | 0.095 | 0.096 | -0.197 | -0.181
28 | -0.638 | -0.608 | -0.589 | -0.578 | -0.571 | -0.573 | -0.583 | -0.649 | -0.351 | -0.372 | -0.383 | -0.395 | -0.389 | -0.388 | -0.4 | -0.405 | -0.404 | -0.397 | -0.386 | -0.386 | -0.378 | -0.383 | -0.786 | -0.723
67 | -0.159 | -0.152 | -0.147 | -0.144 | -0.143 | -0.143 | -0.146 | -0.162 | -0.614 | -0.652 | -0.671 | -0.691 | -0.68 | -0.679 | -0.699 | -0.709 | -0.708 | -0.694 | -0.675 | -0.675 | -0.662 | -0.671 | -0.197 | -0.181
108 | 10.202 | 9.73 | 9.43 | 9.241 | 9.139 | 9.174 | 9.331 | 10.388 | 11.674 | 12.385 | 12.742 | 13.121 | 12.923 | 12.903 | 13.287 | 13.469 | 13.446 | 13.189 | 12.833 | 12.829 | 12.578 | 12.744 | 12.582 | 11.567
109 | 43.995 | 41.961 | 40.666 | 39.85 | 39.413 | 39.565 | 40.238 | 44.797 | 37.743 | 40.043 | 41.197 | 42.422 | 41.782 | 41.716 | 42.959 | 43.545 | 43.473 | 42.643 | 41.489 | 41.477 | 40.665 | 41.203 | 54.26 | 49.883
110 | 6.376 | 6.081 | 5.894 | 5.775 | 5.712 | 5.734 | 5.832 | 6.492 | 13.693 | 14.527 | 14.946 | 15.39 | 15.158 | 15.134 | 15.585 | 15.798 | 15.772 | 15.47 | 15.052 | 15.048 | 14.753 | 14.948 | 7.864 | 7.229
111 | 2.71 | 2.585 | 2.505 | 2.455 | 2.428 | 2.437 | 2.478 | 2.759 | 17.555 | 18.625 | 19.161 | 19.731 | 19.434 | 19.403 | 19.981 | 20.253 | 20.22 | 19.834 | 19.297 | 19.292 | 18.914 | 19.164 | 3.342 | 3.072
112 | 57.863 | 55.188 | 53.485 | 52.412 | 51.836 | 52.036 | 52.922 | 58.918 | 35.724 | 37.901 | 38.993 | 40.152 | 39.547 | 39.485 | 40.662 | 41.216 | 41.148 | 40.362 | 39.27 | 39.259 | 38.49 | 38.999 | 71.364 | 65.606
113 | 22.157 | 21.132 | 20.48 | 20.07 | 19.849 | 19.926 | 20.265 | 22.561 | 14.307 | 15.179 | 15.616 | 16.081 | 15.838 | 15.813 | 16.285 | 16.507 | 16.479 | 16.165 | 15.727 | 15.723 | 15.415 | 15.619 | 27.327 | 25.122
114 | 29.33 | 27.974 | 27.111 | 26.567 | 26.275 | 26.376 | 26.825 | 29.865 | 28.702 | 30.451 | 31.329 | 32.26 | 31.774 | 31.724 | 32.669 | 33.114 | 33.06 | 32.428 | 31.551 | 31.542 | 30.924 | 31.333 | 36.173 | 33.255
115 | 4.623 | 4.409 | 4.273 | 4.187 | 4.141 | 4.157 | 4.228 | 4.707 | 6.056 | 6.426 | 6.611 | 6.807 | 6.705 | 6.694 | 6.893 | 6.987 | 6.976 | 6.843 | 6.658 | 6.656 | 6.525 | 6.612 | 5.701 | 5.241
116 | 51.008 | 48.65 | 47.149 | 46.203 | 45.696 | 45.872 | 46.653 | 51.939 | 55.912 | 59.32 | 61.028 | 62.843 | 61.896 | 61.799 | 63.64 | 64.507 | 64.401 | 63.171 | 61.462 | 61.444 | 60.24 | 61.037 | 62.91 | 57.835
117 | 12.433 | 11.859 | 11.493 | 11.262 | 11.138 | 11.181 | 11.372 | 12.66 | 11.323 | 12.013 | 12.359 | 12.726 | 12.535 | 12.515 | 12.888 | 13.063 | 13.042 | 12.793 | 12.447 | 12.443 | 12.199 | 12.361 | 15.334 | 14.097
118 | 20.563 | 19.612 | 19.007 | 18.626 | 18.421 | 18.492 | 18.807 | 20.938 | 27.824 | 29.52 | 30.37 | 31.274 | 30.802 | 30.754 | 31.67 | 32.102 | 32.049 | 31.437 | 30.586 | 30.578 | 29.978 | 30.375 | 25.361 | 23.315
119 | 17.215 | 16.419 | 15.913 | 15.594 | 15.422 | 15.482 | 15.745 | 17.529 | 22.821 | 24.212 | 24.91 | 25.65 | 25.264 | 25.224 | 25.975 | 26.33 | 26.286 | 25.784 | 25.087 | 25.079 | 24.588 | 24.913 | 21.232 | 19.519
120 | 42.56 | 40.593 | 39.34 | 38.551 | 38.127 | 38.275 | 38.926 | 43.336 | 48.714 | 51.684 | 53.172 | 54.753 | 53.928 | 53.843 | 55.448 | 56.203 | 56.111 | 55.039 | 53.55 | 53.535 | 52.486 | 53.18 | 52.491 | 48.256
121 | 42.879 | 40.897 | 39.635 | 38.84 | 38.413 | 38.561 | 39.217 | 43.661 | 49.592 | 52.615 | 54.13 | 55.74 | 54.9 | 54.813 | 56.447 | 57.216 | 57.122 | 56.03 | 54.515 | 54.499 | 53.432 | 54.138 | 52.884 | 48.617
122 | 38.256 | 36.488 | 35.362 | 34.653 | 34.272 | 34.404 | 34.989 | 38.954 | 52.225 | 55.409 | 57.005 | 58.7 | 57.815 | 57.724 | 59.444 | 60.254 | 60.155 | 59.006 | 57.41 | 57.393 | 56.269 | 57.013 | 47.183 | 43.376
123 | 5.42 | 5.169 | 5.01 | 4.909 | 4.855 | 4.874 | 4.957 | 5.518 | 3.686 | 3.911 | 4.024 | 4.144 | 4.081 | 4.075 | 4.196 | 4.253 | 4.246 | 4.165 | 4.052 | 4.051 | 3.972 | 4.024 | 6.684 | 6.145
124 | 18.809 | 17.94 | 17.386 | 17.038 | 16.85 | 16.915 | 17.203 | 19.152 | 30.896 | 32.78 | 33.724 | 34.726 | 34.203 | 34.149 | 35.167 | 35.646 | 35.587 | 34.907 | 33.963 | 33.954 | 33.288 | 33.729 | 23.198 | 21.327
125 | 15.143 | 14.443 | 13.997 | 13.717 | 13.566 | 13.618 | 13.85 | 15.419 | 18.257 | 19.37 | 19.928 | 20.52 | 20.211 | 20.179 | 20.78 | 21.064 | 21.029 | 20.627 | 20.069 | 20.063 | 19.67 | 19.931 | 18.677 | 17.17
126 | 15.94 | 15.203 | 14.734 | 14.439 | 14.28 | 14.335 | 14.579 | 16.231 | 15.536 | 16.483 | 16.958 | 17.462 | 17.199 | 17.172 | 17.683 | 17.924 | 17.895 | 17.553 | 17.078 | 17.073 | 16.739 | 16.96 | 19.659 | 18.073
127 | 18.65 | 17.788 | 17.239 | 16.893 | 16.707 | 16.772 | 17.057 | 18.99 | 27.21 | 28.868 | 29.7 | 30.583 | 30.122 | 30.075 | 30.971 | 31.393 | 31.341 | 30.742 | 29.911 | 29.902 | 29.316 | 29.704 | 23.002 | 21.146
128 | 38.416 | 36.64 | 35.509 | 34.797 | 34.415 | 34.547 | 35.135 | 39.116 | 67.234 | 71.333 | 73.387 | 75.57 | 74.431 | 74.313 | 76.528 | 77.571 | 77.443 | 75.963 | 73.909 | 73.888 | 72.44 | 73.398 | 47.379 | 43.557
129 | 31.243 | 29.798 | 28.879 | 28.3 | 27.989 | 28.097 | 28.575 | 31.812 | 33.266 | 35.294 | 36.31 | 37.39 | 36.827 | 36.769 | 37.864 | 38.38 | 38.317 | 37.585 | 36.569 | 36.558 | 35.842 | 36.316 | 38.533 | 35.424
130 | 38.416 | 36.64 | 35.509 | 34.797 | 34.415 | 34.547 | 35.135 | 39.116 | 47.837 | 50.752 | 52.214 | 53.767 | 52.956 | 52.873 | 54.448 | 55.191 | 55.1 | 54.047 | 52.585 | 52.57 | 51.54 | 52.222 | 47.379 | 43.557
131 | 29.649 | 28.278 | 27.405 | 26.856 | 26.561 | 26.663 | 27.117 | 30.189 | 25.63 | 27.192 | 27.975 | 28.807 | 28.373 | 28.328 | 29.172 | 29.57 | 29.521 | 28.957 | 28.174 | 28.166 | 27.614 | 27.979 | 36.567 | 33.617
132 | 5.42 | 5.169 | 5.01 | 4.909 | 4.855 | 4.874 | 4.957 | 5.518 | 14.921 | 15.831 | 16.287 | 16.771 | 16.519 | 16.493 | 16.984 | 17.215 | 17.187 | 16.859 | 16.403 | 16.398 | 16.077 | 16.289 | 6.684 | 6.145
133 | 41.126 | 39.224 | 38.014 | 37.252 | 36.842 | 36.984 | 37.614 | 41.876 | 49.592 | 52.615 | 54.13 | 55.74 | 54.9 | 54.813 | 56.447 | 57.216 | 57.122 | 56.03 | 54.515 | 54.499 | 53.432 | 54.138 | 50.722 | 46.629
134 | 15.462 | 14.747 | 14.292 | 14.005 | 13.852 | 13.905 | 14.142 | 15.744 | 29.755 | 31.569 | 32.478 | 33.444 | 32.94 | 32.888 | 33.868 | 34.33 | 34.273 | 33.618 | 32.709 | 32.7 | 32.059 | 32.483 | 19.07 | 17.531
135 | 7.173 | 6.841 | 6.63 | 6.497 | 6.426 | 6.451 | 6.561 | 7.304 | 21.153 | 22.443 | 23.089 | 23.776 | 23.417 | 23.381 | 24.077 | 24.405 | 24.365 | 23.9 | 23.253 | 23.247 | 22.791 | 23.093 | 8.847 | 8.133
136 | 17.056 | 16.267 | 15.765 | 15.449 | 15.28 | 15.338 | 15.599 | 17.367 | 26.244 | 27.844 | 28.646 | 29.498 | 29.053 | 29.007 | 29.872 | 30.279 | 30.229 | 29.652 | 28.85 | 28.841 | 28.276 | 28.65 | 21.036 | 19.339
137 | 4.144 | 3.953 | 3.831 | 3.754 | 3.713 | 3.727 | 3.791 | 4.22 | 33.003 | 35.015 | 36.023 | 37.094 | 36.535 | 36.478 | 37.564 | 38.077 | 38.014 | 37.288 | 36.279 | 36.269 | 35.558 | 36.028 | 5.111 | 4.699
138 | 18.012 | 17.18 | 16.649 | 16.316 | 16.136 | 16.199 | 16.474 | 18.341 | 29.404 | 31.196 | 32.095 | 33.049 | 32.551 | 32.5 | 33.468 | 33.925 | 33.869 | 33.222 | 32.323 | 32.314 | 31.681 | 32.1 | 22.215 | 20.423
139 | 12.593 | 12.011 | 11.64 | 11.406 | 11.281 | 11.325 | 11.517 | 12.822 | 41.78 | 44.327 | 45.604 | 46.96 | 46.252 | 46.179 | 47.555 | 48.203 | 48.124 | 47.204 | 45.928 | 45.915 | 45.015 | 45.61 | 15.531 | 14.278
140 | 13.071 | 12.467 | 12.082 | 11.84 | 11.71 | 11.755 | 11.955 | 13.309 | 20.188 | 21.418 | 22.035 | 22.691 | 22.349 | 22.313 | 22.978 | 23.292 | 23.253 | 22.809 | 22.192 | 22.186 | 21.751 | 22.039 | 16.121 | 14.82
141 | 12.433 | 11.859 | 11.493 | 11.262 | 11.138 | 11.181 | 11.372 | 12.66 | 13.956 | 14.807 | 15.233 | 15.686 | 15.45 | 15.425 | 15.885 | 16.102 | 16.075 | 15.768 | 15.341 | 15.337 | 15.036 | 15.235 | 15.334 | 14.097
142 | 6.535 | 6.233 | 6.041 | 5.92 | 5.855 | 5.877 | 5.977 | 6.655 | 28.526 | 30.265 | 31.137 | 32.063 | 31.58 | 31.53 | 32.469 | 32.912 | 32.858 | 32.23 | 31.358 | 31.349 | 30.735 | 31.141 | 8.06 | 7.41
143 | 4.463 | 4.257 | 4.126 | 4.043 | 3.998 | 4.014 | 4.082 | 4.545 | 12.639 | 13.41 | 13.796 | 14.206 | 13.992 | 13.97 | 14.386 | 14.583 | 14.558 | 14.28 | 13.894 | 13.89 | 13.618 | 13.798 | 5.505 | 5.061
144 | 5.898 | 5.625 | 5.452 | 5.342 | 5.284 | 5.304 | 5.394 | 6.005 | 7.373 | 7.822 | 8.048 | 8.287 | 8.162 | 8.149 | 8.392 | 8.506 | 8.492 | 8.33 | 8.105 | 8.103 | 7.944 | 8.049 | 7.274 | 6.687
145 | 42.082 | 40.136 | 38.898 | 38.118 | 37.699 | 37.844 | 38.488 | 42.849 | 36.426 | 38.646 | 39.759 | 40.942 | 40.325 | 40.261 | 41.461 | 42.026 | 41.957 | 41.155 | 40.042 | 40.031 | 39.246 | 39.765 | 51.901 | 47.714
146 | 1.753 | 1.672 | 1.621 | 1.588 | 1.571 | 1.577 | 1.604 | 1.785 | 2.37 | 2.514 | 2.587 | 2.664 | 2.624 | 2.619 | 2.697 | 2.734 | 2.73 | 2.678 | 2.605 | 2.604 | 2.553 | 2.587 | 2.163 | 1.988
147 | 9.723 | 9.274 | 8.988 | 8.808 | 8.711 | 8.744 | 8.893 | 9.901 | 8.251 | 8.754 | 9.006 | 9.274 | 9.134 | 9.119 | 9.391 | 9.519 | 9.503 | 9.322 | 9.07 | 9.067 | 8.889 | 9.007 | 11.992 | 11.025
149 | 44.154 | 42.113 | 40.813 | 39.995 | 39.555 | 39.708 | 40.384 | 44.959 | 59.247 | 62.859 | 64.669 | 66.592 | 65.588 | 65.485 | 67.436 | 68.355 | 68.243 | 66.939 | 65.129 | 65.11 | 63.834 | 64.678 | 54.457 | 50.063
150 | 4.623 | 4.409 | 4.273 | 4.187 | 4.141 | 4.157 | 4.228 | 4.707 | 6.934 | 7.357 | 7.569 | 7.794 | 7.676 | 7.664 | 7.893 | 8 | 7.987 | 7.834 | 7.622 | 7.62 | 7.471 | 7.57 | 5.701 | 5.241
151 | 47.98 | 45.762 | 44.35 | 43.46 | 42.983 | 43.148 | 43.883 | 48.855 | 55.648 | 59.04 | 60.741 | 62.547 | 61.604 | 61.507 | 63.34 | 64.204 | 64.098 | 62.873 | 61.173 | 61.155 | 59.957 | 60.75 | 59.175 | 54.401
152 | 15.781 | 15.051 | 14.587 | 14.294 | 14.137 | 14.192 | 14.433 | 16.069 | 20.451 | 21.698 | 22.323 | 22.987 | 22.64 | 22.604 | 23.278 | 23.595 | 23.556 | 23.106 | 22.481 | 22.475 | 22.035 | 22.326 | 19.463 | 17.893
153 | 2.072 | 1.976 | 1.915 | 1.877 | 1.856 | 1.864 | 1.895 | 2.11 | 1.317 | 1.397 | 1.437 | 1.48 | 1.458 | 1.455 | 1.499 | 1.519 | 1.517 | 1.488 | 1.447 | 1.447 | 1.419 | 1.437 | 2.556 | 2.35
154 | 26.461 | 25.237 | 24.459 | 23.968 | 23.705 | 23.796 | 24.201 | 26.943 | 15.975 | 16.949 | 17.437 | 17.955 | 17.685 | 17.657 | 18.183 | 18.431 | 18.4 | 18.049 | 17.561 | 17.556 | 17.212 | 17.439 | 32.635 | 30.002
155 | 10.361 | 9.882 | 9.577 | 9.385 | 9.282 | 9.318 | 9.476 | 10.55 | 10.708 | 11.361 | 11.688 | 12.036 | 11.854 | 11.836 | 12.188 | 12.355 | 12.334 | 12.099 | 11.771 | 11.768 | 11.537 | 11.69 | 12.779 | 11.748
156 | 9.245 | 8.818 | 8.546 | 8.374 | 8.282 | 8.314 | 8.456 | 9.414 | 4.301 | 4.563 | 4.694 | 4.834 | 4.761 | 4.754 | 4.895 | 4.962 | 4.954 | 4.859 | 4.728 | 4.726 | 4.634 | 4.695 | 11.403 | 10.483
157 | 5.42 | 5.169 | 5.01 | 4.909 | 4.855 | 4.874 | 4.957 | 5.518 | 21.066 | 22.35 | 22.993 | 23.677 | 23.32 | 23.284 | 23.977 | 24.304 | 24.264 | 23.801 | 23.157 | 23.15 | 22.697 | 22.997 | 6.684 | 6.145
158 | 17.853 | 17.028 | 16.502 | 16.171 | 15.993 | 16.055 | 16.328 | 18.179 | 20.451 | 21.698 | 22.323 | 22.987 | 22.64 | 22.604 | 23.278 | 23.595 | 23.556 | 23.106 | 22.481 | 22.475 | 22.035 | 22.326 | 22.019 | 20.242
159 | 15.94 | 15.203 | 14.734 | 14.439 | 14.28 | 14.335 | 14.579 | 16.231 | 28.263 | 29.986 | 30.849 | 31.767 | 31.288 | 31.239 | 32.17 | 32.608 | 32.554 | 31.932 | 31.069 | 31.06 | 30.451 | 30.854 | 19.659 | 18.073
160 | 13.39 | 12.771 | 12.377 | 12.128 | 11.995 | 12.041 | 12.246 | 13.634 | 16.852 | 17.88 | 18.395 | 18.942 | 18.656 | 18.627 | 19.182 | 19.443 | 19.411 | 19.04 | 18.525 | 18.52 | 18.157 | 18.397 | 16.514 | 15.182
161 | 2.232 | 2.128 | 2.063 | 2.021 | 1.999 | 2.007 | 2.041 | 2.272 | 4.564 | 4.842 | 4.982 | 5.13 | 5.053 | 5.045 | 5.195 | 5.266 | 5.257 | 5.157 | 5.017 | 5.016 | 4.918 | 4.983 | 2.752 | 2.53
162 | 7.014 | 6.689 | 6.483 | 6.353 | 6.283 | 6.307 | 6.415 | 7.142 | 15.185 | 16.11 | 16.574 | 17.067 | 16.81 | 16.784 | 17.284 | 17.519 | 17.49 | 17.156 | 16.692 | 16.687 | 16.36 | 16.577 | 8.65 | 7.952
163 | 6.854 | 6.537 | 6.336 | 6.209 | 6.14 | 6.164 | 6.269 | 6.979 | 10.094 | 10.709 | 11.018 | 11.345 | 11.174 | 11.157 | 11.489 | 11.646 | 11.627 | 11.404 | 11.096 | 11.093 | 10.875 | 11.019 | 8.454 | 7.772
164 | 10.361 | 9.882 | 9.577 | 9.385 | 9.282 | 9.318 | 9.476 | 10.55 | 17.028 | 18.066 | 18.586 | 19.139 | 18.851 | 18.821 | 19.382 | 19.646 | 19.614 | 19.239 | 18.718 | 18.713 | 18.346 | 18.589 | 12.779 | 11.748
165 | 2.55 | 2.433 | 2.357 | 2.31 | 2.285 | 2.294 | 2.333 | 2.597 | 8.075 | 8.567 | 8.814 | 9.076 | 8.939 | 8.925 | 9.191 | 9.317 | 9.301 | 9.124 | 8.877 | 8.874 | 8.7 | 8.815 | 3.146 | 2.892
166 | 18.012 | 17.18 | 16.649 | 16.316 | 16.136 | 16.199 | 16.474 | 18.341 | 16.765 | 17.787 | 18.299 | 18.843 | 18.559 | 18.53 | 19.082 | 19.342 | 19.31 | 18.941 | 18.429 | 18.424 | 18.063 | 18.302 | 22.215 | 20.423
167 | 5.101 | 4.865 | 4.715 | 4.62 | 4.57 | 4.587 | 4.665 | 5.194 | 5.793 | 6.146 | 6.323 | 6.511 | 6.413 | 6.403 | 6.594 | 6.684 | 6.673 | 6.545 | 6.368 | 6.366 | 6.242 | 6.324 | 6.291 | 5.783
168 | 10.68 | 10.186 | 9.872 | 9.674 | 9.568 | 9.604 | 9.768 | 10.875 | 30.457 | 32.314 | 33.245 | 34.233 | 33.717 | 33.664 | 34.667 | 35.14 | 35.082 | 34.412 | 33.481 | 33.471 | 32.815 | 33.249 | 13.172 | 12.109
169 | 8.289 | 7.906 | 7.662 | 7.508 | 7.426 | 7.454 | 7.581 | 8.44 | 7.549 | 8.009 | 8.239 | 8.484 | 8.356 | 8.343 | 8.592 | 8.709 | 8.695 | 8.529 | 8.298 | 8.295 | 8.133 | 8.241 | 10.223 | 9.398
170 | 8.608 | 8.21 | 7.956 | 7.797 | 7.711 | 7.741 | 7.873 | 8.765 | 8.865 | 9.406 | 9.676 | 9.964 | 9.814 | 9.799 | 10.09 | 10.228 | 10.211 | 10.016 | 9.745 | 9.742 | 9.551 | 9.678 | 10.616 | 9.76
171 | 4.623 | 4.409 | 4.273 | 4.187 | 4.141 | 4.157 | 4.228 | 4.707 | 12.113 | 12.851 | 13.221 | 13.614 | 13.409 | 13.388 | 13.787 | 13.975 | 13.952 | 13.685 | 13.315 | 13.311 | 13.051 | 13.223 | 5.701 | 5.241
172 | 4.623 | 4.409 | 4.273 | 4.187 | 4.141 | 4.157 | 4.228 | 4.707 | 6.407 | 6.798 | 6.994 | 7.202 | 7.093 | 7.082 | 7.293 | 7.393 | 7.38 | 7.239 | 7.044 | 7.042 | 6.904 | 6.995 | 5.701 | 5.241
245 | 1.594 | 1.52 | 1.473 | 1.444 | 1.428 | 1.434 | 1.458 | 1.623 | 6.934 | 7.357 | 7.569 | 7.794 | 7.676 | 7.664 | 7.893 | 8 | 7.987 | 7.834 | 7.622 | 7.62 | 7.471 | 7.57 | 1.966 | 1.807
246 | 0.159 | 0.152 | 0.147 | 0.144 | 0.143 | 0.143 | 0.146 | 0.162 | 4.389 | 4.656 | 4.79 | 4.933 | 4.858 | 4.851 | 4.995 | 5.063 | 5.055 | 4.958 | 4.824 | 4.823 | 4.728 | 4.791 | 0.197 | 0.181
247 | -0.319 | -0.304 | -0.295 | -0.289 | -0.286 | -0.287 | -0.292 | -0.325 | -0.527 | -0.559 | -0.575 | -0.592 | -0.583 | -0.582 | -0.599 | -0.608 | -0.607 | -0.595 | -0.579 | -0.579 | -0.567 | -0.575 | -0.393 | -0.361
248 | -0.478 | -0.456 | -0.442 | -0.433 | -0.428 | -0.43 | -0.437 | -0.487 | -1.229 | -1.304 | -1.341 | -1.381 | -1.36 | -1.358 | -1.399 | -1.418 | -1.415 | -1.388 | -1.351 | -1.35 | -1.324 | -1.341 | -0.59 | -0.542
249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.527 | 0.559 | 0.575 | 0.592 | 0.583 | 0.582 | 0.599 | 0.608 | 0.607 | 0.595 | 0.579 | 0.579 | 0.567 | 0.575 | 0 | 0
250 | 0.638 | 0.608 | 0.589 | 0.578 | 0.571 | 0.573 | 0.583 | 0.649 | 5.003 | 5.308 | 5.461 | 5.623 | 5.539 | 5.53 | 5.695 | 5.772 | 5.763 | 5.653 | 5.5 | 5.498 | 5.39 | 5.462 | 0.786 | 0.723
255 | 9.564 | 9.122 | 8.84 | 8.663 | 8.568 | 8.601 | 8.747 | 9.738 | 8.426 | 8.94 | 9.197 | 9.471 | 9.328 | 9.313 | 9.591 | 9.722 | 9.706 | 9.52 | 9.263 | 9.26 | 9.079 | 9.199 | 11.796 | 10.844
256 | 10.565 | 10.563 | 10.566 | 10.568 | 10.574 | 10.567 | 10.562 | 10.537 | 11.849 | 12.572 | 12.934 | 13.318 | 13.118 | 13.097 | 13.487 | 13.671 | 13.649 | 13.388 | 13.026 | 13.022 | 12.767 | 12.936 | 10.549 | 10.536
257 | -0.638 | -0.608 | -0.589 | -0.578 | -0.571 | -0.573 | -0.583 | -0.649 | -1.053 | -1.117 | -1.15 | -1.184 | -1.166 | -1.164 | -1.199 | -1.215 | -1.213 | -1.19 | -1.158 | -1.158 | -1.135 | -1.15 | -0.786 | -0.723
258 | -1.275 | -1.216 | -1.179 | -1.155 | -1.142 | -1.147 | -1.166 | -1.298 | -1.053 | -1.117 | -1.15 | -1.184 | -1.166 | -1.164 | -1.199 | -1.215 | -1.213 | -1.19 | -1.158 | -1.158 | -1.135 | -1.15 | -1.573 | -1.446
259 | -0.956 | -0.912 | -0.884 | -0.866 | -0.857 | -0.86 | -0.875 | -0.974 | -1.58 | -1.676 | -1.725 | -1.776 | -1.749 | -1.746 | -1.798 | -1.823 | -1.82 | -1.785 | -1.737 | -1.736 | -1.702 | -1.725 | -1.18 | -1.084
260 | 33.09 | 33.085 | 33.094 | 33.099 | 33.118 | 33.098 | 33.08 | 33.002 | 19.749 | 20.953 | 21.556 | 22.197 | 21.863 | 21.828 | 22.479 | 22.785 | 22.748 | 22.313 | 21.71 | 21.703 | 21.278 | 21.559 | 33.04 | 33
261 | -1.116 | -1.064 | -1.031 | -1.011 | -1 | -1.003 | -1.021 | -1.136 | -1.141 | -1.211 | -1.245 | -1.283 | -1.263 | -1.261 | -1.299 | -1.316 | -1.314 | -1.289 | -1.254 | -1.254 | -1.229 | -1.246 | -1.376 | -1.265

## Gen Status
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
108 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
111 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
112 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
112 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
113 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
113 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
113 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
115 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
121 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
122 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
123 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
125 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
130 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
132 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
132 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
134 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
136 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
136 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
140 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
140 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
141 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
146 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
147 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
147 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
149 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
151 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
151 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
153 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
153 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
154 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
154 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
157 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
158 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
158 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
161 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
163 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
163 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
164 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
164 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
165 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
165 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
168 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
169 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
169 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
170 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
170 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
171 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
171 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
172 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
172 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
175 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
183 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
187 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
220 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
220 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
222 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
227 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
227 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1
234 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
235 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
236 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
237 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
238 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
239 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
242 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
243 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
250 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
251 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
252 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
253 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
254 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
255 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
262 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
263 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
264 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
265 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
266 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
267 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
268 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen P (MW)
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
1 | -28.757 | 117.126 | 89.777 | 65.4 | 55.293 | 41.618 | -84.173 | -204.508 | -198.461 | -149.216 | -86.271 | -119.471 | -166.495 | -85.284 | -31.472 | -43.814 | -128.604 | -127.123 | -320.03 | -239.683 | -252.149 | -181.799 | -36.656 | -187.846
2 | -40.467 | 30.724 | 23.55 | 17.156 | 14.504 | 10.917 | -118.448 | -287.784 | -279.274 | -209.977 | -121.401 | -168.12 | -234.292 | -120.012 | -44.288 | -61.656 | -180.972 | -178.888 | -450.347 | -337.283 | -354.824 | -255.828 | -51.582 | -264.338
3 | -86.688 | 0.612 | 0.469 | 0.342 | 0.289 | 0.217 | -253.74 | -616.491 | -598.261 | -449.812 | -260.065 | -360.147 | -501.899 | -257.088 | -94.873 | -132.079 | -387.679 | -383.214 | -964.733 | -722.526 | -760.104 | -548.034 | -110.5 | -566.264
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | -12.143 | 7.508 | 5.755 | 4.192 | 3.544 | 2.668 | -35.543 | -86.356 | -83.802 | -63.008 | -36.429 | -50.448 | -70.304 | -36.012 | -13.289 | -18.501 | -54.304 | -53.679 | -135.136 | -101.208 | -106.472 | -76.766 | -15.478 | -79.32
6 | -1.271 | 41.03 | 31.45 | 22.91 | 19.37 | 14.579 | -3.722 | -9.042 | -8.775 | -6.598 | -3.814 | -5.282 | -7.362 | -3.771 | -1.392 | -1.937 | -5.686 | -5.621 | -14.15 | -10.598 | -11.149 | -8.038 | -1.621 | -8.306
7 | -63.673 | 0 | 0 | 0 | 0 | 0 | -186.374 | -452.818 | -439.428 | -330.391 | -191.02 | -264.531 | -368.649 | -188.834 | -69.685 | -97.013 | -284.754 | -281.474 | -708.604 | -530.702 | -558.303 | -402.535 | -81.163 | -415.926
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.233 | 3.618 | 10.737 | 16.689 | 21.066 | 23.984 | 25.676 | 26.143 | 25.734 | 24.217 | 21.649 | 17.74 | 11.671 | 4.785 | 0.642 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.314 | 4.874 | 14.464 | 22.482 | 28.377 | 32.308 | 34.587 | 35.216 | 34.666 | 32.622 | 29.163 | 23.897 | 15.722 | 6.446 | 0.865 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 41 | 34 | 38 | 38 | 30 | 30 | 30 | 50 | 44 | 44 | 44 | 44 | 35 | 33
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 39 | 39 | 0 | 0 | 0 | 0 | 42 | 44 | 44 | 44 | 36 | 34
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 1.949 | 1.961 | 1.883 | 1.809 | 1.713 | 1.584 | 1.422 | 1.123 | 0.59 | 0.309 | 0.205 | 0.213 | 0.36 | 0.537 | 0.611 | 0.821 | 1.239 | 1.698 | 2.238 | 2.461 | 2.653 | 2.787 | 2.564 | 2.336
108 | 0.689 | 0.689 | 0.689 | 0.758 | 0.724 | 0.689 | 0.896 | 0.758 | 1.034 | 1.654 | 1.826 | 2.067 | 1.93 | 1.688 | 1.378 | 1.206 | 1.378 | 1.275 | 1.275 | 1.309 | 1.62 | 1.585 | 1.206 | 0.827
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 21.477 | 21.789 | 21.93 | 21.732 | 21.222 | 20.854 | 21.052 | 25.812 | 26.152 | 26.266 | 26.407 | 26.322 | 26.379 | 25.784 | 25.586 | 25.614 | 25.812 | 25.897 | 25.501 | 25.557 | 25.869 | 26.237 | 26.096 | 26.294
109 | 5.51 | 5.546 | 5.324 | 5.116 | 4.844 | 4.478 | 4.02 | 3.174 | 1.67 | 0.874 | 0.58 | 0.602 | 1.017 | 1.519 | 1.727 | 2.322 | 3.504 | 4.801 | 6.327 | 6.958 | 7.502 | 7.882 | 7.251 | 6.606
109 | 0.439 | 0.439 | 0.439 | 0.483 | 0.461 | 0.439 | 0.571 | 0.483 | 0.659 | 1.054 | 1.164 | 1.318 | 1.23 | 1.076 | 0.879 | 0.769 | 0.879 | 0.813 | 0.813 | 0.835 | 1.032 | 1.01 | 0.769 | 0.527
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 0.29 | 0.862 | 1.339 | 1.691 | 1.925 | 2.061 | 2.098 | 2.065 | 1.944 | 1.738 | 1.424 | 0.937 | 0.384 | 0.052 | 0 | 0 | 0
110 | 5.894 | 5.98 | 6.019 | 5.964 | 5.824 | 5.723 | 5.778 | 7.084 | 7.177 | 7.209 | 7.247 | 7.224 | 7.24 | 7.076 | 7.022 | 7.03 | 7.084 | 7.107 | 6.999 | 7.014 | 7.1 | 7.201 | 7.162 | 7.216
111 | 1.931 | 1.959 | 1.972 | 1.954 | 1.908 | 1.875 | 1.893 | 2.321 | 2.351 | 2.361 | 2.374 | 2.367 | 2.372 | 2.318 | 2.3 | 2.303 | 2.321 | 2.328 | 2.293 | 2.298 | 2.326 | 2.359 | 2.346 | 2.364
112 | 70.597 | 71.621 | 72.087 | 71.435 | 69.758 | 68.548 | 69.2 | 84.846 | 85.964 | 86.337 | 86.802 | 86.523 | 86.709 | 84.753 | 84.101 | 84.194 | 84.846 | 85.126 | 83.822 | 84.008 | 85.033 | 86.243 | 85.778 | 86.43
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0.132 | 2.048 | 6.079 | 9.449 | 11.927 | 13.579 | 14.537 | 14.801 | 14.57 | 13.711 | 12.257 | 10.044 | 6.608 | 2.709 | 0.363 | 0 | 0 | 0
113 | 0.203 | 0.206 | 0.208 | 0.206 | 0.201 | 0.197 | 0.199 | 0.244 | 0.247 | 0.249 | 0.25 | 0.249 | 0.25 | 0.244 | 0.242 | 0.242 | 0.244 | 0.245 | 0.241 | 0.242 | 0.245 | 0.248 | 0.247 | 0.249
113 | 0.181 | 0.181 | 0.181 | 0.199 | 0.19 | 0.181 | 0.235 | 0.199 | 0.271 | 0.434 | 0.479 | 0.543 | 0.507 | 0.443 | 0.362 | 0.317 | 0.362 | 0.335 | 0.335 | 0.344 | 0.425 | 0.416 | 0.317 | 0.217
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0.231 | 3.579 | 10.621 | 16.508 | 20.837 | 23.724 | 25.397 | 25.859 | 25.455 | 23.954 | 21.415 | 17.547 | 11.544 | 4.733 | 0.635 | 0 | 0 | 0
114 | 9.451 | 9.588 | 9.651 | 9.564 | 9.339 | 9.177 | 9.264 | 11.359 | 11.509 | 11.559 | 11.621 | 11.583 | 11.608 | 11.347 | 11.259 | 11.272 | 11.359 | 11.396 | 11.222 | 11.247 | 11.384 | 11.546 | 11.484 | 11.571
114 | 17.095 | 17.206 | 16.517 | 15.872 | 15.027 | 13.894 | 12.471 | 9.848 | 5.18 | 2.712 | 1.801 | 1.867 | 3.157 | 4.713 | 5.357 | 7.203 | 10.87 | 14.894 | 19.629 | 21.585 | 23.275 | 24.453 | 22.497 | 20.496
114 | 0.376 | 0.376 | 0.376 | 0.414 | 0.395 | 0.376 | 0.489 | 0.414 | 0.564 | 0.903 | 0.997 | 1.128 | 1.053 | 0.922 | 0.752 | 0.658 | 0.752 | 0.696 | 0.696 | 0.715 | 0.884 | 0.865 | 0.658 | 0.451
114 | 0.747 | 0.747 | 0.747 | 0.821 | 0.784 | 0.747 | 0.971 | 0.821 | 1.12 | 1.792 | 1.978 | 2.24 | 2.09 | 1.829 | 1.493 | 1.307 | 1.493 | 1.381 | 1.381 | 1.419 | 1.754 | 1.717 | 1.307 | 0.896
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021 | 0.322 | 0.955 | 1.484 | 1.874 | 2.133 | 2.284 | 2.325 | 2.289 | 2.154 | 1.925 | 1.578 | 1.038 | 0.426 | 0.057 | 0 | 0 | 0
115 | 0 | 0 | 0 | 12 | 10 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0 | 0 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0.339 | 0.344 | 0.346 | 0.343 | 0.335 | 0.329 | 0.332 | 0.407 | 0.412 | 0.414 | 0.417 | 0.415 | 0.416 | 0.407 | 0.404 | 0.404 | 0.407 | 0.408 | 0.402 | 0.403 | 0.408 | 0.414 | 0.412 | 0.415
115 | 1.115 | 1.123 | 1.078 | 1.036 | 0.981 | 0.907 | 0.814 | 0.643 | 0.338 | 0.177 | 0.117 | 0.122 | 0.206 | 0.308 | 0.35 | 0.47 | 0.709 | 0.972 | 1.281 | 1.408 | 1.519 | 1.596 | 1.468 | 1.337
115 | 0.281 | 0.281 | 0.281 | 0.31 | 0.295 | 0.281 | 0.366 | 0.31 | 0.422 | 0.675 | 0.746 | 0.844 | 0.788 | 0.689 | 0.563 | 0.492 | 0.563 | 0.521 | 0.521 | 0.535 | 0.661 | 0.647 | 0.492 | 0.338
116 | 23.239 | 23.576 | 23.729 | 23.515 | 22.963 | 22.564 | 22.779 | 27.929 | 28.297 | 28.42 | 28.573 | 28.481 | 28.542 | 27.899 | 27.684 | 27.715 | 27.929 | 28.021 | 27.592 | 27.653 | 27.991 | 28.389 | 28.236 | 28.45
116 | 0.04 | 0.04 | 0.04 | 0.044 | 0.042 | 0.04 | 0.052 | 0.044 | 0.06 | 0.096 | 0.107 | 0.121 | 0.113 | 0.098 | 0.08 | 0.07 | 0.08 | 0.074 | 0.074 | 0.076 | 0.094 | 0.092 | 0.07 | 0.048
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.157 | 0.466 | 0.724 | 0.914 | 1.041 | 1.114 | 1.134 | 1.116 | 1.051 | 0.939 | 0.77 | 0.506 | 0.208 | 0.028 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082 | 1.264 | 3.75 | 5.829 | 7.357 | 8.376 | 8.967 | 9.13 | 8.987 | 8.458 | 7.561 | 6.195 | 4.076 | 1.671 | 0.224 | 0 | 0 | 0
118 | 13.11 | 13.3 | 13.387 | 13.266 | 12.954 | 12.729 | 12.85 | 15.756 | 15.964 | 16.033 | 16.119 | 16.067 | 16.102 | 15.739 | 15.618 | 15.635 | 15.756 | 15.808 | 15.566 | 15.6 | 15.791 | 16.015 | 15.929 | 16.05
118 | 0.175 | 0.176 | 0.169 | 0.162 | 0.154 | 0.142 | 0.127 | 0.101 | 0.053 | 0.028 | 0.018 | 0.019 | 0.032 | 0.048 | 0.055 | 0.074 | 0.111 | 0.152 | 0.201 | 0.221 | 0.238 | 0.25 | 0.23 | 0.209
118 | 0.692 | 0.692 | 0.692 | 0.761 | 0.727 | 0.692 | 0.9 | 0.761 | 1.038 | 1.661 | 1.834 | 2.076 | 1.938 | 1.695 | 1.384 | 1.211 | 1.384 | 1.28 | 1.28 | 1.315 | 1.626 | 1.592 | 1.211 | 0.83
118 | 2.254 | 2.254 | 2.254 | 2.48 | 2.367 | 2.254 | 2.93 | 2.48 | 3.381 | 5.41 | 5.973 | 6.762 | 6.312 | 5.523 | 4.508 | 3.945 | 4.508 | 4.17 | 4.17 | 4.283 | 5.297 | 5.184 | 3.945 | 2.705
119 | 1.762 | 1.787 | 1.799 | 1.782 | 1.741 | 1.71 | 1.727 | 2.117 | 2.145 | 2.154 | 2.166 | 2.159 | 2.164 | 2.115 | 2.098 | 2.101 | 2.117 | 2.124 | 2.092 | 2.096 | 2.122 | 2.152 | 2.14 | 2.157
119 | 4.892 | 4.924 | 4.727 | 4.542 | 4.3 | 3.976 | 3.569 | 2.818 | 1.482 | 0.776 | 0.515 | 0.534 | 0.903 | 1.349 | 1.533 | 2.061 | 3.111 | 4.262 | 5.617 | 6.177 | 6.66 | 6.998 | 6.438 | 5.865
119 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.157 | 0.466 | 0.724 | 0.914 | 1.041 | 1.114 | 1.134 | 1.116 | 1.051 | 0.939 | 0.77 | 0.506 | 0.208 | 0.028 | 0 | 0 | 0
120 | 9.316 | 9.451 | 9.512 | 9.426 | 9.205 | 9.045 | 9.131 | 11.196 | 11.344 | 11.393 | 11.454 | 11.417 | 11.442 | 11.184 | 11.098 | 11.11 | 11.196 | 11.233 | 11.061 | 11.086 | 11.221 | 11.38 | 11.319 | 11.405
120 | 5.9 | 5.938 | 5.7 | 5.478 | 5.186 | 4.795 | 4.304 | 3.399 | 1.788 | 0.936 | 0.621 | 0.644 | 1.089 | 1.626 | 1.849 | 2.486 | 3.752 | 5.14 | 6.775 | 7.45 | 8.033 | 8.439 | 7.764 | 7.074
120 | 0.563 | 0.563 | 0.563 | 0.619 | 0.591 | 0.563 | 0.732 | 0.619 | 0.844 | 1.351 | 1.491 | 1.688 | 1.576 | 1.379 | 1.126 | 0.985 | 1.126 | 1.041 | 1.041 | 1.069 | 1.323 | 1.294 | 0.985 | 0.675
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0.345 | 1.025 | 1.593 | 2.011 | 2.289 | 2.451 | 2.495 | 2.456 | 2.311 | 2.066 | 1.693 | 1.114 | 0.457 | 0.061 | 0 | 0 | 0
121 | 0.874 | 0.879 | 0.844 | 0.811 | 0.768 | 0.71 | 0.637 | 0.503 | 0.265 | 0.139 | 0.092 | 0.095 | 0.161 | 0.241 | 0.274 | 0.368 | 0.555 | 0.761 | 1.003 | 1.103 | 1.189 | 1.25 | 1.15 | 1.047
121 | 0.017 | 0.017 | 0.017 | 0.019 | 0.018 | 0.017 | 0.022 | 0.019 | 0.026 | 0.041 | 0.046 | 0.052 | 0.048 | 0.042 | 0.034 | 0.03 | 0.034 | 0.032 | 0.032 | 0.033 | 0.04 | 0.04 | 0.03 | 0.021
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 1.57 | 4.658 | 7.241 | 9.139 | 10.405 | 11.139 | 11.342 | 11.165 | 10.506 | 9.392 | 7.696 | 5.063 | 2.076 | 0.278 | 0 | 0 | 0
122 | 7.215 | 7.32 | 7.368 | 7.301 | 7.13 | 7.006 | 7.073 | 8.672 | 8.786 | 8.824 | 8.872 | 8.843 | 8.862 | 8.662 | 8.596 | 8.605 | 8.672 | 8.7 | 8.567 | 8.586 | 8.691 | 8.815 | 8.767 | 8.834
122 | 19.285 | 19.411 | 18.633 | 17.906 | 16.953 | 15.674 | 14.069 | 11.11 | 5.843 | 3.06 | 2.031 | 2.107 | 3.561 | 5.317 | 6.044 | 8.125 | 12.263 | 16.803 | 22.144 | 24.351 | 26.257 | 27.587 | 25.38 | 23.123
122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.008 | 0.023 | 0.036 | 0.046 | 0.052 | 0.056 | 0.057 | 0.056 | 0.053 | 0.047 | 0.038 | 0.025 | 0.01 | 0.001 | 0 | 0 | 0
123 | 15.041 | 15.259 | 15.358 | 15.219 | 14.862 | 14.604 | 14.743 | 18.077 | 18.315 | 18.394 | 18.493 | 18.434 | 18.474 | 18.057 | 17.918 | 17.938 | 18.077 | 18.136 | 17.858 | 17.898 | 18.116 | 18.374 | 18.275 | 18.414
123 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096 | 1.491 | 4.425 | 6.878 | 8.682 | 9.885 | 10.582 | 10.775 | 10.606 | 9.981 | 8.923 | 7.311 | 4.81 | 1.972 | 0.265 | 0 | 0 | 0
124 | 0.034 | 0.034 | 0.035 | 0.034 | 0.033 | 0.033 | 0.033 | 0.041 | 0.041 | 0.041 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.04 | 0.041 | 0.041 | 0.04 | 0.04 | 0.041 | 0.041 | 0.041 | 0.041
124 | 29.352 | 29.542 | 28.359 | 27.252 | 25.802 | 23.855 | 21.413 | 16.909 | 8.893 | 4.657 | 3.092 | 3.206 | 5.42 | 8.092 | 9.199 | 12.367 | 18.664 | 25.573 | 33.703 | 37.062 | 39.962 | 41.985 | 38.626 | 35.191
124 | 0.026 | 0.026 | 0.026 | 0.028 | 0.027 | 0.026 | 0.034 | 0.028 | 0.039 | 0.062 | 0.068 | 0.078 | 0.072 | 0.063 | 0.052 | 0.045 | 0.052 | 0.048 | 0.048 | 0.049 | 0.061 | 0.059 | 0.045 | 0.031
125 | 2.298 | 2.313 | 2.22 | 2.134 | 2.02 | 1.868 | 1.677 | 1.324 | 0.696 | 0.365 | 0.242 | 0.251 | 0.424 | 0.634 | 0.72 | 0.968 | 1.461 | 2.002 | 2.639 | 2.902 | 3.129 | 3.287 | 3.024 | 2.755
126 | 12.161 | 12.338 | 12.418 | 12.306 | 12.017 | 11.808 | 11.921 | 14.616 | 14.809 | 14.873 | 14.953 | 14.905 | 14.937 | 14.6 | 14.488 | 14.504 | 14.616 | 14.664 | 14.44 | 14.472 | 14.648 | 14.857 | 14.777 | 14.889
126 | 2.728 | 2.746 | 2.636 | 2.533 | 2.398 | 2.217 | 1.99 | 1.572 | 0.827 | 0.433 | 0.287 | 0.298 | 0.504 | 0.752 | 0.855 | 1.149 | 1.735 | 2.377 | 3.133 | 3.445 | 3.714 | 3.902 | 3.59 | 3.271
126 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 1.46 | 4.332 | 6.734 | 8.499 | 9.677 | 10.359 | 10.548 | 10.383 | 9.771 | 8.735 | 7.157 | 4.709 | 1.931 | 0.259 | 0 | 0 | 0
127 | 0.305 | 0.309 | 0.311 | 0.309 | 0.301 | 0.296 | 0.299 | 0.366 | 0.371 | 0.373 | 0.375 | 0.374 | 0.374 | 0.366 | 0.363 | 0.364 | 0.366 | 0.368 | 0.362 | 0.363 | 0.367 | 0.372 | 0.37 | 0.373
127 | 45.533 | 45.829 | 43.993 | 42.276 | 40.026 | 37.006 | 33.217 | 26.23 | 13.796 | 7.224 | 4.796 | 4.974 | 8.408 | 12.553 | 14.27 | 19.184 | 28.954 | 39.671 | 52.282 | 57.493 | 61.993 | 65.131 | 59.921 | 54.592
127 | 1.307 | 1.307 | 1.307 | 1.437 | 1.372 | 1.307 | 1.698 | 1.437 | 1.96 | 3.136 | 3.462 | 3.92 | 3.658 | 3.201 | 2.613 | 2.286 | 2.613 | 2.417 | 2.417 | 2.482 | 3.07 | 3.005 | 2.286 | 1.568
127 | 0.856 | 0.856 | 0.856 | 0.941 | 0.898 | 0.856 | 1.112 | 0.941 | 1.284 | 2.054 | 2.268 | 2.567 | 2.396 | 2.096 | 1.711 | 1.497 | 1.711 | 1.583 | 1.583 | 1.626 | 2.011 | 1.968 | 1.497 | 1.027
128 | 54.743 | 55.537 | 55.898 | 55.393 | 54.093 | 53.154 | 53.66 | 65.793 | 66.659 | 66.948 | 67.309 | 67.093 | 67.237 | 65.72 | 65.215 | 65.287 | 65.793 | 66.009 | 64.998 | 65.143 | 65.937 | 66.876 | 66.515 | 67.02
128 | 0.296 | 0.298 | 0.286 | 0.275 | 0.26 | 0.24 | 0.216 | 0.17 | 0.09 | 0.047 | 0.031 | 0.032 | 0.055 | 0.082 | 0.093 | 0.125 | 0.188 | 0.258 | 0.339 | 0.373 | 0.403 | 0.423 | 0.389 | 0.354
128 | 1.292 | 1.292 | 1.292 | 1.421 | 1.357 | 1.292 | 1.68 | 1.421 | 1.938 | 3.101 | 3.424 | 3.877 | 3.618 | 3.166 | 2.584 | 2.261 | 2.584 | 2.391 | 2.391 | 2.455 | 3.037 | 2.972 | 2.261 | 1.551
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0.204 | 0.606 | 0.941 | 1.188 | 1.353 | 1.448 | 1.474 | 1.451 | 1.366 | 1.221 | 1.001 | 0.658 | 0.27 | 0.036 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 24.153 | 24.504 | 24.663 | 24.44 | 23.867 | 23.452 | 23.675 | 29.029 | 29.411 | 29.538 | 29.698 | 29.602 | 29.666 | 28.997 | 28.774 | 28.806 | 29.029 | 29.124 | 28.678 | 28.742 | 29.092 | 29.507 | 29.347 | 29.57
129 | 4.623 | 4.653 | 4.467 | 4.292 | 4.064 | 3.757 | 3.373 | 2.663 | 1.401 | 0.733 | 0.487 | 0.505 | 0.854 | 1.275 | 1.449 | 1.948 | 2.94 | 4.028 | 5.308 | 5.838 | 6.294 | 6.613 | 6.084 | 5.543
129 | 0.514 | 0.514 | 0.514 | 0.565 | 0.54 | 0.514 | 0.668 | 0.565 | 0.771 | 1.234 | 1.362 | 1.542 | 1.439 | 1.259 | 1.028 | 0.899 | 1.028 | 0.951 | 0.951 | 0.977 | 1.208 | 1.182 | 0.899 | 0.617
130 | 2.913 | 2.956 | 2.975 | 2.948 | 2.879 | 2.829 | 2.856 | 3.501 | 3.547 | 3.563 | 3.582 | 3.571 | 3.578 | 3.497 | 3.471 | 3.474 | 3.501 | 3.513 | 3.459 | 3.467 | 3.509 | 3.559 | 3.54 | 3.567
131 | 28.591 | 29.006 | 29.194 | 28.93 | 28.252 | 27.761 | 28.025 | 34.362 | 34.815 | 34.965 | 35.154 | 35.041 | 35.116 | 34.324 | 34.06 | 34.098 | 34.362 | 34.475 | 33.947 | 34.023 | 34.437 | 34.928 | 34.739 | 35.003
131 | 7.902 | 7.954 | 7.635 | 7.337 | 6.947 | 6.423 | 5.765 | 4.552 | 2.394 | 1.254 | 0.832 | 0.863 | 1.459 | 2.179 | 2.477 | 3.329 | 5.025 | 6.885 | 9.074 | 9.978 | 10.759 | 11.304 | 10.399 | 9.475
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093 | 1.436 | 4.262 | 6.625 | 8.362 | 9.521 | 10.192 | 10.378 | 10.216 | 9.613 | 8.594 | 7.042 | 4.633 | 1.899 | 0.255 | 0 | 0 | 0
132 | 11.247 | 11.41 | 11.484 | 11.38 | 11.113 | 10.92 | 11.024 | 13.517 | 13.695 | 13.754 | 13.828 | 13.784 | 13.814 | 13.502 | 13.398 | 13.413 | 13.517 | 13.561 | 13.354 | 13.383 | 13.546 | 13.739 | 13.665 | 13.769
132 | 2.889 | 2.908 | 2.792 | 2.683 | 2.54 | 2.348 | 2.108 | 1.665 | 0.875 | 0.458 | 0.304 | 0.316 | 0.534 | 0.797 | 0.906 | 1.217 | 1.837 | 2.517 | 3.318 | 3.648 | 3.934 | 4.133 | 3.803 | 3.464
133 | 46.443 | 47.117 | 47.424 | 46.995 | 45.892 | 45.095 | 45.524 | 55.818 | 56.553 | 56.798 | 57.105 | 56.921 | 57.043 | 55.757 | 55.328 | 55.389 | 55.818 | 56.002 | 55.144 | 55.266 | 55.94 | 56.737 | 56.431 | 56.859
133 | 16.893 | 17.003 | 16.322 | 15.685 | 14.85 | 13.73 | 12.324 | 9.732 | 5.119 | 2.68 | 1.779 | 1.845 | 3.119 | 4.657 | 5.294 | 7.118 | 10.742 | 14.718 | 19.398 | 21.331 | 23 | 24.165 | 22.231 | 20.254
133 | 0.468 | 0.468 | 0.468 | 0.515 | 0.491 | 0.468 | 0.608 | 0.515 | 0.702 | 1.123 | 1.24 | 1.404 | 1.311 | 1.147 | 0.936 | 0.819 | 0.936 | 0.866 | 0.866 | 0.889 | 1.1 | 1.077 | 0.819 | 0.562
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 62.873 | 63.785 | 64.2 | 63.62 | 62.127 | 61.048 | 61.629 | 75.564 | 76.559 | 76.891 | 77.306 | 77.057 | 77.223 | 75.481 | 74.9 | 74.983 | 75.564 | 75.813 | 74.651 | 74.817 | 75.73 | 76.808 | 76.393 | 76.974
134 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.094 | 0.279 | 0.434 | 0.548 | 0.624 | 0.668 | 0.681 | 0.67 | 0.63 | 0.564 | 0.462 | 0.304 | 0.125 | 0.017 | 0 | 0 | 0
136 | 1.829 | 1.856 | 1.868 | 1.851 | 1.808 | 1.776 | 1.793 | 2.199 | 2.227 | 2.237 | 2.249 | 2.242 | 2.247 | 2.196 | 2.179 | 2.182 | 2.199 | 2.206 | 2.172 | 2.177 | 2.203 | 2.235 | 2.223 | 2.24
136 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.314 | 0.932 | 1.448 | 1.828 | 2.081 | 2.228 | 2.268 | 2.233 | 2.101 | 1.878 | 1.539 | 1.013 | 0.415 | 0.056 | 0 | 0 | 0
137 | 9.553 | 9.692 | 9.755 | 9.666 | 9.439 | 9.276 | 9.364 | 11.481 | 11.632 | 11.683 | 11.746 | 11.708 | 11.733 | 11.469 | 11.38 | 11.393 | 11.481 | 11.519 | 11.343 | 11.368 | 11.506 | 11.67 | 11.607 | 11.695
137 | 5.806 | 5.844 | 5.61 | 5.391 | 5.104 | 4.719 | 4.235 | 3.345 | 1.759 | 0.921 | 0.612 | 0.634 | 1.072 | 1.601 | 1.82 | 2.446 | 3.692 | 5.058 | 6.666 | 7.331 | 7.905 | 8.305 | 7.64 | 6.961
137 | 0.129 | 0.129 | 0.129 | 0.142 | 0.136 | 0.129 | 0.168 | 0.142 | 0.194 | 0.31 | 0.342 | 0.388 | 0.362 | 0.317 | 0.258 | 0.226 | 0.258 | 0.239 | 0.239 | 0.246 | 0.304 | 0.297 | 0.226 | 0.155
138 | 1.829 | 1.856 | 1.868 | 1.851 | 1.808 | 1.776 | 1.793 | 2.199 | 2.227 | 2.237 | 2.249 | 2.242 | 2.247 | 2.196 | 2.179 | 2.182 | 2.199 | 2.206 | 2.172 | 2.177 | 2.203 | 2.235 | 2.223 | 2.24
138 | 0.178 | 0.178 | 0.178 | 0.196 | 0.187 | 0.178 | 0.231 | 0.196 | 0.267 | 0.427 | 0.472 | 0.534 | 0.498 | 0.436 | 0.356 | 0.312 | 0.356 | 0.329 | 0.329 | 0.338 | 0.418 | 0.409 | 0.312 | 0.214
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029 | 0.455 | 1.351 | 2.1 | 2.65 | 3.017 | 3.23 | 3.289 | 3.238 | 3.047 | 2.724 | 2.232 | 1.468 | 0.602 | 0.081 | 0 | 0 | 0
139 | 2.947 | 2.99 | 3.009 | 2.982 | 2.912 | 2.862 | 2.889 | 3.542 | 3.589 | 3.604 | 3.624 | 3.612 | 3.62 | 3.538 | 3.511 | 3.515 | 3.542 | 3.554 | 3.499 | 3.507 | 3.55 | 3.6 | 3.581 | 3.608
140 | 0.187 | 0.187 | 0.187 | 0.205 | 0.196 | 0.187 | 0.243 | 0.205 | 0.28 | 0.448 | 0.495 | 0.56 | 0.523 | 0.457 | 0.373 | 0.327 | 0.373 | 0.345 | 0.345 | 0.355 | 0.439 | 0.429 | 0.327 | 0.224
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0.505 | 7.832 | 23.245 | 36.13 | 45.605 | 51.921 | 55.585 | 56.595 | 55.711 | 52.427 | 46.868 | 38.404 | 25.266 | 10.359 | 1.39 | 0 | 0 | 0
141 | 4.133 | 4.193 | 4.22 | 4.182 | 4.084 | 4.013 | 4.051 | 4.967 | 5.032 | 5.054 | 5.082 | 5.065 | 5.076 | 4.962 | 4.923 | 4.929 | 4.967 | 4.983 | 4.907 | 4.918 | 4.978 | 5.049 | 5.022 | 5.06
142 | 6.335 | 6.427 | 6.468 | 6.41 | 6.26 | 6.151 | 6.209 | 7.613 | 7.714 | 7.747 | 7.789 | 7.764 | 7.781 | 7.605 | 7.547 | 7.555 | 7.613 | 7.638 | 7.521 | 7.538 | 7.63 | 7.739 | 7.697 | 7.755
142 | 15.066 | 15.163 | 14.556 | 13.988 | 13.244 | 12.244 | 10.991 | 8.679 | 4.565 | 2.39 | 1.587 | 1.646 | 2.782 | 4.153 | 4.721 | 6.348 | 9.58 | 13.126 | 17.299 | 19.023 | 20.512 | 21.55 | 19.826 | 18.063
142 | 0.781 | 0.781 | 0.781 | 0.859 | 0.82 | 0.781 | 1.015 | 0.859 | 1.172 | 1.875 | 2.07 | 2.343 | 2.187 | 1.914 | 1.562 | 1.367 | 1.562 | 1.445 | 1.445 | 1.484 | 1.835 | 1.796 | 1.367 | 0.937
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.008 | 0.023 | 0.036 | 0.046 | 0.052 | 0.056 | 0.057 | 0.056 | 0.053 | 0.047 | 0.038 | 0.025 | 0.01 | 0.001 | 0 | 0 | 0
144 | 0.339 | 0.344 | 0.346 | 0.343 | 0.335 | 0.329 | 0.332 | 0.407 | 0.412 | 0.414 | 0.417 | 0.415 | 0.416 | 0.407 | 0.404 | 0.404 | 0.407 | 0.408 | 0.402 | 0.403 | 0.408 | 0.414 | 0.412 | 0.415
144 | 14.797 | 14.893 | 14.296 | 13.738 | 13.007 | 12.026 | 10.794 | 8.524 | 4.483 | 2.347 | 1.559 | 1.616 | 2.732 | 4.079 | 4.637 | 6.234 | 9.409 | 12.892 | 16.99 | 18.684 | 20.146 | 21.166 | 19.472 | 17.741
145 | 136.586 | 138.568 | 139.469 | 138.208 | 134.965 | 132.622 | 133.883 | 164.156 | 166.318 | 167.039 | 167.94 | 167.399 | 167.76 | 163.976 | 162.714 | 162.895 | 164.156 | 164.696 | 162.174 | 162.534 | 164.516 | 166.859 | 165.958 | 167.219
145 | 1.115 | 1.123 | 1.078 | 1.036 | 0.981 | 0.907 | 0.814 | 0.643 | 0.338 | 0.177 | 0.117 | 0.122 | 0.206 | 0.308 | 0.35 | 0.47 | 0.709 | 0.972 | 1.281 | 1.408 | 1.519 | 1.596 | 1.468 | 1.337
146 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072 | 1.114 | 3.307 | 5.141 | 6.489 | 7.388 | 7.909 | 8.053 | 7.927 | 7.459 | 6.669 | 5.464 | 3.595 | 1.474 | 0.198 | 0 | 0 | 0
147 | 1.66 | 1.684 | 1.695 | 1.68 | 1.64 | 1.612 | 1.627 | 1.995 | 2.021 | 2.03 | 2.041 | 2.034 | 2.039 | 1.993 | 1.977 | 1.98 | 1.995 | 2.002 | 1.971 | 1.975 | 1.999 | 2.028 | 2.017 | 2.032
147 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.314 | 0.932 | 1.448 | 1.828 | 2.081 | 2.228 | 2.268 | 2.233 | 2.101 | 1.878 | 1.539 | 1.013 | 0.415 | 0.056 | 0 | 0 | 0
149 | 0.373 | 0.378 | 0.38 | 0.377 | 0.368 | 0.362 | 0.365 | 0.448 | 0.454 | 0.456 | 0.458 | 0.457 | 0.458 | 0.447 | 0.444 | 0.444 | 0.448 | 0.449 | 0.442 | 0.443 | 0.449 | 0.455 | 0.453 | 0.456
149 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066 | 1.02 | 3.028 | 4.706 | 5.941 | 6.763 | 7.241 | 7.372 | 7.257 | 6.829 | 6.105 | 5.003 | 3.291 | 1.349 | 0.181 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 17.819 | 18.077 | 18.195 | 18.03 | 17.607 | 17.301 | 17.466 | 21.415 | 21.697 | 21.791 | 21.909 | 21.838 | 21.885 | 21.392 | 21.227 | 21.251 | 21.415 | 21.486 | 21.157 | 21.204 | 21.462 | 21.768 | 21.65 | 21.815
150 | 8.238 | 8.292 | 7.96 | 7.649 | 7.242 | 6.696 | 6.01 | 4.746 | 2.496 | 1.307 | 0.868 | 0.9 | 1.521 | 2.271 | 2.582 | 3.471 | 5.239 | 7.178 | 9.46 | 10.402 | 11.217 | 11.784 | 10.842 | 9.877
150 | 0.149 | 0.149 | 0.149 | 0.164 | 0.157 | 0.149 | 0.194 | 0.164 | 0.224 | 0.358 | 0.396 | 0.448 | 0.418 | 0.366 | 0.299 | 0.261 | 0.299 | 0.276 | 0.276 | 0.284 | 0.351 | 0.343 | 0.261 | 0.179
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 1.884 | 5.59 | 8.689 | 10.967 | 12.486 | 13.367 | 13.61 | 13.397 | 12.608 | 11.271 | 9.235 | 6.076 | 2.491 | 0.334 | 0 | 0 | 0
151 | 9.146 | 9.279 | 9.339 | 9.255 | 9.038 | 8.881 | 8.965 | 10.993 | 11.137 | 11.186 | 11.246 | 11.21 | 11.234 | 10.981 | 10.896 | 10.908 | 10.993 | 11.029 | 10.86 | 10.884 | 11.017 | 11.174 | 11.113 | 11.198
151 | 0.307 | 0.307 | 0.307 | 0.338 | 0.323 | 0.307 | 0.399 | 0.338 | 0.461 | 0.737 | 0.814 | 0.922 | 0.86 | 0.753 | 0.615 | 0.538 | 0.615 | 0.568 | 0.568 | 0.584 | 0.722 | 0.707 | 0.538 | 0.369
152 | 8.638 | 8.764 | 8.821 | 8.741 | 8.536 | 8.388 | 8.467 | 10.382 | 10.519 | 10.564 | 10.621 | 10.587 | 10.61 | 10.37 | 10.291 | 10.302 | 10.382 | 10.416 | 10.257 | 10.279 | 10.405 | 10.553 | 10.496 | 10.576
152 | 13.036 | 13.121 | 12.595 | 12.104 | 11.46 | 10.595 | 9.51 | 7.51 | 3.95 | 2.068 | 1.373 | 1.424 | 2.407 | 3.594 | 4.085 | 5.492 | 8.29 | 11.358 | 14.969 | 16.461 | 17.749 | 18.647 | 17.156 | 15.63
152 | 0.758 | 0.758 | 0.758 | 0.834 | 0.796 | 0.758 | 0.985 | 0.834 | 1.137 | 1.819 | 2.009 | 2.274 | 2.123 | 1.857 | 1.516 | 1.327 | 1.516 | 1.402 | 1.402 | 1.44 | 1.781 | 1.744 | 1.327 | 0.91
152 | 0.919 | 0.919 | 0.919 | 1.011 | 0.965 | 0.919 | 1.195 | 1.011 | 1.378 | 2.205 | 2.435 | 2.757 | 2.573 | 2.251 | 1.838 | 1.608 | 1.838 | 1.7 | 1.7 | 1.746 | 2.159 | 2.113 | 1.608 | 1.103
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.008 | 0.023 | 0.036 | 0.046 | 0.052 | 0.056 | 0.057 | 0.056 | 0.053 | 0.047 | 0.038 | 0.025 | 0.01 | 0.001 | 0 | 0 | 0
153 | 0.578 | 0.582 | 0.558 | 0.537 | 0.508 | 0.47 | 0.422 | 0.333 | 0.175 | 0.092 | 0.061 | 0.063 | 0.107 | 0.159 | 0.181 | 0.243 | 0.367 | 0.503 | 0.664 | 0.73 | 0.787 | 0.827 | 0.761 | 0.693
153 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.008 | 0.023 | 0.036 | 0.046 | 0.052 | 0.056 | 0.057 | 0.056 | 0.053 | 0.047 | 0.038 | 0.025 | 0.01 | 0.001 | 0 | 0 | 0
154 | 1.389 | 1.409 | 1.418 | 1.405 | 1.372 | 1.349 | 1.361 | 1.669 | 1.691 | 1.699 | 1.708 | 1.702 | 1.706 | 1.667 | 1.655 | 1.656 | 1.669 | 1.675 | 1.649 | 1.653 | 1.673 | 1.697 | 1.688 | 1.7
154 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0.133 | 0.396 | 0.615 | 0.777 | 0.884 | 0.947 | 0.964 | 0.949 | 0.893 | 0.798 | 0.654 | 0.43 | 0.176 | 0.024 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0.102 | 0.103 | 0.104 | 0.103 | 0.1 | 0.099 | 0.1 | 0.122 | 0.124 | 0.124 | 0.125 | 0.125 | 0.125 | 0.122 | 0.121 | 0.121 | 0.122 | 0.123 | 0.121 | 0.121 | 0.122 | 0.124 | 0.123 | 0.124
155 | 34.687 | 34.913 | 33.514 | 32.206 | 30.492 | 28.192 | 25.305 | 19.982 | 10.51 | 5.503 | 3.654 | 3.789 | 6.405 | 9.563 | 10.871 | 14.615 | 22.057 | 30.221 | 39.829 | 43.799 | 47.227 | 49.617 | 45.648 | 41.588
155 | 0.569 | 0.569 | 0.569 | 0.625 | 0.597 | 0.569 | 0.739 | 0.625 | 0.853 | 1.365 | 1.507 | 1.706 | 1.592 | 1.393 | 1.137 | 0.995 | 1.137 | 1.052 | 1.052 | 1.08 | 1.336 | 1.308 | 0.995 | 0.682
156 | 31.018 | 31.22 | 29.969 | 28.8 | 27.267 | 25.21 | 22.628 | 17.869 | 9.398 | 4.921 | 3.267 | 3.388 | 5.728 | 8.551 | 9.721 | 13.069 | 19.724 | 27.025 | 35.616 | 39.166 | 42.231 | 44.369 | 40.82 | 37.189
156 | 0.267 | 0.267 | 0.267 | 0.294 | 0.28 | 0.267 | 0.347 | 0.294 | 0.401 | 0.641 | 0.708 | 0.801 | 0.748 | 0.654 | 0.534 | 0.467 | 0.534 | 0.494 | 0.494 | 0.507 | 0.628 | 0.614 | 0.467 | 0.32
157 | 6.03 | 6.117 | 6.157 | 6.101 | 5.958 | 5.855 | 5.911 | 7.247 | 7.342 | 7.374 | 7.414 | 7.39 | 7.406 | 7.239 | 7.183 | 7.191 | 7.247 | 7.271 | 7.159 | 7.175 | 7.263 | 7.366 | 7.327 | 7.382
158 | 0.949 | 0.962 | 0.969 | 0.96 | 0.937 | 0.921 | 0.93 | 1.14 | 1.155 | 1.16 | 1.166 | 1.162 | 1.165 | 1.139 | 1.13 | 1.131 | 1.14 | 1.144 | 1.126 | 1.129 | 1.142 | 1.159 | 1.152 | 1.161
158 | 8.413 | 8.468 | 8.129 | 7.811 | 7.396 | 6.838 | 6.137 | 4.847 | 2.549 | 1.335 | 0.886 | 0.919 | 1.554 | 2.319 | 2.637 | 3.545 | 5.35 | 7.33 | 9.66 | 10.623 | 11.454 | 12.034 | 11.072 | 10.087
159 | 2.405 | 2.44 | 2.456 | 2.434 | 2.377 | 2.335 | 2.358 | 2.891 | 2.929 | 2.941 | 2.957 | 2.948 | 2.954 | 2.887 | 2.865 | 2.868 | 2.891 | 2.9 | 2.856 | 2.862 | 2.897 | 2.938 | 2.922 | 2.945
159 | 22.524 | 22.671 | 21.763 | 20.913 | 19.8 | 18.307 | 16.432 | 12.976 | 6.825 | 3.573 | 2.373 | 2.46 | 4.159 | 6.21 | 7.059 | 9.49 | 14.323 | 19.625 | 25.863 | 28.441 | 30.667 | 32.22 | 29.642 | 27.006
159 | 0.066 | 0.066 | 0.066 | 0.073 | 0.069 | 0.066 | 0.086 | 0.073 | 0.099 | 0.159 | 0.175 | 0.198 | 0.185 | 0.162 | 0.132 | 0.116 | 0.132 | 0.122 | 0.122 | 0.125 | 0.155 | 0.152 | 0.116 | 0.079
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0.345 | 1.025 | 1.593 | 2.011 | 2.289 | 2.451 | 2.495 | 2.456 | 2.311 | 2.066 | 1.693 | 1.114 | 0.457 | 0.061 | 0 | 0 | 0
160 | 8.909 | 9.039 | 9.097 | 9.015 | 8.803 | 8.651 | 8.733 | 10.708 | 10.849 | 10.896 | 10.954 | 10.919 | 10.943 | 10.696 | 10.614 | 10.625 | 10.708 | 10.743 | 10.578 | 10.602 | 10.731 | 10.884 | 10.825 | 10.907
160 | 25.911 | 26.08 | 25.035 | 24.058 | 22.777 | 21.059 | 18.903 | 14.927 | 7.851 | 4.111 | 2.729 | 2.83 | 4.785 | 7.143 | 8.12 | 10.917 | 16.477 | 22.575 | 29.752 | 32.717 | 35.278 | 37.064 | 34.099 | 31.066
160 | 1.576 | 1.576 | 1.576 | 1.734 | 1.655 | 1.576 | 2.049 | 1.734 | 2.365 | 3.783 | 4.178 | 4.729 | 4.414 | 3.862 | 3.153 | 2.759 | 3.153 | 2.916 | 2.916 | 2.995 | 3.705 | 3.626 | 2.759 | 1.892
161 | 30.05 | 30.246 | 29.034 | 27.901 | 26.416 | 24.423 | 21.922 | 17.311 | 9.105 | 4.767 | 3.165 | 3.282 | 5.549 | 8.284 | 9.418 | 12.661 | 19.109 | 26.182 | 34.505 | 37.944 | 40.914 | 42.985 | 39.546 | 36.029
162 | 19.885 | 20.174 | 20.305 | 20.121 | 19.649 | 19.308 | 19.491 | 23.899 | 24.213 | 24.318 | 24.45 | 24.371 | 24.423 | 23.872 | 23.689 | 23.715 | 23.899 | 23.977 | 23.61 | 23.663 | 23.951 | 24.292 | 24.161 | 24.345
162 | 5.685 | 5.722 | 5.493 | 5.278 | 4.997 | 4.62 | 4.147 | 3.275 | 1.722 | 0.902 | 0.599 | 0.621 | 1.05 | 1.567 | 1.782 | 2.395 | 3.615 | 4.953 | 6.528 | 7.178 | 7.74 | 8.132 | 7.481 | 6.816
162 | 0.08 | 0.08 | 0.08 | 0.088 | 0.084 | 0.08 | 0.105 | 0.088 | 0.121 | 0.193 | 0.213 | 0.241 | 0.225 | 0.197 | 0.161 | 0.141 | 0.161 | 0.149 | 0.149 | 0.153 | 0.189 | 0.185 | 0.141 | 0.096
163 | 29.002 | 29.191 | 28.022 | 26.928 | 25.495 | 23.571 | 21.158 | 16.707 | 8.787 | 4.601 | 3.055 | 3.168 | 5.355 | 7.995 | 9.089 | 12.219 | 18.442 | 25.268 | 33.302 | 36.62 | 39.487 | 41.485 | 38.167 | 34.772
163 | 0.192 | 0.192 | 0.192 | 0.212 | 0.202 | 0.192 | 0.25 | 0.212 | 0.289 | 0.462 | 0.51 | 0.577 | 0.539 | 0.471 | 0.385 | 0.337 | 0.385 | 0.356 | 0.356 | 0.366 | 0.452 | 0.442 | 0.337 | 0.231
164 | 0.376 | 0.376 | 0.376 | 0.414 | 0.395 | 0.376 | 0.489 | 0.414 | 0.564 | 0.903 | 0.997 | 1.128 | 1.053 | 0.922 | 0.752 | 0.658 | 0.752 | 0.696 | 0.696 | 0.715 | 0.884 | 0.865 | 0.658 | 0.451
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0.233 | 3.61 | 10.714 | 16.653 | 21.02 | 23.932 | 25.62 | 26.086 | 25.678 | 24.165 | 21.603 | 17.701 | 11.646 | 4.775 | 0.641 | 0 | 0 | 0
165 | 10.026 | 10.091 | 9.687 | 9.309 | 8.813 | 8.148 | 7.314 | 5.776 | 3.038 | 1.591 | 1.056 | 1.095 | 1.851 | 2.764 | 3.142 | 4.224 | 6.375 | 8.735 | 11.512 | 12.659 | 13.65 | 14.341 | 13.194 | 12.02
165 | 0.594 | 0.594 | 0.594 | 0.654 | 0.624 | 0.594 | 0.773 | 0.654 | 0.892 | 1.427 | 1.575 | 1.783 | 1.664 | 1.456 | 1.189 | 1.04 | 1.189 | 1.1 | 1.1 | 1.129 | 1.397 | 1.367 | 1.04 | 0.713
166 | 6.47 | 6.564 | 6.607 | 6.547 | 6.393 | 6.282 | 6.342 | 7.776 | 7.879 | 7.913 | 7.955 | 7.93 | 7.947 | 7.768 | 7.708 | 7.716 | 7.776 | 7.802 | 7.682 | 7.699 | 7.793 | 7.904 | 7.862 | 7.921
166 | 31.488 | 31.693 | 30.424 | 29.236 | 27.68 | 25.592 | 22.971 | 18.14 | 9.541 | 4.996 | 3.317 | 3.44 | 5.815 | 8.681 | 9.868 | 13.267 | 20.023 | 27.435 | 36.156 | 39.76 | 42.872 | 45.042 | 41.439 | 37.753
166 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.016 | 0.047 | 0.072 | 0.091 | 0.104 | 0.111 | 0.113 | 0.112 | 0.105 | 0.094 | 0.077 | 0.051 | 0.021 | 0.003 | 0 | 0 | 0
167 | 0.305 | 0.309 | 0.311 | 0.309 | 0.301 | 0.296 | 0.299 | 0.366 | 0.371 | 0.373 | 0.375 | 0.374 | 0.374 | 0.366 | 0.363 | 0.364 | 0.366 | 0.368 | 0.362 | 0.363 | 0.367 | 0.372 | 0.37 | 0.373
167 | 15.643 | 15.745 | 15.115 | 14.525 | 13.752 | 12.714 | 11.412 | 9.012 | 4.74 | 2.482 | 1.648 | 1.709 | 2.889 | 4.313 | 4.903 | 6.591 | 9.948 | 13.63 | 17.962 | 19.753 | 21.299 | 22.377 | 20.587 | 18.756
167 | 1.06 | 1.06 | 1.06 | 1.166 | 1.113 | 1.06 | 1.377 | 1.166 | 1.589 | 2.543 | 2.808 | 3.179 | 2.967 | 2.596 | 2.119 | 1.854 | 2.119 | 1.96 | 1.96 | 2.013 | 2.49 | 2.437 | 1.854 | 1.272
168 | 1.558 | 1.581 | 1.591 | 1.577 | 1.54 | 1.513 | 1.527 | 1.873 | 1.897 | 1.906 | 1.916 | 1.91 | 1.914 | 1.871 | 1.856 | 1.858 | 1.873 | 1.879 | 1.85 | 1.854 | 1.877 | 1.904 | 1.893 | 1.908
169 | 20.508 | 20.642 | 19.815 | 19.042 | 18.028 | 16.668 | 14.961 | 11.814 | 6.214 | 3.254 | 2.16 | 2.24 | 3.787 | 5.654 | 6.427 | 8.641 | 13.041 | 17.868 | 23.549 | 25.896 | 27.922 | 29.336 | 26.989 | 24.589
169 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033 | 0.518 | 1.537 | 2.389 | 3.016 | 3.434 | 3.676 | 3.743 | 3.684 | 3.467 | 3.099 | 2.54 | 1.671 | 0.685 | 0.092 | 0 | 0 | 0
170 | 12.525 | 12.607 | 12.102 | 11.63 | 11.011 | 10.18 | 9.138 | 7.216 | 3.795 | 1.987 | 1.319 | 1.368 | 2.313 | 3.453 | 3.925 | 5.277 | 7.965 | 10.913 | 14.382 | 15.816 | 17.054 | 17.917 | 16.483 | 15.018
170 | 0.103 | 0.103 | 0.103 | 0.114 | 0.109 | 0.103 | 0.134 | 0.114 | 0.155 | 0.248 | 0.274 | 0.31 | 0.289 | 0.253 | 0.207 | 0.181 | 0.207 | 0.191 | 0.191 | 0.196 | 0.243 | 0.238 | 0.181 | 0.124
171 | 0.017 | 0.017 | 0.017 | 0.019 | 0.018 | 0.017 | 0.022 | 0.019 | 0.026 | 0.041 | 0.046 | 0.052 | 0.048 | 0.042 | 0.034 | 0.03 | 0.034 | 0.032 | 0.032 | 0.033 | 0.04 | 0.04 | 0.03 | 0.021
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0.942 | 2.795 | 4.344 | 5.484 | 6.243 | 6.684 | 6.805 | 6.699 | 6.304 | 5.635 | 4.618 | 3.038 | 1.246 | 0.167 | 0 | 0 | 0
172 | 7.203 | 7.25 | 6.96 | 6.688 | 6.332 | 5.855 | 5.255 | 4.15 | 2.183 | 1.143 | 0.759 | 0.787 | 1.33 | 1.986 | 2.258 | 3.035 | 4.581 | 6.276 | 8.271 | 9.096 | 9.808 | 10.304 | 9.48 | 8.637
172 | 0.948 | 0.948 | 0.948 | 1.042 | 0.995 | 0.948 | 1.232 | 1.042 | 1.421 | 2.274 | 2.511 | 2.843 | 2.653 | 2.322 | 1.895 | 1.658 | 1.895 | 1.753 | 1.753 | 1.8 | 2.227 | 2.179 | 1.658 | 1.137
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 45 | 45 | 43 | 43 | 40 | 31 | 0 | 0 | 0 | 0 | 0 | 30 | 31 | 44 | 43 | 27 | 48
175 | 41 | 40 | 0 | 0 | 0 | 29 | 43 | 45 | 45 | 43 | 43 | 40 | 35 | 37 | 27 | 0 | 0 | 0 | 31 | 31 | 44 | 44 | 0 | 47
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 39 | 35 | 35 | 35 | 45 | 41 | 32 | 53
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 39 | 34 | 34 | 34 | 59 | 58 | 0 | 51
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5 | 36 | 33 | 37 | 29 | 25 | 27 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 23 | 25 | 26 | 0 | 0 | 0 | 37 | 29 | 25 | 28 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 75 | 90 | 90 | 60 | 91 | 84 | 90 | 93 | 89 | 90 | 90 | 93 | 64 | 92 | 87 | 0 | 85
182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 89 | 89 | 59 | 90 | 83 | 90 | 91 | 89 | 89 | 89 | 91 | 63 | 90 | 84 | 0 | 85
183 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 268 | 285 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
187 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 48 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 52 | 38 | 42 | 26.5 | 52
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 31 | 30 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 60 | 60 | 60 | 58.5 | 60 | 60 | 52 | 50 | 50 | 30 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 56 | 42 | 43 | 40 | 58 | 79 | 0 | 0 | 0 | 46 | 70
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 41 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 61 | 60 | 60 | 60 | 65
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 42 | 48 | 43 | 80 | 64 | 40 | 40 | 40 | 40 | 40 | 59 | 61 | 60 | 60 | 60 | 63
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 65 | 0 | 0 | 79 | 89 | 0 | 0 | 0 | 63 | 80 | 80 | 0 | 0 | 0 | 0 | 78
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 67 | 84 | 0 | 79 | 80 | 86 | 58 | 0 | 63 | 82 | 83 | 67 | 83 | 79 | 0 | 76
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 42 | 0 | 0 | 0 | 31 | 33 | 38 | 38 | 40 | 37 | 38
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 37 | 37 | 40 | 37 | 37
198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 61 | 58 | 34 | 33 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 59 | 59 | 59 | 62 | 57 | 60 | 57 | 60 | 60 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 59 | 60 | 60 | 59 | 59 | 59 | 59 | 58.5 | 63 | 58 | 61 | 57 | 61 | 62 | 42 | 60
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0
206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 49 | 49 | 40 | 67 | 44 | 34 | 34 | 33.5 | 40 | 65 | 66 | 45 | 39 | 51 | 46 | 44
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 39 | 51 | 48 | 46
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 296 | 303 | 300 | 299 | 298 | 298 | 301 | 300 | 301 | 304 | 305 | 307 | 309 | 311 | 257 | 0
220 | 0 | 0 | 0 | 0 | 0 | 199 | 290 | 242 | 297 | 303 | 300 | 299 | 299 | 299 | 302 | 302 | 302 | 304 | 305 | 306 | 309 | 311 | 257 | 236
220 | 313 | 313 | 310 | 312 | 314 | 199 | 292 | 241 | 296 | 302 | 299 | 298 | 298 | 298 | 301 | 301 | 301 | 303 | 304 | 307 | 308 | 310 | 257 | 235
222 | 348 | 253 | 236 | 237 | 236 | 236 | 294 | 344 | 354 | 349 | 345 | 335 | 331 | 330 | 321 | 319 | 315 | 321 | 326 | 334 | 340 | 343 | 335 | 264
225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 129 | 123 | 131 | 160 | 120 | 0 | 0 | 0 | 138 | 169 | 190 | 126 | 140 | 171 | 0 | 116
227 | 60 | 60 | 0 | 0 | 0 | 0 | 83 | 91 | 108 | 108 | 107 | 107 | 107 | 65 | 89 | 106 | 106 | 106 | 106 | 113 | 100 | 0 | 0 | 0
227 | 60 | 0 | 0 | 0 | 0 | 0 | 82 | 90 | 105 | 105 | 105 | 105 | 104 | 0 | 87 | 103 | 104 | 103 | 103 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 195 | 195 | 201 | 239 | 0 | 0 | 0 | 265 | 201 | 237 | 200 | 198 | 195 | 0 | 293
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 200 | 198 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 187 | 192 | 114 | 122 | 200 | 110 | 0 | 0 | 0 | 0 | 200 | 202 | 165 | 0 | 0 | 200
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 93 | 70 | 100 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 262 | 280 | 193 | 207 | 251 | 191 | 182 | 242 | 165 | 0 | 270 | 202 | 260 | 194 | 157.5 | 255
234 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 268 | 284 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
235 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 268 | 284 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
236 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 268 | 284 | 294 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 294 | 295 | 295
237 | 287 | 287 | 287 | 276 | 256 | 288 | 287 | 287 | 287 | 287 | 287 | 288 | 287 | 287 | 287 | 287 | 286 | 286 | 286 | 286 | 287 | 288 | 288 | 288
238 | 287 | 286 | 286 | 275 | 257 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 285 | 285 | 285 | 285 | 280 | 287 | 287 | 288 | 288 | 288
239 | 349.2096 | 252.6016 | 255.084 | 237.2105 | 246.1388 | 240.9924 | 293.1786 | 344.8868 | 357.0611 | 350.9177 | 348.8797 | 339.2536 | 332.3682 | 340.5514 | 326.1348 | 328.3908 | 327.016 | 333.9275 | 339.15 | 343.9903 | 346.5264 | 347.6734 | 337.0177 | 272.628
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 264 | 248 | 252 | 269 | 278 | 248 | 313 | 352 | 386 | 364 | 367 | 354 | 340 | 360 | 344 | 347 | 345 | 338 | 360 | 357 | 325 | 294 | 371 | 315
242 | 274 | 248 | 252 | 269 | 278 | 248 | 314 | 354 | 387 | 365 | 368 | 355 | 341 | 362 | 343 | 346 | 346 | 339 | 361 | 358 | 326 | 295 | 0 | 317
243 | 259 | 261 | 288 | 256 | 281 | 263 | 390 | 327 | 338 | 341 | 344 | 328 | 308 | 334 | 315 | 317 | 315 | 317 | 325 | 329 | 308 | 311 | 306 | 379
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 334 | 330 | 332 | 320 | 307 | 326 | 312 | 314 | 313 | 313 | 324 | 328 | 306 | 310 | 306 | 0
250 | 17.073 | 17.321 | 17.434 | 17.276 | 16.871 | 16.578 | 16.735 | 20.519 | 20.79 | 20.88 | 20.992 | 20.925 | 20.97 | 20.497 | 20.339 | 20.362 | 20.519 | 20.587 | 20.272 | 20.317 | 20.565 | 20.857 | 20.745 | 20.902
251 | 15.321 | 15.42 | 14.803 | 14.225 | 13.468 | 12.452 | 11.177 | 8.826 | 4.642 | 2.431 | 1.614 | 1.674 | 2.829 | 4.224 | 4.801 | 6.455 | 9.742 | 13.348 | 17.592 | 19.345 | 20.859 | 21.915 | 20.162 | 18.369
252 | 24.271 | 24.429 | 23.451 | 22.536 | 21.336 | 19.726 | 17.707 | 13.982 | 7.354 | 3.851 | 2.557 | 2.651 | 4.482 | 6.691 | 7.607 | 10.226 | 15.434 | 21.147 | 27.87 | 30.647 | 33.046 | 34.719 | 31.941 | 29.101
253 | 16.477 | 16.584 | 15.92 | 15.298 | 14.484 | 13.391 | 12.02 | 9.492 | 4.992 | 2.614 | 1.736 | 1.8 | 3.043 | 4.542 | 5.164 | 6.942 | 10.477 | 14.355 | 18.919 | 20.805 | 22.433 | 23.569 | 21.683 | 19.755
254 | 34.674 | 34.899 | 33.501 | 32.194 | 30.48 | 28.181 | 25.295 | 19.974 | 10.506 | 5.501 | 3.652 | 3.787 | 6.403 | 9.559 | 10.866 | 14.609 | 22.049 | 30.21 | 39.814 | 43.782 | 47.208 | 49.598 | 45.63 | 41.572
255 | 68.7 | 69.697 | 70.15 | 69.515 | 67.884 | 66.706 | 67.34 | 82.566 | 83.654 | 84.017 | 84.47 | 84.198 | 84.379 | 82.476 | 81.841 | 81.932 | 82.566 | 82.838 | 81.57 | 81.751 | 82.748 | 83.926 | 83.473 | 84.107
262 | 32.053 | 32.261 | 30.969 | 29.76 | 28.177 | 26.051 | 23.383 | 18.465 | 9.712 | 5.085 | 3.376 | 3.501 | 5.919 | 8.836 | 10.045 | 13.505 | 20.382 | 27.926 | 36.805 | 40.472 | 43.64 | 45.849 | 42.181 | 38.43
263 | 17.874 | 17.991 | 17.27 | 16.596 | 15.713 | 14.527 | 13.04 | 10.297 | 5.416 | 2.836 | 1.883 | 1.952 | 3.301 | 4.928 | 5.602 | 7.531 | 11.366 | 15.573 | 20.524 | 22.57 | 24.336 | 25.568 | 23.523 | 21.431
264 | 36.972 | 37.212 | 35.722 | 34.327 | 32.5 | 30.048 | 26.972 | 21.298 | 11.202 | 5.865 | 3.894 | 4.039 | 6.827 | 10.192 | 11.587 | 15.577 | 23.51 | 32.212 | 42.453 | 46.683 | 50.337 | 52.885 | 48.655 | 44.328
265 | 14.703 | 14.798 | 14.206 | 13.651 | 12.925 | 11.949 | 10.726 | 8.47 | 4.455 | 2.333 | 1.549 | 1.606 | 2.715 | 4.053 | 4.608 | 6.195 | 9.349 | 12.81 | 16.882 | 18.565 | 20.018 | 21.031 | 19.349 | 17.628
266 | 18.815 | 18.937 | 18.179 | 17.469 | 16.54 | 15.292 | 13.726 | 10.839 | 5.701 | 2.985 | 1.982 | 2.055 | 3.474 | 5.187 | 5.897 | 7.927 | 11.964 | 16.393 | 21.604 | 23.757 | 25.617 | 26.914 | 24.761 | 22.559
267 | 24.191 | 24.348 | 23.373 | 22.461 | 21.265 | 19.661 | 17.648 | 13.936 | 7.33 | 3.838 | 2.548 | 2.642 | 4.467 | 6.669 | 7.581 | 10.192 | 15.383 | 21.077 | 27.777 | 30.545 | 32.936 | 34.603 | 31.835 | 29.004
268 | 21.019 | 21.156 | 20.308 | 19.516 | 18.477 | 17.083 | 15.334 | 12.109 | 6.369 | 3.335 | 2.214 | 2.296 | 3.881 | 5.795 | 6.587 | 8.856 | 13.366 | 18.313 | 24.135 | 26.54 | 28.618 | 30.066 | 27.661 | 25.201
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 30 | 30 | 22 | 21.5 | 32 | 39 | 21 | 22 | 0 | 0 | 0 | 25
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen Q (Mvar)
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
1 | -34.1118 | -36.066 | -37.8633 | -38.615 | -39.0229 | -39.565 | -39.2773 | -36.4009 | -35.1566 | -33.6785 | -33.2773 | -36.5505 | -36.3776 | -33.2893 | -29.4443 | -28.2765 | -35.8546 | -32.5195 | -33.7006 | -35.6036 | -36.5703 | -34.8854 | -35.7162 | -38.9583
2 | -70.4091 | -79.1766 | -79.6274 | -79.3129 | -78.9556 | -79.0157 | -76.3007 | -51.3934 | -51.0542 | -53.5264 | -52.6099 | -42.6931 | -45.9765 | -47.6402 | -48.9317 | -49.162 | -42.0901 | -38.4323 | -24.4522 | -43.8007 | -45.0765 | -46.201 | -62.8608 | -54.1063
3 | -16.4043 | -20.3973 | -19.3262 | -19.1637 | -18.8555 | -18.3743 | -9.3318 | 30.0756 | 33.971 | 16.9449 | -2.1759 | 4.3981 | 17.6628 | -4.5767 | -14.1482 | -11.9171 | 4.8447 | 1.3354 | 86.5951 | 41.2873 | 47.7374 | 17.4784 | -22.2515 | 17.2478
4 | -40.1191 | -47.1622 | -61.2031 | -61.6054 | -62.0416 | -61.95 | -42.8191 | -43.5716 | -44.3262 | -44.2929 | -44.2665 | -43.6146 | -44.331 | -49.9726 | -44.2931 | -43.593 | -43.6368 | -43.6196 | -43.0316 | -48.7137 | -48.0669 | -52.5166 | -49.3601 | -54.2406
5 | -13.9426 | -14.3125 | -14.5664 | -14.4261 | -14.3994 | -14.5248 | -12.2236 | -10.189 | -9.4885 | -10.1176 | -11.3517 | -9.6007 | -8.9485 | -10.4011 | -11.8078 | -11.3461 | -10.7596 | -10.082 | -5.9312 | -8.0283 | -7.6186 | -9.3749 | -10.5325 | -8.8908
6 | -7.3177 | -7.296 | -7.5629 | -7.6968 | -7.8981 | -7.623 | -6.6672 | -5.827 | -5.7854 | -5.4486 | -5.7352 | -5.238 | -5.0247 | -5.7921 | -6.3138 | -6.1428 | -6.048 | -5.5215 | -4.4903 | -5.1117 | -5.0418 | -5.5967 | -5.2874 | -5.2151
7 | 62.9851 | 52.8524 | 49.3566 | 47.653 | 46.7689 | 47.3305 | 64.1543 | 148.4865 | 173.624 | 147.9066 | 116.54 | 138.2452 | 164.3697 | 114.9483 | 101.6333 | 108.0586 | 145.8511 | 140.9899 | 286.603 | 219.8729 | 227.5925 | 189.7066 | 94.9525 | 162.0909
22 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8393 | 8.128 | 9.8619 | 9.2284 | 8.4365 | 9.198 | 9.742 | 8.3042 | 7.7526 | 8.0351 | 9.1985 | 9.2423 | 11.4873 | 10.6299 | 10.829 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1719 | 10.9491 | 13.2849 | 12.4315 | 11.3647 | 12.3906 | 13.1233 | 11.1865 | 10.4435 | 10.824 | 12.3913 | 12.4502 | 15.4744 | 14.3194 | 14.5876 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415 | 2.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415 | 2.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8742 | -0.18695 | -0.42688 | -0.38261 | 0.14641 | 0.29987 | 0.12041 | 1.3862 | 1.0313 | 0.66583 | 1.0809 | -0.080608 | 0.222 | 0.6693 | -0.077515 | 0.35764 | -0.78126
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14641 | 0.29987 | 0.12041 | 0 | 0 | 0 | 0 | -0.080608 | 0.222 | 0.6693 | -0.077515 | 0.35764 | -0.78126
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.73927 | 0.84535 | 0.77864 | 0.77555 | 0.75227 | 0.79114 | 0.76706 | 0.51833 | 0.65159 | 0.82769 | 0.86264 | 0.89884 | 0.85573 | 0.93349 | 1.141 | 1.183 | 0.89699 | 0.88579 | 0.82543 | 0.83788 | 0.83575 | 0.81362 | 0.77055 | 0.50907
108 | 1.2236 | 1.3992 | 1.2887 | 1.2836 | 1.2451 | 1.3094 | 1.2696 | 0.8579 | 1.0785 | 1.3699 | 1.4278 | 1.4877 | 1.4163 | 1.545 | 1.8884 | 1.9581 | 1.4846 | 1.4661 | 1.3662 | 1.3868 | 1.3833 | 1.3466 | 1.2753 | 0.84257
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 11.1176 | 10.4607 | 10.3796 | 10.1509 | 9.9468 | 9.7794 | 8.2634 | 9.3106 | 7.8178 | 8.4134 | 10.5501 | 10.6453 | 10.5802 | 10.4357 | 10.9007 | 9.5569 | 11.3693 | 11.1158 | 9.234 | 9.0953 | 9.1377 | 9.3167 | 12.0865 | 11.2791
109 | 7.1893 | 6.7645 | 6.712 | 6.5642 | 6.4322 | 6.3239 | 5.3436 | 6.0208 | 5.0555 | 5.4406 | 6.8223 | 6.8839 | 6.8418 | 6.7483 | 7.049 | 6.18 | 7.3521 | 7.1882 | 5.9712 | 5.8815 | 5.9089 | 6.0247 | 7.8159 | 7.2937
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48242 | 0.54356 | 0.45641 | 0.49118 | 0.61592 | 0.62148 | 0.61768 | 0.60924 | 0.63639 | 0.55793 | 0.66375 | 0.64895 | 0.53908 | 0.53099 | 0.53346 | 0 | 0 | 0
110 | -2.2313 | -2.3957 | -2.3704 | -2.2834 | -2.1821 | -2.3365 | -2.2796 | -2.4115 | -1.6792 | -1.5598 | -1.3876 | -1.362 | -1.362 | -1.3427 | -1.1463 | -1.2173 | -1.2932 | -1.3563 | -1.3567 | -1.2272 | -1.3243 | -1.2895 | -2.0359 | -2.1278
111 | 0.013298 | -0.084658 | 0.015068 | -0.00039847 | 0.034056 | -0.04054 | 0.083621 | 0.070959 | 0.13579 | 0.069385 | 0.15111 | -0.00095794 | 0.11319 | -0.040829 | 0.11055 | 0.17647 | 0.097215 | 0.14714 | 0.076307 | 0.10668 | 0.10763 | 0.16835 | 0.078229 | -0.1813
112 | 13.3363 | 7.2527 | 3.0893 | 1.0121 | -0.10375 | 0.6762 | -1.9691 | -2.441 | -5.3638 | 3.1122 | 6.9845 | 9.6108 | 6.2476 | 7.3741 | 17.8631 | 19.9419 | 13.5797 | 11.6078 | 2.2022 | 5.238 | 4.2231 | 11.8096 | 32.0857 | 19.84
112 | 0 | 0 | 0 | 0 | 0 | 0 | -0.24662 | -0.30571 | -0.67177 | 0.38978 | 0.87475 | 1.2037 | 0.78246 | 0.92354 | 2.2372 | 2.4975 | 1.7007 | 1.4538 | 0.27581 | 0.65602 | 0.52891 | 0 | 0 | 0
113 | -0.092162 | 0.071973 | 0.016444 | -0.022587 | 0.011489 | 0.036108 | 0.026359 | 0.039904 | 0.022806 | 0.021089 | 0.011302 | 0.020218 | 0.019706 | -0.0064113 | 0.021482 | 0.0066247 | 0.026479 | 0.027816 | 0.047067 | 0.031877 | 0.038676 | -0.054146 | -0.059052 | 0.080428
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0048 | 3.0351 | 1.7346 | 1.604 | 0.85965 | 1.5378 | 1.4988 | -0.48764 | 1.6339 | 0.50388 | 2.014 | 2.1157 | 3.5799 | 2.4246 | 2.9417 | 0 | 0 | 0
114 | 2.7627 | 2.5164 | 2.3845 | 2.2797 | 2.2225 | 2.2234 | 2.1149 | 2.4212 | 2.6714 | 3.0521 | 3.6111 | 3.3441 | 3.3656 | 3.3744 | 3.5405 | 3.8498 | 3.5338 | 3.3879 | 3.3257 | 3.1851 | 3.0487 | 3.1709 | 3.541 | 3.0469
114 | 12.5963 | 11.4733 | 10.8717 | 10.3939 | 10.1331 | 10.1374 | 9.6425 | 11.0393 | 12.1801 | 13.9158 | 16.4643 | 15.247 | 15.3452 | 15.3852 | 16.1424 | 17.5527 | 16.112 | 15.4468 | 15.1632 | 14.522 | 13.9002 | 14.4573 | 16.1448 | 13.8921
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2.5747 | 2.3451 | 2.2221 | 2.1245 | 2.0712 | 2.0721 | 1.9709 | 2.2564 | 2.4896 | 2.8444 | 3.3653 | 3.1164 | 3.1365 | 3.1447 | 3.2995 | 3.5877 | 3.2933 | 3.1573 | 3.0993 | 2.9682 | 2.8412 | 2.955 | 3.2999 | 2.8395
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31079 | 0.35581 | 0.39258 | 0.44853 | 0.53067 | 0.49143 | 0.4946 | 0.49589 | 0.5203 | 0.56575 | 0.51932 | 0.49788 | 0.48873 | 0.46807 | 0.44803 | 0 | 0 | 0
115 | 0 | 0 | 0 | -0.070286 | -0.18137 | -0.17608 | 0.028022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18367 | 0.18556 | 0.21214 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0 | 0 | 0 | -0.18137 | -0.17608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | -0.02136 | -0.0014102 | -0.011856 | -0.034228 | -0.03933 | -0.039087 | -0.029713 | -0.0035654 | -0.013982 | -0.010169 | -0.0087943 | 0.00080552 | -0.0066499 | -0.019441 | -0.022565 | -0.022478 | -0.021257 | -0.0091208 | -0.020804 | -0.014736 | -0.011099 | -0.022408 | -0.013115 | 0.005478
115 | -0.17701 | -0.011686 | -0.098252 | -0.28364 | -0.32592 | -0.3239 | -0.24622 | -0.029545 | -0.11586 | -0.084268 | -0.072876 | 0.0066752 | -0.055106 | -0.1611 | -0.18699 | -0.18627 | -0.17616 | -0.075582 | -0.1724 | -0.12211 | -0.091979 | -0.18569 | -0.10868 | 0.045395
115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 6.1208 | 6.3042 | 5.9099 | 5.789 | 5.6151 | 5.4019 | 3.9749 | 4.7838 | 8.3499 | 9.8676 | 9.9476 | 9.7503 | 8.8238 | 9.485 | 10.7259 | 10.9352 | 9.8681 | 9.7834 | 9.2382 | 8.5653 | 9.1345 | 10.0945 | 7.8886 | 6.6595
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11587 | 0.13945 | 0.2434 | 0.28764 | 0.28997 | 0.28422 | 0.25721 | 0.27649 | 0.31266 | 0.31876 | 0.28766 | 0.28519 | 0.2693 | 0.24968 | 0.26627 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83003 | 0.95385 | 1.1071 | 1.3274 | 1.4297 | 1.4879 | 1.4576 | 1.4417 | 1.7511 | 1.7783 | 1.6302 | 1.5327 | 1.325 | 1.4247 | 1.46 | 0 | 0 | 0
118 | 4.1515 | 4.002 | 3.9391 | 3.8336 | 3.8249 | 3.7399 | 3.72 | 4.06 | 5.0875 | 5.3804 | 5.6672 | 5.698 | 5.632 | 5.6733 | 5.8689 | 6.025 | 5.8772 | 5.7911 | 5.5717 | 5.6382 | 5.4482 | 5.5874 | 5.3073 | 4.5971
118 | 0.13941 | 0.13439 | 0.13228 | 0.12874 | 0.12844 | 0.12559 | 0.12492 | 0.13634 | 0.17084 | 0.18068 | 0.19031 | 0.19134 | 0.18913 | 0.19051 | 0.19708 | 0.20232 | 0.19736 | 0.19447 | 0.1871 | 0.18933 | 0.18296 | 0.18763 | 0.17822 | 0.15437
118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 8.4209 | 8.1176 | 7.9901 | 7.776 | 7.7584 | 7.586 | 7.5457 | 8.2352 | 10.3195 | 10.9136 | 11.4954 | 11.5578 | 11.4239 | 11.5076 | 11.9044 | 12.2211 | 11.9212 | 11.7465 | 11.3015 | 11.4363 | 11.0511 | 11.3335 | 10.7652 | 9.3246
119 | -0.79482 | -0.81501 | -0.80867 | -0.84219 | -0.80315 | -0.85081 | -0.81789 | -0.80227 | -0.54446 | -0.43279 | -0.34452 | -0.2768 | -0.33793 | -0.33196 | -0.22555 | -0.2015 | -0.24294 | -0.25695 | -0.2972 | -0.26893 | -0.30332 | -0.25469 | -0.62902 | -0.72264
119 | -5.5654 | -5.7068 | -5.6623 | -5.897 | -5.6237 | -5.9574 | -5.7269 | -5.6176 | -3.8124 | -3.0304 | -2.4124 | -1.9382 | -2.3662 | -2.3244 | -1.5793 | -1.4109 | -1.7011 | -1.7992 | -2.081 | -1.8831 | -2.1239 | -1.7834 | -4.4044 | -5.06
119 | 0 | 0 | 0 | 0 | 0 | 0 | -0.31461 | -0.30861 | -0.20944 | -0.16648 | -0.13253 | -0.10648 | -0.12999 | -0.1277 | -0.086764 | -0.077511 | -0.093453 | -0.09884 | -0.11432 | -0.10345 | -0.11668 | 0 | 0 | 0
120 | 4.1323 | 3.9242 | 3.7785 | 3.6151 | 3.6824 | 3.6025 | 3.5077 | 3.819 | 4.3101 | 4.5754 | 4.731 | 4.7634 | 4.7008 | 4.6723 | 4.7831 | 4.8795 | 4.8132 | 4.7603 | 4.6065 | 4.6324 | 4.5059 | 4.8389 | 4.7885 | 4.4679
120 | 6.5966 | 6.2643 | 6.0318 | 5.7709 | 5.8784 | 5.7508 | 5.5995 | 6.0965 | 6.8804 | 7.3039 | 7.5523 | 7.6041 | 7.5041 | 7.4585 | 7.6355 | 7.7894 | 7.6836 | 7.599 | 7.3535 | 7.3948 | 7.1929 | 7.7245 | 7.644 | 7.1323
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56141 | 0.61125 | 0.68984 | 0.7323 | 0.7572 | 0.7624 | 0.75238 | 0.7478 | 0.76555 | 0.78098 | 0.77037 | 0.76189 | 0.73728 | 0.74142 | 0.72118 | 0 | 0 | 0
121 | 0.77551 | 0.72269 | 0.80254 | 0.86021 | 0.74378 | 0.76104 | 1.1555 | 1.3394 | 1.416 | 1.3862 | 1.3778 | 1.3877 | 1.4297 | 1.3414 | 1.3512 | 1.4016 | 1.4238 | 1.4253 | 1.5171 | 1.459 | 1.4935 | 1.0597 | 0.8969 | 1.2048
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5546 | 4.1202 | 4.3559 | 4.2643 | 4.2385 | 4.2687 | 4.3981 | 4.1263 | 4.1567 | 4.3115 | 4.38 | 4.3846 | 4.6669 | 4.488 | 4.5943 | 0 | 0 | 0
122 | -0.37275 | -0.36982 | -0.48377 | -0.69642 | -0.75587 | -0.65669 | -0.92727 | -1.0069 | 1.1944 | 1.8937 | 2.4531 | 2.5572 | 2.2004 | 2.4869 | 2.9395 | 2.9553 | 2.6697 | 2.4691 | 2.717 | 2.5711 | 2.4706 | 2.5017 | 1.5853 | 0.45692
122 | -2.5112 | -2.4915 | -3.2592 | -4.6918 | -5.0923 | -4.4241 | -6.2471 | -6.7835 | 8.0466 | 12.758 | 16.5265 | 17.2283 | 14.8239 | 16.7546 | 19.8035 | 19.9102 | 17.9859 | 16.6348 | 18.3049 | 17.3219 | 16.6445 | 16.854 | 10.6806 | 3.0783
122 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0043761 | -0.0047519 | 0.0056367 | 0.0089371 | 0.011577 | 0.012069 | 0.010384 | 0.011737 | 0.013872 | 0.013947 | 0.012599 | 0.011653 | 0.012823 | 0.012134 | 0.01166 | 0 | 0 | 0
123 | -5.9832 | -6.4607 | -6.7013 | -6.6112 | -6.2044 | -6.7503 | -6.0439 | -6.1405 | -4.3927 | -3.175 | -2.582 | -2.1649 | -2.833 | -2.6253 | -1.9271 | -1.6597 | -1.5946 | -1.9506 | -3.1565 | -2.962 | -2.9879 | -2.7498 | -3.249 | -5.4033
123 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5862 | -2.6276 | -1.8797 | -1.3586 | -1.1049 | -0.92638 | -1.2123 | -1.1234 | -0.82463 | -0.7102 | -0.68236 | -0.83468 | -1.3507 | -1.2675 | -1.2786 | 0 | 0 | 0
124 | 0.0050988 | 0.006562 | 0.0039934 | 0.0036858 | 0.0033579 | 0.0035661 | 0.0038296 | 0.0040109 | 0.014636 | 0.01805 | 0.019103 | 0.019101 | 0.019291 | 0.018958 | 0.020979 | 0.021647 | 0.020036 | 0.018797 | 0.020223 | 0.020269 | 0.019659 | 0.020176 | 0.013938 | 0.010886
124 | 11.0778 | 14.2568 | 8.6762 | 8.008 | 7.2955 | 7.7478 | 8.3204 | 8.7142 | 31.7984 | 39.2168 | 41.5047 | 41.5005 | 41.9117 | 41.1891 | 45.5808 | 47.0321 | 43.5302 | 40.8398 | 43.9369 | 44.0378 | 42.7113 | 43.8354 | 30.2823 | 23.6518
124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 0.2629 | 0.17466 | 0.19701 | 0.15983 | 0.28425 | 0.033466 | 0.099654 | 0.27114 | 0.16907 | 0.35061 | 0.32125 | 0.26828 | 0.50969 | 0.41329 | 0.38758 | 0.45612 | 0.2688 | 0.33852 | 0.33206 | 0.39876 | 0.50361 | 0.57645 | 0.12995 | -0.0010452
126 | 0.98059 | 1.1604 | 1.0659 | 1.0233 | 0.92212 | 0.98611 | 0.64934 | 1.1312 | 1.327 | 1.2335 | 1.6067 | 1.6655 | 1.3243 | 1.4394 | 1.3212 | 1.5575 | 1.7515 | 1.7441 | 2.1566 | 1.7515 | 1.7162 | 1.8942 | 1.8015 | 2.0483
126 | 0.55443 | 0.65607 | 0.60265 | 0.57855 | 0.52137 | 0.55755 | 0.36714 | 0.6396 | 0.75029 | 0.6974 | 0.90844 | 0.9417 | 0.74875 | 0.81382 | 0.74698 | 0.88059 | 0.99029 | 0.98614 | 1.2193 | 0.99029 | 0.97036 | 1.071 | 1.0186 | 1.1581
126 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33642 | 0.58609 | 0.68752 | 0.63906 | 0.83244 | 0.86292 | 0.68611 | 0.74574 | 0.68449 | 0.80693 | 0.90744 | 0.90364 | 1.1173 | 0.90744 | 0.88918 | 0 | 0 | 0
127 | 0.015624 | 0.013084 | 0.010996 | 0.0097389 | 0.009996 | 0.0083705 | 0.011234 | 0.015875 | 0.045015 | 0.051583 | 0.055157 | 0.056528 | 0.054481 | 0.055509 | 0.060787 | 0.059798 | 0.055416 | 0.053332 | 0.050375 | 0.050848 | 0.048992 | 0.048368 | 0.028684 | 0.021393
127 | 5.8741 | 4.9194 | 4.1344 | 3.6616 | 3.7583 | 3.1471 | 4.2236 | 5.9686 | 16.9247 | 19.3938 | 20.7377 | 21.2533 | 20.4835 | 20.8699 | 22.8546 | 22.4828 | 20.8352 | 20.0516 | 18.9399 | 19.1177 | 18.4198 | 18.1854 | 10.7846 | 8.0432
127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 0.5167 | 0.43272 | 0.36367 | 0.32208 | 0.33059 | 0.27683 | 0.37152 | 0.52501 | 1.4887 | 1.7059 | 1.8241 | 1.8695 | 1.8018 | 1.8358 | 2.0103 | 1.9776 | 1.8327 | 1.7638 | 1.666 | 1.6816 | 1.6202 | 1.5996 | 0.94863 | 0.7075
128 | 27.046 | 23.5442 | 22.117 | 21.9813 | 21.7773 | 21.9237 | 20.896 | 22.4435 | 33.453 | 35.0011 | 35.1858 | 35.2662 | 35.2976 | 35.5454 | 36.7881 | 37.0479 | 35.9479 | 35.3276 | 34.7353 | 34.6806 | 34.6169 | 35.3879 | 30.4221 | 27.3795
128 | 0.36832 | 0.32063 | 0.3012 | 0.29935 | 0.29657 | 0.29856 | 0.28457 | 0.30564 | 0.45557 | 0.47666 | 0.47917 | 0.48027 | 0.48069 | 0.48407 | 0.50099 | 0.50453 | 0.48955 | 0.4811 | 0.47304 | 0.47229 | 0.47142 | 0.48192 | 0.4143 | 0.37286
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3361 | 0.36099 | 0.53807 | 0.56297 | 0.56594 | 0.56723 | 0.56773 | 0.57172 | 0.59171 | 0.59589 | 0.57819 | 0.56822 | 0.55869 | 0.55781 | 0.55679 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 11.9552 | 11.1722 | 10.7749 | 10.7188 | 10.4335 | 10.4301 | 10.2427 | 11.1067 | 12.2806 | 13.3304 | 13.9973 | 13.5845 | 13.6446 | 13.7389 | 13.9706 | 14.2934 | 13.8859 | 13.4025 | 13.2957 | 13.3021 | 13.0108 | 13.0509 | 13.2724 | 11.9454
129 | 5.7681 | 5.3903 | 5.1986 | 5.1716 | 5.0339 | 5.0323 | 4.9419 | 5.3587 | 5.9251 | 6.4316 | 6.7534 | 6.5542 | 6.5832 | 6.6287 | 6.7405 | 6.8962 | 6.6996 | 6.4664 | 6.4149 | 6.4179 | 6.2774 | 6.2968 | 6.4037 | 5.7634
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 0.18699 | 0.38737 | 0.19442 | 0.42428 | 0.20967 | -0.11741 | 0.28255 | -0.045697 | 0.2159 | 0.29921 | 0.33148 | 0.24593 | 0.41639 | 0.058888 | 0.25286 | 0.23178 | 0.17999 | 0.62779 | 0.29893 | 0.046736 | 0.32931 | 0.18912 | 0.16296 | -0.19417
131 | -15.8698 | -16.0572 | -16.2551 | -16.3451 | -16.4384 | -16.4215 | -15.9187 | -15.9376 | -11.8023 | -8.8978 | -6.8917 | -5.7727 | -7.1104 | -6.4538 | -3.977 | -3.2973 | -4.1975 | -5.5152 | -6.6357 | -6.0325 | -6.791 | -6.0692 | -11.6047 | -14.5648
131 | -11.056 | -11.1865 | -11.3245 | -11.3871 | -11.4522 | -11.4403 | -11.0901 | -11.1032 | -8.2223 | -6.1988 | -4.8013 | -4.0217 | -4.9536 | -4.4961 | -2.7706 | -2.2971 | -2.9243 | -3.8423 | -4.6229 | -4.2027 | -4.7311 | -4.2283 | -8.0846 | -10.1469
131 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4513 | -3.4554 | -2.5589 | -1.9291 | -1.4942 | -1.2516 | -1.5416 | -1.3992 | -0.86225 | -0.71488 | -0.91007 | -1.1958 | -1.4387 | -1.3079 | -1.4724 | 0 | 0 | 0
132 | -0.098717 | -0.013056 | -0.20712 | -0.22901 | -0.27432 | -0.32943 | -0.08673 | -0.079142 | 2.7658 | 3.4416 | 3.6014 | 3.3798 | 3.5069 | 3.527 | 3.6287 | 3.8438 | 3.6624 | 3.0691 | 3.4149 | 3.4208 | 3.3066 | 3.244 | 0.78719 | 0.68577
132 | -0.063929 | -0.0084549 | -0.13413 | -0.14831 | -0.17765 | -0.21334 | -0.056166 | -0.051252 | 1.7912 | 2.2288 | 2.3323 | 2.1888 | 2.271 | 2.2841 | 2.3499 | 2.4892 | 2.3718 | 1.9875 | 2.2115 | 2.2153 | 2.1413 | 2.1008 | 0.50978 | 0.44411
133 | 23.3392 | 22.4015 | 21.4057 | 20.9245 | 20.6663 | 20.9257 | 21.0212 | 22.883 | 27.8321 | 30.0602 | 30.8894 | 31.5682 | 31.096 | 31.2592 | 32.1918 | 32.6176 | 31.9521 | 31.4494 | 30.5857 | 30.5058 | 29.9512 | 30.3507 | 28.8383 | 25.4965
133 | 21.3987 | 20.539 | 19.626 | 19.1848 | 18.948 | 19.1859 | 19.2734 | 20.9805 | 25.5181 | 27.561 | 28.3212 | 28.9436 | 28.5107 | 28.6603 | 29.5154 | 29.9057 | 29.2956 | 28.8347 | 28.0428 | 27.9695 | 27.461 | 27.8273 | 26.4406 | 23.3766
133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 9.3969 | 9.6738 | 8.9137 | 6.9413 | 8.008 | 4.9717 | 7.8041 | 6.8179 | 26.5587 | 30.7779 | 32.972 | 33.3116 | 31.0716 | 32.9159 | 36.0805 | 35.5132 | 34.5017 | 33.4131 | 30.6397 | 31.3337 | 31.7049 | 30.697 | 16.6233 | 10.1882
134 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050419 | 0.044048 | 0.17159 | 0.19884 | 0.21302 | 0.21521 | 0.20074 | 0.21266 | 0.2331 | 0.22944 | 0.2229 | 0.21587 | 0.19795 | 0.20243 | 0.20483 | 0 | 0 | 0
136 | -0.35759 | -0.34951 | -0.20818 | -0.39891 | -0.26008 | -0.4391 | -0.29339 | -0.31995 | -0.17949 | -0.18245 | -0.16677 | -0.11739 | -0.11182 | -0.13145 | -0.16157 | -0.16469 | -0.077149 | -0.16562 | -0.24153 | -0.20347 | -0.14773 | -0.25 | -0.32565 | -0.49952
136 | 0 | 0 | 0 | 0 | 0 | 0 | -0.21731 | -0.23698 | -0.13295 | -0.13514 | -0.12353 | -0.086951 | -0.082822 | -0.097361 | -0.11968 | -0.12198 | -0.057144 | -0.12268 | -0.1789 | -0.15071 | -0.10943 | 0 | 0 | 0
137 | 3.2561 | 3.2027 | 3.1578 | 3.1555 | 3.1684 | 3.1101 | 3.1052 | 2.7482 | 4.3737 | 4.5457 | 4.6991 | 4.5857 | 4.5215 | 4.6328 | 4.8334 | 4.8362 | 4.6801 | 4.5968 | 4.5215 | 4.4861 | 4.4714 | 4.4519 | 3.011 | 2.8088
137 | 4.9879 | 4.9061 | 4.8375 | 4.8339 | 4.8536 | 4.7643 | 4.7568 | 4.2099 | 6.7 | 6.9635 | 7.1986 | 7.0247 | 6.9265 | 7.097 | 7.4042 | 7.4086 | 7.1695 | 7.0418 | 6.9265 | 6.8721 | 6.8497 | 6.8199 | 4.6125 | 4.3028
137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0.31004 | 0.20658 | 0.15138 | 0.21201 | 0.045996 | -0.22262 | 0.16194 | -0.10149 | 0.12858 | 0.098813 | 0.056702 | 0.035365 | 0.13037 | 0.083487 | -0.12023 | 0.21899 | 0.22542 | -0.0045595 | 0.090602 | 0.010393 | 0.010112 | 0.21382 | 0.17996 | 0.063991
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0.174 | -0.10905 | 0.13816 | 0.10617 | 0.060925 | 0.037999 | 0.14007 | 0.089704 | -0.12919 | 0.2353 | 0.24221 | -0.004899 | 0.097349 | 0.011167 | 0.010865 | 0 | 0 | 0
139 | -0.59035 | -0.70498 | -0.74048 | -0.88179 | -0.731 | -0.61045 | -0.61046 | -0.72363 | -0.47243 | -0.26801 | -0.16745 | 0.034266 | -0.14228 | 0.060675 | 0.15652 | -0.12875 | -0.1774 | -0.12041 | -0.21049 | -0.152 | -0.18442 | -0.062337 | -0.42875 | -0.81762
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5867 | 6.6862 | 12.424 | 13.0787 | 13.3381 | 13.5711 | 12.8835 | 12.6712 | 14.8447 | 14.6615 | 14.688 | 14.7214 | 14.3674 | 15.8875 | 16.6248 | 0 | 0 | 0
141 | -0.0063739 | -0.056965 | -0.095849 | -0.16971 | -0.13547 | -0.1471 | -0.17517 | -0.26986 | 0.17822 | 0.46392 | 0.55407 | 0.55892 | 0.52928 | 0.47385 | 0.68039 | 0.77784 | 0.73062 | 0.6088 | 0.39315 | 0.49126 | 0.40677 | 0.5991 | 0.51439 | 0.11762
142 | 0.75334 | 0.59111 | 0.51958 | 0.50433 | 0.48942 | 0.49781 | 0.50278 | 0.65816 | 3.088 | 3.3254 | 3.3727 | 3.4278 | 3.3864 | 3.3873 | 3.5334 | 3.5484 | 3.4586 | 3.384 | 3.2594 | 3.2675 | 3.2221 | 3.2499 | 1.0916 | 0.93177
142 | 4.5158 | 3.5434 | 3.1146 | 3.0232 | 2.9338 | 2.9841 | 3.0139 | 3.9453 | 18.5111 | 19.9337 | 20.2172 | 20.5477 | 20.2996 | 20.3047 | 21.1806 | 21.2708 | 20.7321 | 20.2853 | 19.5385 | 19.5869 | 19.3148 | 19.4812 | 6.5433 | 5.5854
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027026 | 0.0035378 | 0.016599 | 0.017875 | 0.018129 | 0.018425 | 0.018203 | 0.018208 | 0.018993 | 0.019074 | 0.018591 | 0.01819 | 0.017521 | 0.017564 | 0.01732 | 0 | 0 | 0
144 | 0.033104 | 0.025527 | 0.021293 | 0.020521 | 0.019692 | 0.019811 | 0.021972 | 0.027415 | 0.055016 | 0.064591 | 0.070398 | 0.070743 | 0.05322 | 0.056077 | 0.07973 | 0.079104 | 0.072991 | 0.06917 | 0.055819 | 0.05887 | 0.055204 | 0.056936 | 0.046478 | 0.03304
144 | 3.6389 | 2.806 | 2.3405 | 2.2557 | 2.1646 | 2.1776 | 2.4152 | 3.0135 | 6.0475 | 7.0999 | 7.7383 | 7.7762 | 5.85 | 6.164 | 8.764 | 8.6952 | 8.0232 | 7.6032 | 6.1357 | 6.471 | 6.0681 | 6.2584 | 5.1089 | 3.6318
145 | 16.3892 | 15.1388 | 15.2618 | 12.3761 | 13.8022 | 11.8051 | 12.4347 | 12.3742 | 15.5664 | 19.7501 | 25.5645 | 25.9501 | 21.4022 | 23.9581 | 30.5184 | 30.5567 | 25.9238 | 24.8835 | 24.7789 | 23.8195 | 22.0623 | 21.2472 | 20.6413 | 16.7585
145 | 0.33739 | 0.31165 | 0.31418 | 0.25477 | 0.28413 | 0.24302 | 0.25598 | 0.25474 | 0.32045 | 0.40658 | 0.52627 | 0.53421 | 0.44059 | 0.4932 | 0.62825 | 0.62904 | 0.53367 | 0.51225 | 0.5101 | 0.49035 | 0.45417 | 0.4374 | 0.42492 | 0.34499
146 | 0 | 0 | 0 | 0 | 0 | 0 | 0.306 | 1.014 | 1.5727 | 1.3938 | 1.1444 | 1.3124 | 1.5483 | 1.0465 | 1.0138 | 1.0691 | 1.4868 | 1.3613 | 2.4071 | 2.0626 | 2.0401 | 0 | 0 | 0
147 | -0.075336 | -0.13189 | -0.08497 | -0.084532 | -0.061323 | -0.1588 | -0.10876 | -0.13008 | -0.10859 | -0.07546 | -0.01037 | -0.060767 | -0.054718 | -0.035615 | -0.020319 | -0.038644 | -0.034975 | -0.020904 | -0.072598 | -0.047381 | -0.045544 | -0.06846 | -0.080488 | -0.069695
147 | 0 | 0 | 0 | 0 | 0 | 0 | -0.088764 | -0.10616 | -0.08862 | -0.061585 | -0.008463 | -0.049593 | -0.044656 | -0.029066 | -0.016583 | -0.031538 | -0.028544 | -0.01706 | -0.059249 | -0.038668 | -0.037169 | 0 | 0 | 0
149 | 0.0024675 | 0.063463 | -0.016594 | -0.032113 | 0.080896 | -0.042952 | 0.19254 | 0.21442 | 0.22726 | 0.23622 | 0.22629 | 0.22991 | 0.23237 | 0.22635 | 0.22774 | 0.237 | 0.24059 | 0.22736 | 0.23994 | 0.23983 | 0.24145 | 0.018413 | 0.077503 | 0.027682
149 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2784 | 2.5373 | 2.6893 | 2.7953 | 2.6777 | 2.7206 | 2.7497 | 2.6785 | 2.6949 | 2.8045 | 2.8469 | 2.6904 | 2.8393 | 2.838 | 2.8571 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 1.6578 | 1.2548 | 1.1225 | 1.1043 | 1.0703 | 1.0943 | 1.063 | 2.0042 | 2.9208 | 2.8486 | 2.8456 | 2.7219 | 3.0027 | 2.4712 | 2.7651 | 2.6547 | 2.7157 | 2.9046 | 3.8133 | 3.1861 | 3.1564 | 2.9561 | 1.6635 | 2.4177
150 | 1.9321 | 1.4624 | 1.3083 | 1.2871 | 1.2474 | 1.2754 | 1.2388 | 2.3358 | 3.404 | 3.3198 | 3.3164 | 3.1722 | 3.4995 | 2.8801 | 3.2225 | 3.0939 | 3.165 | 3.3852 | 4.4442 | 3.7133 | 3.6786 | 3.4452 | 1.9388 | 2.8177
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48501 | 0.9145 | 1.3327 | 1.2997 | 1.2984 | 1.2419 | 1.3701 | 1.1276 | 1.2617 | 1.2113 | 1.2391 | 1.3253 | 1.7399 | 1.4538 | 1.4402 | 0 | 0 | 0
151 | 4.9241 | 4.872 | 4.6171 | 4.5068 | 4.564 | 4.5485 | 4.7324 | 4.8838 | 5.0983 | 5.4464 | 5.5043 | 5.4246 | 5.5159 | 5.603 | 5.772 | 5.6179 | 5.6601 | 5.4794 | 5.4954 | 5.5715 | 5.4997 | 5.437 | 5.3581 | 4.9245
151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 1.572 | 1.4438 | 1.3886 | 1.3269 | 1.324 | 1.3256 | 1.2545 | 1.4377 | 2.0379 | 2.1919 | 2.4588 | 2.3102 | 2.2759 | 2.2953 | 2.5138 | 2.4951 | 2.3588 | 2.2901 | 2.3168 | 2.1931 | 2.1666 | 2.0455 | 1.7133 | 1.6541
152 | 5.9796 | 5.492 | 5.2823 | 5.0475 | 5.0364 | 5.0423 | 4.7718 | 5.4687 | 7.7519 | 8.3377 | 9.3532 | 8.7879 | 8.6573 | 8.7312 | 9.5622 | 9.4909 | 8.9728 | 8.7112 | 8.8127 | 8.3422 | 8.2415 | 7.7809 | 6.5172 | 6.292
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 1.9726 | 1.8117 | 1.7425 | 1.6651 | 1.6614 | 1.6633 | 1.5741 | 1.804 | 2.5572 | 2.7504 | 3.0854 | 2.899 | 2.8558 | 2.8802 | 3.1544 | 3.1308 | 2.9599 | 2.8736 | 2.9071 | 2.7519 | 2.7187 | 2.5668 | 2.1499 | 2.0756
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049451 | 0.0056673 | 0.0080334 | 0.0086405 | 0.0096928 | 0.009107 | 0.0089716 | 0.0090482 | 0.0099094 | 0.0098355 | 0.0092986 | 0.0090275 | 0.0091327 | 0.0086451 | 0.0085408 | 0 | 0 | 0
153 | -0.060303 | -0.086661 | -0.09669 | -0.11458 | -0.079774 | -0.091403 | -0.042519 | -0.073443 | -0.045906 | -0.078638 | -0.055163 | -0.0019018 | -0.045061 | -0.017401 | -0.035076 | 0.016917 | -0.03042 | -0.015199 | 0.0054139 | 0.034708 | -0.068504 | -0.0062644 | -0.059355 | -0.088089
153 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00099377 | -0.0017165 | -0.0010729 | -0.0018379 | -0.0012893 | -4.4449e-05 | -0.0010532 | -0.00040671 | -0.00081981 | 0.00039538 | -0.000711 | -0.00035524 | 0.00012653 | 0.0008112 | -0.0016011 | 0 | 0 | 0
154 | 0.14972 | 0.15073 | 0.056619 | 0.019973 | 0.095588 | -0.016623 | 0.090393 | 0.14513 | 0.083763 | 0.022309 | 0.093323 | 0.064822 | 0.042063 | 0.10322 | 0.074013 | 0.13224 | 0.091442 | 0.15295 | 0.048502 | 0.092754 | 0.1107 | 0.072727 | 0.10564 | 0.10025
154 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037519 | 0.060238 | 0.034767 | 0.0092596 | 0.038735 | 0.026905 | 0.017459 | 0.042842 | 0.03072 | 0.054889 | 0.037954 | 0.063485 | 0.020131 | 0.038499 | 0.045949 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | -0.0021054 | -0.0030197 | -0.0033953 | -0.0039309 | -0.0042956 | -0.0043677 | -0.0044206 | -0.002802 | -0.00050684 | 0.0013666 | 0.0039881 | 0.0039498 | 0.004379 | 0.0041137 | 0.0056086 | 0.0069216 | 0.0041383 | 0.0038988 | 0.003354 | 0.003221 | 0.0025001 | 0.0030088 | 0.0060473 | 0.00058325
155 | -1.8019 | -2.5844 | -2.9059 | -3.3643 | -3.6764 | -3.7381 | -3.7834 | -2.3981 | -0.43378 | 1.1696 | 3.4132 | 3.3804 | 3.7478 | 3.5208 | 4.8002 | 5.9239 | 3.5418 | 3.3368 | 2.8706 | 2.7567 | 2.1397 | 2.5751 | 5.1756 | 0.49918
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 8.7523 | 6.3696 | 5.324 | 4.845 | 4.4537 | 4.4092 | 3.9838 | 5.6751 | 5.45 | 7.9858 | 9.2269 | 9.8235 | 9.4237 | 8.3192 | 10.7362 | 11.6532 | 10.4555 | 9.5687 | 7.9912 | 7.8577 | 7.0948 | 7.7185 | 12.7153 | 9.4782
156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 0.066382 | 0.087258 | 0.073527 | -0.068993 | 0.095826 | -0.086277 | -0.076724 | -0.14146 | 0.76204 | 0.99495 | 1.0951 | 1.1897 | 0.93708 | 1.0608 | 1.2751 | 1.2121 | 1.2868 | 1.1226 | 0.88654 | 0.938 | 0.94645 | 0.90511 | 0.23114 | 0.0050588
158 | 0.34217 | 0.34247 | 0.33175 | 0.33198 | 0.33413 | 0.32468 | 0.33537 | 0.28686 | 0.35312 | 0.37922 | 0.41528 | 0.40342 | 0.37905 | 0.3993 | 0.43804 | 0.43513 | 0.40566 | 0.39716 | 0.39472 | 0.38447 | 0.38351 | 0.36996 | 0.35042 | 0.30944
158 | 7.6492 | 7.656 | 7.4163 | 7.4215 | 7.4696 | 7.2583 | 7.4972 | 6.4127 | 7.8939 | 8.4774 | 9.2837 | 9.0186 | 8.4738 | 8.9264 | 9.7923 | 9.7275 | 9.0686 | 8.8785 | 8.8239 | 8.5949 | 8.5734 | 8.2706 | 7.8338 | 6.9175
159 | 1.752 | 1.7398 | 1.7287 | 1.7119 | 1.706 | 1.7128 | 1.6959 | 1.8143 | 1.8339 | 1.8285 | 1.8194 | 1.8255 | 1.8363 | 1.8096 | 1.7999 | 1.8084 | 1.8317 | 1.822 | 1.8823 | 1.8639 | 1.8635 | 1.8789 | 1.8172 | 1.8525
159 | 41.3501 | 41.0631 | 40.8005 | 40.4025 | 40.2641 | 40.4254 | 40.0248 | 42.8194 | 43.2824 | 43.1564 | 42.9402 | 43.0858 | 43.3389 | 42.7103 | 42.4806 | 42.6807 | 43.2309 | 43.0016 | 44.425 | 43.9906 | 43.9818 | 44.3453 | 42.8883 | 43.7212
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0511 | 1.1245 | 1.1367 | 1.1334 | 1.1277 | 1.1315 | 1.1382 | 1.1216 | 1.1156 | 1.1209 | 1.1353 | 1.1293 | 1.1667 | 1.1553 | 1.155 | 0 | 0 | 0
160 | 0.67208 | 0.61543 | 0.55722 | 0.52271 | 0.52257 | 0.47201 | 0.67624 | 0.38397 | 1.0794 | 1.3714 | 1.7344 | 1.6798 | 1.4071 | 1.6324 | 2.0564 | 2.0559 | 1.7004 | 1.6147 | 1.5851 | 1.3075 | 1.2687 | 1.2476 | 0.88119 | 0.46051
160 | 4.9266 | 4.5114 | 4.0847 | 3.8317 | 3.8306 | 3.46 | 4.9572 | 2.8147 | 7.9123 | 10.0533 | 12.7139 | 12.3138 | 10.3148 | 11.9662 | 15.0747 | 15.0707 | 12.465 | 11.8367 | 11.6197 | 9.5847 | 9.3003 | 9.1456 | 6.4596 | 3.3757
160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 4.5821 | 2.7808 | 2.5645 | 1.8841 | 1.6267 | 1.02 | -1.0108 | 0.76301 | 2.4386 | 4.4442 | 9.8685 | 9.3852 | 9.603 | 9.187 | 10.5376 | 11.2707 | 13.2857 | 11.9893 | 8.1623 | 6.9008 | 6.527 | 6.7886 | 9.1876 | 5.9025
162 | 8.6703 | 8.3612 | 8.3333 | 8.3545 | 8.3426 | 8.335 | 8.3623 | 8.872 | 10.4376 | 10.5536 | 10.8464 | 10.6204 | 10.5814 | 10.6071 | 10.8449 | 10.8137 | 10.5611 | 10.5777 | 10.8693 | 10.5585 | 10.5533 | 10.2413 | 8.6571 | 8.9451
162 | 6.2479 | 6.0252 | 6.0051 | 6.0203 | 6.0118 | 6.0063 | 6.026 | 6.3932 | 7.5214 | 7.605 | 7.8161 | 7.6532 | 7.6251 | 7.6436 | 7.815 | 7.7925 | 7.6104 | 7.6224 | 7.8325 | 7.6086 | 7.6048 | 7.38 | 6.2384 | 6.446
162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 7.4706 | 8.511 | 7.624 | 7.23 | 6.9705 | 7.3391 | 5.0012 | 4.3727 | 7.6977 | 9.546 | 9.1651 | 9.8744 | 9.5429 | 10.2107 | 10.8904 | 10.9954 | 9.4966 | 9.4864 | 9.0856 | 8.9178 | 9.5091 | 9.2918 | 8.6147 | 4.8536
163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7428 | -1.6673 | -0.84462 | -0.59951 | -0.63437 | -0.57725 | -0.50453 | -2.0953 | -0.59318 | -0.45577 | -0.40919 | -0.45178 | -0.11962 | -1.6155 | -1.6334 | 0 | 0 | 0
165 | -6.3952 | -6.2937 | -6.2035 | -6.2119 | -5.9384 | -5.8412 | -5.6896 | -6.1672 | -1.7042 | -1.7135 | -1.354 | -0.63244 | -0.47749 | -0.72606 | -0.43174 | -0.87793 | -1.2819 | -1.0394 | -0.98325 | -2.1561 | -2.4371 | -2.5016 | -6.757 | -6.3446
165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | -0.49802 | -0.54596 | -0.64418 | -0.68981 | -0.71631 | -0.70322 | -0.7218 | -0.5191 | 0.11059 | 0.42452 | 0.60824 | 0.73274 | 0.64437 | 0.64303 | 0.78947 | 0.86902 | 0.7962 | 0.61685 | 0.66727 | 0.67767 | 0.57339 | 0.66307 | 0.35304 | 0.031715
166 | -6.1094 | -6.6976 | -7.9025 | -8.4623 | -8.7873 | -8.6268 | -8.8547 | -6.3681 | 1.3567 | 5.2077 | 7.4616 | 8.9888 | 7.9048 | 7.8883 | 9.6848 | 10.6607 | 9.7674 | 7.5672 | 8.1858 | 8.3133 | 7.034 | 8.1342 | 4.3309 | 0.38906
166 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0075979 | -0.0054643 | 0.0011641 | 0.0044686 | 0.0064026 | 0.007713 | 0.0067829 | 0.0067687 | 0.0083102 | 0.0091476 | 0.0083811 | 0.0064931 | 0.0070239 | 0.0071333 | 0.0060356 | 0 | 0 | 0
167 | -0.007445 | -0.0070974 | -0.0082829 | -0.008949 | -0.0067171 | -0.0090303 | -0.0045978 | -0.0095158 | -0.0084743 | -0.0088008 | 0.0015399 | -0.0064074 | -0.014877 | -0.015227 | -0.0035824 | -0.0077251 | -0.0095441 | -0.0079695 | -0.025952 | -0.013859 | -0.018739 | -0.014541 | -0.0010184 | -0.011072
167 | -0.96168 | -0.91678 | -1.0699 | -1.156 | -0.86766 | -1.1665 | -0.5939 | -1.2292 | -1.0946 | -1.1368 | 0.19891 | -0.82765 | -1.9217 | -1.9669 | -0.46274 | -0.99786 | -1.2328 | -1.0294 | -3.3522 | -1.7902 | -2.4205 | -1.8783 | -0.13154 | -1.4301
167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | -0.1179 | -0.217 | -0.17374 | 0.073303 | -0.11141 | -0.32153 | -0.3293 | 0.0033542 | 0.085699 | -0.29391 | -0.18045 | -0.25341 | -0.29895 | -0.0037504 | -0.0046825 | 0.15612 | 0.032976 | 0.19766 | -0.12513 | -0.2273 | 0.11766 | -0.14956 | -0.14447 | -0.0178
169 | 37.5815 | 36.8717 | 36.4079 | 36.4839 | 36.4037 | 36.4904 | 36.0751 | 38.6692 | 39.1983 | 38.9443 | 38.4319 | 38.8915 | 39.2227 | 38.3983 | 38.2615 | 38.4418 | 39.0661 | 38.9659 | 40.3522 | 39.8529 | 39.8015 | 40.5658 | 39.3092 | 40.0852
169 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5599 | 1.6721 | 1.695 | 1.684 | 1.6618 | 1.6817 | 1.696 | 1.6604 | 1.6545 | 1.6623 | 1.6893 | 1.6849 | 1.7449 | 1.7233 | 1.7211 | 0 | 0 | 0
170 | 14.9801 | 14.531 | 14.3512 | 14.2606 | 14.262 | 14.1027 | 13.9492 | 14.5742 | 15.3425 | 15.6731 | 16.365 | 16.1899 | 16.0914 | 16.1955 | 16.4754 | 16.8498 | 16.3521 | 16.2068 | 15.8829 | 15.8531 | 15.7405 | 15.8335 | 16.5653 | 15.2962
170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50203 | 0.76687 | 1.6734 | 1.728 | 1.7117 | 1.7829 | 1.7616 | 1.6914 | 1.7526 | 1.7725 | 1.7908 | 1.8329 | 1.8855 | 1.8561 | 1.8486 | 0 | 0 | 0
172 | -2.2295 | -2.032 | -2.1982 | -2.1788 | -2.1011 | -2.0406 | -1.7739 | -2.18 | -1.1786 | -1.1073 | -1.6117 | -0.63354 | -0.46075 | -0.31548 | -0.35883 | -0.71474 | -1.0116 | -1.0064 | -1.3249 | -1.4847 | -1.641 | -1.6187 | -2.9004 | -2.1983
172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59887 | 0.75563 | 0.50012 | 0.48931 | 1.4073 | 1.1331 | 1.1965 | 0 | 0 | 0 | 0 | 0 | 0.63929 | 0.50938 | 0.49808 | 0.5509 | 2.138 | 1.6774
175 | 1.9038 | 1.4755 | 0 | 0 | 0 | 0.79979 | 0.59887 | 0.75563 | 0.50012 | 0.48931 | 1.4073 | 1.1331 | 1.1965 | 1.5047 | 1.6578 | 0 | 0 | 0 | 0.63929 | 0.50938 | 0.49808 | 0.5509 | 0 | 1.6774
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0092911 | -0.22366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0092911 | -0.22366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2667 | 2.0634 | 1.4942 | 1.6229 | 1.6785 | 1.6815 | 2.0453 | 2.042 | 1.9213 | 1.1244
179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2667 | 2.0634 | 1.4942 | 1.6229 | 1.6785 | 1.6815 | 2.0453 | 2.042 | 0 | 1.1244
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6251 | 1.7004 | 2.0699 | 2.746 | 2.022 | 1.9082 | 1.3948 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1931 | 1.6079 | 2.3569 | 1.3139 | 2.1211 | 0 | 0 | 0 | 2.746 | 2.022 | 1.9082 | 1.3948 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8525 | 1.4065 | 2.6383 | 3.3746 | 2.9386 | 3.5313 | 3.4657 | 3.9222 | 3.9018 | 3.6105 | 2.6777 | 3.2995 | 3.0877 | 2.6171 | 3.1387 | 3.1756 | 0 | 1.8361
182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4065 | 2.6383 | 3.3746 | 2.9386 | 3.5313 | 3.4657 | 3.9222 | 3.9018 | 3.6105 | 2.6777 | 3.2995 | 3.0877 | 2.6171 | 3.1387 | 3.1756 | 0 | 1.8361
183 | 7.2119 | 4.8347 | 4.2595 | 4.0689 | 3.4961 | 4.0988 | 4.3829 | -1.4691 | -1.4634 | -0.56066 | 6.0085 | -0.94811 | -1.2052 | 6.7558 | 6.1671 | 6.281 | -1.1291 | -0.66771 | -8.9065 | -5.1411 | -8.6198 | -5.2887 | 2.2056 | -1.3375
187 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5996 | 9.8765 | 7.2276 | 8.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0711 | 9.5296 | 9.0812 | 9.9333 | 12.5703 | 12.9324
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3028 | -5.3723 | -6.8337 | -5.356 | -3.1169 | -2.5477 | -2.5576 | -2.5563 | -2.4331 | -2.5514 | -1.7251 | -0.9965 | -1.7804 | -2.6985 | -3.1514 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1169 | -2.5477 | -2.5576 | -2.5563 | -2.4331 | -2.5514 | -1.7251 | -0.9965 | -1.7804 | -2.6985 | -3.1514 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | -9.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.0902 | -3.5441 | -2.2657 | -2.319 | -2.7195 | -4.79 | -1.8949 | 1.3204 | 0 | 0 | 0 | -5.3917 | -7.1107
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2657 | -2.319 | -2.7195 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3917 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34011 | -2.0789 | -2.7704 | -2.5078 | -2.636 | -3.2991
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.6122 | -6.039 | -4.6663 | -5.2518 | -3.297 | -2.807 | -4.1316 | -3.1403 | -2.0114 | -3.5605 | -1.2747 | -0.34011 | -2.0789 | -2.7704 | -2.5078 | -2.636 | -3.2991
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70058 | 1.4 | 0 | 0 | 3.3059 | 3.6104 | 0 | 0 | 0 | 3.316 | 3.3562 | 3.3715 | 0 | 0 | 0 | 0 | 1.8593
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70058 | 1.4 | 3.3301 | 0 | 3.3059 | 3.6104 | 4.7955 | 4.8496 | 0 | 3.316 | 3.3562 | 3.3715 | 3.3645 | 3.342 | 2.9248 | 0 | 1.8593
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.708 | -2.763 | 0 | 0 | 0 | -2.5629 | -0.91731 | -1.4292 | -1.8686 | -1.9253 | -2.2237 | -2.7673
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.7207 | -1.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.91731 | -1.4292 | -1.8686 | -1.9253 | -2.2237 | -2.7673
198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9214 | -4.4339 | -3.5638 | -3.5723 | -3.8073 | -2.7109 | -2.3627 | -3.1894 | -3.9771 | -3.8316 | -3.5669 | -3.2962 | -2.2161 | -2.836 | -2.8867 | -2.833 | -2.9326 | -3.0021
200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8618 | -0.8712 | -3.818 | -0.85377 | -19.5 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5357 | -3.5574 | -4.0801 | -4.1485 | -3.9594 | -4.5569 | -2.5193 | -0.69998 | -3.6467 | -5.3067 | 3.9517 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7105 | -8.2193 | -5.9194 | -7.6412 | -4.3645 | -3.3862 | -4.0801 | -4.1485 | -3.8738 | -4.7281 | -2.6906 | -0.8712 | -3.6467 | -5.4779 | 3.6093 | -8.045 | -7.803
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.134 | 0 | 0 | 0 | 0 | 0
206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2437 | 3.5366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7038 | 2.5724 | 4.9883 | 4.7679 | 5.9699 | 3.9231 | 6.0178 | 6.9963 | 7.991 | 7.2647 | 6.5432 | 5.0641 | 4.6446 | 4.4798 | 4.4856 | 4.0083 | 2.4323
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0641 | 4.6446 | 4.4798 | 4.4856 | 4.0083 | 2.4323
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.827 | 36.0593 | 37.3516 | 42.4033 | 41.4671 | 41.4146 | 44.8736 | 51.7989 | 48.2436 | 43.8253 | 44.6549 | 40.3326 | 39.9931 | 40.0757 | 40.3497 | 28.7951 | 0
220 | 0 | 0 | 0 | 0 | 0 | 16.8371 | 24.1841 | 16.827 | 36.0593 | 37.3516 | 42.4033 | 41.4671 | 41.4146 | 44.8736 | 51.7989 | 48.2436 | 43.8253 | 44.6549 | 40.3326 | 39.9931 | 40.0757 | 40.3497 | 28.7951 | 26.8189
220 | 41.3611 | 34.2061 | 32.1711 | 29.9295 | 29.2501 | 16.8371 | 24.1841 | 16.827 | 36.0593 | 37.3516 | 42.4033 | 41.4671 | 41.4146 | 44.8736 | 51.7989 | 48.2436 | 43.8253 | 44.6549 | 40.3326 | 39.9931 | 40.0757 | 40.3497 | 28.7951 | 26.8189
222 | -23.6817 | -27.226 | -29.1512 | -31.261 | -33.0725 | -32.9354 | -37.1332 | -34.1613 | -15.7374 | -2.1928 | 14.4818 | 16.991 | 9.8693 | 15.0401 | 24.743 | 28.3245 | 28.5287 | 18.8174 | 15.7677 | 15.9188 | 11.1107 | 16.663 | 9.4453 | -7.3327
225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.1693 | -13.5063 | -13.5841 | -13.6756 | -11.5162 | -12.237 | 0 | 0 | 0 | -11.6201 | -11.5904 | -11.648 | -13.0534 | -13.1899 | -13.5981 | 0 | -14.4451
227 | -16.3953 | -23.1895 | 0 | 0 | 0 | 0 | -18.6328 | -17.9787 | -18.7891 | -18.1543 | -17.915 | -17.6315 | -18.6478 | -22.8901 | -17.9647 | -17.4591 | -17.8361 | -17.6705 | -17.3418 | -21.7779 | -21.3161 | 0 | 0 | 0
227 | -16.3953 | 0 | 0 | 0 | 0 | 0 | -18.6328 | -17.9787 | -18.7891 | -18.1543 | -17.915 | -17.6315 | -18.6478 | 0 | -17.9647 | -17.4591 | -17.8361 | -17.6705 | -17.3418 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.9994 | 45.4929 | 48.0233 | 48.0693 | 53.0645 | 0 | 0 | 0 | 58.2229 | 57.1921 | 26.7594 | 28.8853 | 24.9742 | 49.9268 | 0 | 34.7045
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.7594 | 28.8853 | 24.9742 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.753 | 7.7416 | 15.3018 | 14.7849 | 14.1837 | 8.6484 | 40.504 | 0 | 0 | 0 | 0 | 3.9991 | 3.7931 | 5.7174 | 0 | 0 | 6.3862
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | -0.0062059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3937 | 2.137 | 4.6072 | 4.3085 | 1.9724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 0.44342 | 0 | 0 | 0 | 0 | 0 | 0 | -13.7171 | -2.5467 | 1.4626 | 2.9185 | 6.6592 | 3.8379 | 8.399 | 31.0665 | 32.4643 | 4.7054 | 0 | 3.921 | 2.6387 | 3.6657 | -1.5097 | 6.8074 | -9.9521
234 | -24.8509 | -27.6428 | -32.1896 | -32.7314 | -33.0699 | -36.0101 | -30.1728 | -16.6627 | -9.6064 | -5.5889 | -10.5007 | -5.1187 | -2.7635 | -13.1149 | -9.8833 | -8.4202 | -2.3369 | -4.0541 | 18.8024 | 6.6204 | 9.778 | 9.4284 | -11.6485 | -5.1302
235 | -25.1573 | -28.0001 | -32.6299 | -33.1816 | -33.5263 | -31.7932 | -30.5757 | -16.8188 | -4.8746 | -5.5433 | -10.5446 | -5.0592 | -2.664 | -13.2066 | -9.9161 | -8.4263 | -2.2321 | -3.9806 | 19.2923 | 6.8885 | 10.1036 | 9.7473 | -11.7147 | -5.0766
236 | -25.1573 | -28.0001 | -32.6299 | -33.1816 | -33.5263 | -31.7932 | -30.5757 | -16.8188 | -4.8746 | -5.5433 | -10.5446 | -5.0592 | -2.664 | -13.1126 | -9.9161 | -8.4263 | -2.2321 | -3.9806 | 19.2923 | 6.8885 | 10.1036 | 9.8413 | -11.7147 | -5.0766
237 | -10.1512 | -8.5166 | -7.3286 | -9.3135 | -9.9029 | -8.7684 | -10.6186 | -3.9148 | 0.79133 | 0.96489 | 2.4259 | 2.4475 | 0.094277 | 2.4702 | 2.887 | 3.3994 | 2.2802 | 0.49995 | -0.49888 | -1.7955 | -1.5 | -1.1026 | 1.6526 | -6.701
238 | -10.1474 | -8.5129 | -7.3249 | -9.3098 | -9.8991 | -8.7648 | -10.6149 | -3.9111 | 0.79507 | 0.96863 | 2.4296 | 2.4512 | 0.098016 | 2.4739 | 2.8907 | 3.403 | 2.2839 | 0.50369 | -0.49564 | -1.7915 | -1.4962 | -1.0988 | 1.6564 | -6.6971
239 | -82.1731 | -81.3132 | -83.3916 | -82.6381 | -82.8684 | -81.9688 | -83.7923 | -82.6629 | -79.4362 | -76.3428 | -75.3609 | -72.3373 | -74.1153 | -73.8115 | -71.7743 | -68.5125 | -70.9433 | -72.6632 | -72.1758 | -70.5063 | -72.4701 | -70.6416 | -79.8229 | -80.0802
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | -13.2282 | -13.5498 | -11.0746 | -10.5553 | -10.8402 | -11.3399 | -11.9404 | -22.0527 | -9.7432 | -6.0938 | 0.20099 | -3.1484 | -7.2502 | -3.3651 | 4.1228 | 4.262 | -1.7148 | -5.6668 | -8.0489 | -5.6646 | -6.2623 | -8.5984 | -17.6952 | -15.1244
242 | -13.4479 | -13.3548 | -15.4619 | -14.4638 | -14.5951 | -15.8588 | -15.1892 | -21.1529 | -11.0261 | -7.2309 | 0.21508 | -4.0006 | -9.1236 | 0.93231 | 4.4665 | 4.6962 | -2.5218 | -2.1727 | -4.4803 | -6.9009 | -8.3136 | -6.5972 | 0 | -18.9935
243 | -13.5139 | -11.3342 | -9.7483 | -12.3957 | -13.1772 | -11.67 | -14.1254 | -5.193 | 1.0831 | 1.3148 | 3.2631 | 3.2903 | 0.15104 | 3.3212 | 3.8753 | 4.5587 | 3.0663 | 0.69286 | -0.63811 | -2.3666 | -1.9746 | -1.4447 | 2.2285 | -8.9028
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9194 | 0.79446 | 0.96754 | 2.4288 | 2.4489 | 0.094246 | 2.4724 | 2.8875 | 3.4001 | 2.2809 | 0.5007 | -0.49687 | -1.793 | -1.5002 | -1.1024 | 1.6523 | 0
250 | 0.054333 | -1.6593 | -1.5118 | -2.1401 | -1.8776 | -1.9062 | -1.0505 | -0.31096 | 1.3079 | 0.4822 | 1.6316 | 0.88135 | 1.0033 | 2.2279 | 0.51623 | 0.98137 | 1.3889 | 0.65266 | 2.5107 | 2.446 | 1.1377 | 1.7933 | -0.49339 | 0.16318
251 | -0.73174 | -1.0688 | -1.0258 | -1.1337 | -1.0823 | -0.96658 | -1.1951 | -1.0415 | 2.5912 | 3.5568 | 3.6982 | 3.9742 | 3.9599 | 3.9345 | 4.2818 | 4.6262 | 3.9543 | 3.6671 | 3.2735 | 3.1517 | 3.2183 | 3.1233 | -0.4638 | -0.84852
252 | -1.1182 | -1.5283 | -1.6515 | -1.5808 | -1.5938 | -1.641 | -1.5356 | -0.52315 | -0.2469 | -0.64682 | -0.78772 | -0.93543 | -0.40829 | -1.0901 | -1.0162 | -1.2402 | -0.93886 | -0.49737 | 0.82014 | 0.2437 | 0.3663 | -0.61055 | -1.443 | -0.27907
253 | 4.5363 | 4.2166 | 4.2104 | 4.171 | 4.1848 | 4.1316 | 4.2168 | 4.6153 | 5.5352 | 5.5698 | 6.0954 | 5.557 | 5.6586 | 5.6067 | 6.0152 | 5.8934 | 5.5578 | 5.5628 | 6.0719 | 5.722 | 5.6786 | 5.2052 | 4.248 | 4.6457
254 | 0.21691 | 0.77804 | 0.54308 | 0.40353 | 0.3972 | 0.32036 | 0.11445 | -1.2232 | -1.0053 | -0.19565 | -0.12886 | -0.045632 | -0.097353 | 0.27733 | 1.1893 | 1.3388 | -0.23275 | -0.033082 | -0.01637 | 0.19053 | 0.1568 | 0.20739 | 0.44826 | -1.435
255 | 6.0017 | 3.4631 | 2.9749 | 2.5685 | 1.9871 | 2.2857 | 2.7409 | 4.0038 | 4.3726 | 4.5879 | 7.0684 | 4.468 | 5.1943 | 6.9753 | 6.7535 | 7.1099 | 5.3524 | 4.7599 | 6.43 | 6.3793 | 3.5964 | 5.5749 | 7.9249 | 7.4579
262 | 4.0191 | 3.0891 | 3.3222 | 3.5362 | 2.9276 | 2.4228 | 2.0102 | 2.9176 | 3.641 | 2.7058 | 3.9226 | 3.0104 | 4.3554 | 3.818 | 4.5021 | 4.7739 | 4.4185 | 3.9501 | 3.2609 | 3.4792 | 3.8169 | 4.3261 | 4.059 | 2.9311
263 | -1.3298 | -0.4054 | -1.2218 | -1.0979 | -0.93623 | -1.6652 | -1.391 | -0.88097 | -0.91185 | -0.4306 | -0.25029 | -0.26859 | -0.51724 | -0.82225 | -0.94305 | -0.34856 | -0.1156 | -0.89268 | -0.85542 | -0.28292 | -0.60794 | -0.83285 | -1.4116 | -1.0394
264 | -7.7276 | -8.1593 | -7.8972 | -8.4993 | -8.632 | -9.1644 | -8.2653 | -8.1062 | -6.3939 | -5.7571 | -4.977 | -5.1815 | -6.2686 | -5.3949 | -4.6715 | -5.2956 | -5.0326 | -5.1343 | -6.5471 | -6.836 | -7.0871 | -4.9745 | -7.7686 | -7.9595
265 | 7.473 | 8.2084 | 7.7244 | 7.2227 | 7.6785 | 8.4311 | 8.458 | 8.0709 | 7.8551 | 9.6013 | 9.6033 | 10.0281 | 8.5178 | 8.9628 | 8.7174 | 9.588 | 9.0913 | 9.1178 | 9.5167 | 9.4273 | 8.7899 | 8.5391 | 9.9729 | 9.3459
266 | 0.85377 | -0.93462 | -0.23173 | -0.36079 | -0.70802 | 0.15719 | -0.22563 | -0.31845 | 1.2714 | 1.2112 | 1.9716 | 0.99032 | 1.3535 | 1.7959 | 3.0687 | 2.1912 | 0.61169 | 1.6666 | 1.9216 | 0.95457 | 1.0752 | 0.3988 | 0.37986 | 0.028327
267 | -6.2701 | -6.3195 | -6.3141 | -6.0811 | -6.8322 | -6.4157 | -7.2017 | -5.976 | -3.9629 | -2.8018 | -2.6354 | -3.1159 | -2.4338 | -2.7272 | -2.9581 | -2.0551 | -2.7252 | -2.1677 | -3.3901 | -3.8343 | -3.3699 | -3.4599 | -4.5521 | -5.6799
268 | 5.9077 | 5.9958 | 5.2392 | 5.1709 | 4.6334 | 4.4913 | 6.0965 | 6.8849 | 8.1963 | 9.1797 | 10.8648 | 13.1759 | 9.376 | 13.027 | 15.25 | 14.5057 | 13.3517 | 12.9175 | 12.4297 | 8.9609 | 8.7021 | 9.3287 | 8.137 | 5.2744
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2777 | 1.5245 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 1.8169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4408 | 2.602 | 2.6628 | 2.7511 | 2.646 | 2.7379 | 2.6665 | 1.2777 | 1.5245 | 0 | 0 | 0 | 1.8452
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen Vg (pu)
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
1 | 1.0272 | 1.0275 | 1.0271 | 1.0262 | 1.0262 | 1.0255 | 1.0264 | 1.0291 | 1.0348 | 1.0358 | 1.034 | 1.0354 | 1.0375 | 1.0341 | 1.0341 | 1.0348 | 1.0378 | 1.0341 | 1.0417 | 1.0402 | 1.0414 | 1.0373 | 1.0318 | 1.0395
2 | 1.0263 | 1.0272 | 1.027 | 1.0265 | 1.0265 | 1.0262 | 1.025 | 1.0269 | 1.0316 | 1.0333 | 1.0345 | 1.0384 | 1.0386 | 1.0369 | 1.0376 | 1.0376 | 1.038 | 1.0413 | 1.0433 | 1.0391 | 1.0385 | 1.0387 | 1.0336 | 1.0356
3 | 1.038 | 1.0399 | 1.0397 | 1.0387 | 1.0386 | 1.0387 | 1.0373 | 1.0387 | 1.0413 | 1.0415 | 1.0428 | 1.0421 | 1.0419 | 1.0428 | 1.0442 | 1.0439 | 1.0423 | 1.0426 | 1.0436 | 1.0429 | 1.0429 | 1.0426 | 1.0436 | 1.0405
4 | 1.0359 | 1.0349 | 1.0331 | 1.0329 | 1.0327 | 1.0327 | 1.037 | 1.0391 | 1.0408 | 1.0406 | 1.0403 | 1.0405 | 1.0409 | 1.0378 | 1.04 | 1.0402 | 1.0407 | 1.0405 | 1.0417 | 1.0396 | 1.0396 | 1.038 | 1.035 | 1.0369
5 | 1.0109 | 1.014 | 1.0137 | 1.0134 | 1.0131 | 1.0134 | 1.0103 | 1.0088 | 1.0125 | 1.015 | 1.018 | 1.0205 | 1.0187 | 1.0209 | 1.0227 | 1.0238 | 1.0203 | 1.0206 | 1.0195 | 1.0195 | 1.0195 | 1.0218 | 1.0236 | 1.0174
6 | 1.0113 | 1.0158 | 1.0151 | 1.0144 | 1.0139 | 1.0141 | 1.0112 | 1.011 | 1.0145 | 1.0166 | 1.019 | 1.0217 | 1.0204 | 1.0217 | 1.023 | 1.0242 | 1.0216 | 1.0219 | 1.0227 | 1.0219 | 1.022 | 1.0236 | 1.024 | 1.0193
7 | 1.0329 | 1.0342 | 1.0333 | 1.0337 | 1.0335 | 1.0335 | 1.0332 | 1.0428 | 1.0441 | 1.0406 | 1.0373 | 1.0387 | 1.0421 | 1.0364 | 1.0378 | 1.0383 | 1.0398 | 1.0399 | 1.0491 | 1.0476 | 1.0479 | 1.0439 | 1.0347 | 1.0419
22 | 1.0297 | 1.029 | 1.0289 | 1.0286 | 1.0286 | 1.0286 | 1.0302 | 1.032 | 1.0309 | 1.0324 | 1.0334 | 1.0335 | 1.033 | 1.0337 | 1.0333 | 1.0337 | 1.0333 | 1.0328 | 1.0283 | 1.0295 | 1.0294 | 1.0264 | 1.031 | 1.0285
22 | 1.0297 | 1.029 | 1.0289 | 1.0286 | 1.0286 | 1.0286 | 1.0302 | 1.032 | 1.0309 | 1.0324 | 1.0334 | 1.0335 | 1.033 | 1.0337 | 1.0333 | 1.0337 | 1.0333 | 1.0328 | 1.0283 | 1.0295 | 1.0294 | 1.0264 | 1.031 | 1.0285
30 | 1.0157 | 1.014 | 1.014 | 1.0135 | 1.0136 | 1.013 | 1.0156 | 1.0214 | 1.028 | 1.0279 | 1.0284 | 1.0307 | 1.0288 | 1.0295 | 1.0337 | 1.036 | 1.0359 | 1.0324 | 1.0333 | 1.0308 | 1.0339 | 1.0327 | 1.0221 | 1.0319
30 | 1.0157 | 1.014 | 1.014 | 1.0135 | 1.0136 | 1.013 | 1.0156 | 1.0214 | 1.028 | 1.0279 | 1.0284 | 1.0307 | 1.0288 | 1.0295 | 1.0337 | 1.036 | 1.0359 | 1.0324 | 1.0333 | 1.0308 | 1.0339 | 1.0327 | 1.0221 | 1.0319
61 | 1.0108 | 1.0096 | 1.0097 | 1.0095 | 1.0092 | 1.0096 | 1.0095 | 1.0144 | 1.0195 | 1.0207 | 1.0209 | 1.0236 | 1.0232 | 1.0221 | 1.0217 | 1.0236 | 1.0246 | 1.0232 | 1.0298 | 1.0269 | 1.0272 | 1.0256 | 1.0199 | 1.0197
61 | 1.0108 | 1.0096 | 1.0097 | 1.0095 | 1.0092 | 1.0096 | 1.0095 | 1.0144 | 1.0195 | 1.0207 | 1.0209 | 1.0236 | 1.0232 | 1.0221 | 1.0217 | 1.0236 | 1.0246 | 1.0232 | 1.0298 | 1.0269 | 1.0272 | 1.0256 | 1.0199 | 1.0197
61 | 1.0108 | 1.0096 | 1.0097 | 1.0095 | 1.0092 | 1.0096 | 1.0095 | 1.0144 | 1.0195 | 1.0207 | 1.0209 | 1.0236 | 1.0232 | 1.0221 | 1.0217 | 1.0236 | 1.0246 | 1.0232 | 1.0298 | 1.0269 | 1.0272 | 1.0256 | 1.0199 | 1.0197
108 | 1.0049 | 1.0039 | 1.0041 | 1.0038 | 1.004 | 1.0035 | 1.0052 | 1.0042 | 1.0098 | 1.0093 | 1.01 | 1.0113 | 1.0098 | 1.0103 | 1.0091 | 1.0101 | 1.0095 | 1.0115 | 1.0085 | 1.0108 | 1.0089 | 1.0075 | 1.0079 | 1.0118
108 | 1.0049 | 1.0039 | 1.0041 | 1.0038 | 1.004 | 1.0035 | 1.0052 | 1.0042 | 1.0098 | 1.0093 | 1.01 | 1.0113 | 1.0098 | 1.0103 | 1.0091 | 1.0101 | 1.0095 | 1.0115 | 1.0085 | 1.0108 | 1.0089 | 1.0075 | 1.0079 | 1.0118
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
109 | 1.0089 | 1.0074 | 1.0058 | 1.0059 | 1.0059 | 1.008 | 1.0127 | 1.0143 | 1.018 | 1.019 | 1.0178 | 1.0185 | 1.0173 | 1.0138 | 1.0146 | 1.0136 | 1.0131 | 1.0124 | 1.0167 | 1.0174 | 1.0186 | 1.0182 | 1.0109 | 1.0153
110 | 1.0195 | 1.0183 | 1.0189 | 1.0188 | 1.019 | 1.0187 | 1.0183 | 1.017 | 1.0203 | 1.0216 | 1.0201 | 1.0217 | 1.0208 | 1.022 | 1.0249 | 1.0247 | 1.0218 | 1.0216 | 1.0188 | 1.0182 | 1.0186 | 1.018 | 1.0222 | 1.0196
111 | 1.0133 | 1.012 | 1.0122 | 1.0123 | 1.0119 | 1.0128 | 1.0084 | 1.0133 | 1.0169 | 1.0176 | 1.0171 | 1.0186 | 1.0185 | 1.0168 | 1.0165 | 1.0187 | 1.0195 | 1.0173 | 1.0194 | 1.0165 | 1.0167 | 1.0191 | 1.0156 | 1.0165
112 | 1.0186 | 1.0175 | 1.0169 | 1.0165 | 1.0154 | 1.0164 | 1.0173 | 1.0211 | 1.0206 | 1.0217 | 1.0217 | 1.0226 | 1.0224 | 1.0215 | 1.0223 | 1.023 | 1.0235 | 1.0231 | 1.0267 | 1.027 | 1.0273 | 1.0278 | 1.0255 | 1.0254
112 | 1.0186 | 1.0175 | 1.0169 | 1.0165 | 1.0154 | 1.0164 | 1.0173 | 1.0211 | 1.0206 | 1.0217 | 1.0217 | 1.0226 | 1.0224 | 1.0215 | 1.0223 | 1.023 | 1.0235 | 1.0231 | 1.0267 | 1.027 | 1.0273 | 1.0278 | 1.0255 | 1.0254
113 | 1.0265 | 1.0243 | 1.0245 | 1.0247 | 1.0248 | 1.0248 | 1.0265 | 1.0314 | 1.0285 | 1.0279 | 1.028 | 1.0274 | 1.0284 | 1.0283 | 1.027 | 1.0288 | 1.0274 | 1.0284 | 1.031 | 1.0307 | 1.031 | 1.0294 | 1.0278 | 1.0293
113 | 1.0265 | 1.0243 | 1.0245 | 1.0247 | 1.0248 | 1.0248 | 1.0265 | 1.0314 | 1.0285 | 1.0279 | 1.028 | 1.0274 | 1.0284 | 1.0283 | 1.027 | 1.0288 | 1.0274 | 1.0284 | 1.031 | 1.0307 | 1.031 | 1.0294 | 1.0278 | 1.0293
113 | 1.0265 | 1.0243 | 1.0245 | 1.0247 | 1.0248 | 1.0248 | 1.0265 | 1.0314 | 1.0285 | 1.0279 | 1.028 | 1.0274 | 1.0284 | 1.0283 | 1.027 | 1.0288 | 1.0274 | 1.0284 | 1.031 | 1.0307 | 1.031 | 1.0294 | 1.0278 | 1.0293
114 | 1.0125 | 1.011 | 1.0113 | 1.011 | 1.0108 | 1.0108 | 1.0104 | 1.0138 | 1.0179 | 1.0193 | 1.0194 | 1.021 | 1.02 | 1.0192 | 1.0216 | 1.0216 | 1.0212 | 1.0204 | 1.0227 | 1.0193 | 1.0201 | 1.0198 | 1.0164 | 1.0171
114 | 1.0125 | 1.011 | 1.0113 | 1.011 | 1.0108 | 1.0108 | 1.0104 | 1.0138 | 1.0179 | 1.0193 | 1.0194 | 1.021 | 1.02 | 1.0192 | 1.0216 | 1.0216 | 1.0212 | 1.0204 | 1.0227 | 1.0193 | 1.0201 | 1.0198 | 1.0164 | 1.0171
114 | 1.0125 | 1.011 | 1.0113 | 1.011 | 1.0108 | 1.0108 | 1.0104 | 1.0138 | 1.0179 | 1.0193 | 1.0194 | 1.021 | 1.02 | 1.0192 | 1.0216 | 1.0216 | 1.0212 | 1.0204 | 1.0227 | 1.0193 | 1.0201 | 1.0198 | 1.0164 | 1.0171
114 | 1.0125 | 1.011 | 1.0113 | 1.011 | 1.0108 | 1.0108 | 1.0104 | 1.0138 | 1.0179 | 1.0193 | 1.0194 | 1.021 | 1.02 | 1.0192 | 1.0216 | 1.0216 | 1.0212 | 1.0204 | 1.0227 | 1.0193 | 1.0201 | 1.0198 | 1.0164 | 1.0171
114 | 1.0125 | 1.011 | 1.0113 | 1.011 | 1.0108 | 1.0108 | 1.0104 | 1.0138 | 1.0179 | 1.0193 | 1.0194 | 1.021 | 1.02 | 1.0192 | 1.0216 | 1.0216 | 1.0212 | 1.0204 | 1.0227 | 1.0193 | 1.0201 | 1.0198 | 1.0164 | 1.0171
115 | 1.0042 | 1.007 | 1.0068 | 1.0067 | 1.0086 | 1.0092 | 1.0069 | 1.0039 | 1.0045 | 1.004 | 1.0062 | 1.0066 | 1.0054 | 1.0068 | 1.0084 | 1.0076 | 1.0047 | 1.0046 | 1.0031 | 1.0048 | 1.005 | 1.0066 | 1.0097 | 1.0055
115 | 1.0042 | 1.007 | 1.0068 | 1.0067 | 1.0086 | 1.0092 | 1.0069 | 1.0039 | 1.0045 | 1.004 | 1.0062 | 1.0066 | 1.0054 | 1.0068 | 1.0084 | 1.0076 | 1.0047 | 1.0046 | 1.0031 | 1.0048 | 1.005 | 1.0066 | 1.0097 | 1.0055
115 | 1.0042 | 1.007 | 1.0068 | 1.0067 | 1.0086 | 1.0092 | 1.0069 | 1.0039 | 1.0045 | 1.004 | 1.0062 | 1.0066 | 1.0054 | 1.0068 | 1.0084 | 1.0076 | 1.0047 | 1.0046 | 1.0031 | 1.0048 | 1.005 | 1.0066 | 1.0097 | 1.0055
115 | 1.0042 | 1.007 | 1.0068 | 1.0067 | 1.0086 | 1.0092 | 1.0069 | 1.0039 | 1.0045 | 1.004 | 1.0062 | 1.0066 | 1.0054 | 1.0068 | 1.0084 | 1.0076 | 1.0047 | 1.0046 | 1.0031 | 1.0048 | 1.005 | 1.0066 | 1.0097 | 1.0055
115 | 1.0042 | 1.007 | 1.0068 | 1.0067 | 1.0086 | 1.0092 | 1.0069 | 1.0039 | 1.0045 | 1.004 | 1.0062 | 1.0066 | 1.0054 | 1.0068 | 1.0084 | 1.0076 | 1.0047 | 1.0046 | 1.0031 | 1.0048 | 1.005 | 1.0066 | 1.0097 | 1.0055
116 | 1.0073 | 1.0076 | 1.0059 | 1.0059 | 1.0059 | 1.006 | 1.0063 | 1.0088 | 1.0106 | 1.0104 | 1.0111 | 1.0122 | 1.0109 | 1.011 | 1.0103 | 1.0111 | 1.0127 | 1.0114 | 1.0119 | 1.0134 | 1.0122 | 1.0118 | 1.0099 | 1.0088
116 | 1.0073 | 1.0076 | 1.0059 | 1.0059 | 1.0059 | 1.006 | 1.0063 | 1.0088 | 1.0106 | 1.0104 | 1.0111 | 1.0122 | 1.0109 | 1.011 | 1.0103 | 1.0111 | 1.0127 | 1.0114 | 1.0119 | 1.0134 | 1.0122 | 1.0118 | 1.0099 | 1.0088
116 | 1.0073 | 1.0076 | 1.0059 | 1.0059 | 1.0059 | 1.006 | 1.0063 | 1.0088 | 1.0106 | 1.0104 | 1.0111 | 1.0122 | 1.0109 | 1.011 | 1.0103 | 1.0111 | 1.0127 | 1.0114 | 1.0119 | 1.0134 | 1.0122 | 1.0118 | 1.0099 | 1.0088
117 | 1.0103 | 1.0106 | 1.011 | 1.0111 | 1.0103 | 1.0111 | 1.0135 | 1.0134 | 1.0123 | 1.0132 | 1.0144 | 1.0146 | 1.0133 | 1.0143 | 1.0111 | 1.0111 | 1.0143 | 1.0143 | 1.0161 | 1.0153 | 1.0158 | 1.0152 | 1.0127 | 1.0154
118 | 1.0107 | 1.0089 | 1.0093 | 1.009 | 1.0088 | 1.0087 | 1.009 | 1.0105 | 1.0119 | 1.0121 | 1.0128 | 1.0139 | 1.0126 | 1.0132 | 1.0143 | 1.0145 | 1.0143 | 1.0136 | 1.0151 | 1.0132 | 1.014 | 1.0147 | 1.014 | 1.0131
118 | 1.0107 | 1.0089 | 1.0093 | 1.009 | 1.0088 | 1.0087 | 1.009 | 1.0105 | 1.0119 | 1.0121 | 1.0128 | 1.0139 | 1.0126 | 1.0132 | 1.0143 | 1.0145 | 1.0143 | 1.0136 | 1.0151 | 1.0132 | 1.014 | 1.0147 | 1.014 | 1.0131
118 | 1.0107 | 1.0089 | 1.0093 | 1.009 | 1.0088 | 1.0087 | 1.009 | 1.0105 | 1.0119 | 1.0121 | 1.0128 | 1.0139 | 1.0126 | 1.0132 | 1.0143 | 1.0145 | 1.0143 | 1.0136 | 1.0151 | 1.0132 | 1.014 | 1.0147 | 1.014 | 1.0131
118 | 1.0107 | 1.0089 | 1.0093 | 1.009 | 1.0088 | 1.0087 | 1.009 | 1.0105 | 1.0119 | 1.0121 | 1.0128 | 1.0139 | 1.0126 | 1.0132 | 1.0143 | 1.0145 | 1.0143 | 1.0136 | 1.0151 | 1.0132 | 1.014 | 1.0147 | 1.014 | 1.0131
119 | 1.03 | 1.0268 | 1.027 | 1.0268 | 1.0271 | 1.0267 | 1.028 | 1.0291 | 1.029 | 1.0315 | 1.0303 | 1.0297 | 1.0311 | 1.0298 | 1.0301 | 1.03 | 1.0296 | 1.0299 | 1.0323 | 1.0317 | 1.0321 | 1.0314 | 1.0287 | 1.0316
119 | 1.03 | 1.0268 | 1.027 | 1.0268 | 1.0271 | 1.0267 | 1.028 | 1.0291 | 1.029 | 1.0315 | 1.0303 | 1.0297 | 1.0311 | 1.0298 | 1.0301 | 1.03 | 1.0296 | 1.0299 | 1.0323 | 1.0317 | 1.0321 | 1.0314 | 1.0287 | 1.0316
119 | 1.03 | 1.0268 | 1.027 | 1.0268 | 1.0271 | 1.0267 | 1.028 | 1.0291 | 1.029 | 1.0315 | 1.0303 | 1.0297 | 1.0311 | 1.0298 | 1.0301 | 1.03 | 1.0296 | 1.0299 | 1.0323 | 1.0317 | 1.0321 | 1.0314 | 1.0287 | 1.0316
120 | 1.0085 | 1.0064 | 1.006 | 1.0061 | 1.0061 | 1.0064 | 1.0063 | 1.0112 | 1.0155 | 1.0154 | 1.0161 | 1.0182 | 1.0165 | 1.0166 | 1.0174 | 1.0195 | 1.0182 | 1.0173 | 1.022 | 1.0189 | 1.0195 | 1.0179 | 1.015 | 1.0146
120 | 1.0085 | 1.0064 | 1.006 | 1.0061 | 1.0061 | 1.0064 | 1.0063 | 1.0112 | 1.0155 | 1.0154 | 1.0161 | 1.0182 | 1.0165 | 1.0166 | 1.0174 | 1.0195 | 1.0182 | 1.0173 | 1.022 | 1.0189 | 1.0195 | 1.0179 | 1.015 | 1.0146
120 | 1.0085 | 1.0064 | 1.006 | 1.0061 | 1.0061 | 1.0064 | 1.0063 | 1.0112 | 1.0155 | 1.0154 | 1.0161 | 1.0182 | 1.0165 | 1.0166 | 1.0174 | 1.0195 | 1.0182 | 1.0173 | 1.022 | 1.0189 | 1.0195 | 1.0179 | 1.015 | 1.0146
120 | 1.0085 | 1.0064 | 1.006 | 1.0061 | 1.0061 | 1.0064 | 1.0063 | 1.0112 | 1.0155 | 1.0154 | 1.0161 | 1.0182 | 1.0165 | 1.0166 | 1.0174 | 1.0195 | 1.0182 | 1.0173 | 1.022 | 1.0189 | 1.0195 | 1.0179 | 1.015 | 1.0146
121 | 1.0093 | 1.01 | 1.0108 | 1.0111 | 1.0113 | 1.0111 | 1.0113 | 1.0084 | 1.0057 | 1.006 | 1.0066 | 1.0066 | 1.0041 | 1.0073 | 1.007 | 1.0064 | 1.0076 | 1.0077 | 1.001 | 1.0045 | 1.0053 | 1.0064 | 1.011 | 1.0061
121 | 1.0093 | 1.01 | 1.0108 | 1.0111 | 1.0113 | 1.0111 | 1.0113 | 1.0084 | 1.0057 | 1.006 | 1.0066 | 1.0066 | 1.0041 | 1.0073 | 1.007 | 1.0064 | 1.0076 | 1.0077 | 1.001 | 1.0045 | 1.0053 | 1.0064 | 1.011 | 1.0061
121 | 1.0093 | 1.01 | 1.0108 | 1.0111 | 1.0113 | 1.0111 | 1.0113 | 1.0084 | 1.0057 | 1.006 | 1.0066 | 1.0066 | 1.0041 | 1.0073 | 1.007 | 1.0064 | 1.0076 | 1.0077 | 1.001 | 1.0045 | 1.0053 | 1.0064 | 1.011 | 1.0061
122 | 1.0238 | 1.025 | 1.025 | 1.0242 | 1.0243 | 1.0241 | 1.025 | 1.0253 | 1.0285 | 1.0285 | 1.0289 | 1.0288 | 1.0291 | 1.0289 | 1.0291 | 1.0289 | 1.029 | 1.0291 | 1.0291 | 1.0323 | 1.0283 | 1.0314 | 1.0288 | 1.0301
122 | 1.0238 | 1.025 | 1.025 | 1.0242 | 1.0243 | 1.0241 | 1.025 | 1.0253 | 1.0285 | 1.0285 | 1.0289 | 1.0288 | 1.0291 | 1.0289 | 1.0291 | 1.0289 | 1.029 | 1.0291 | 1.0291 | 1.0323 | 1.0283 | 1.0314 | 1.0288 | 1.0301
122 | 1.0238 | 1.025 | 1.025 | 1.0242 | 1.0243 | 1.0241 | 1.025 | 1.0253 | 1.0285 | 1.0285 | 1.0289 | 1.0288 | 1.0291 | 1.0289 | 1.0291 | 1.0289 | 1.029 | 1.0291 | 1.0291 | 1.0323 | 1.0283 | 1.0314 | 1.0288 | 1.0301
123 | 1.0215 | 1.0212 | 1.0212 | 1.0211 | 1.0195 | 1.021 | 1.0223 | 1.0233 | 1.0235 | 1.0251 | 1.0244 | 1.0249 | 1.0253 | 1.0242 | 1.022 | 1.0223 | 1.0251 | 1.025 | 1.0266 | 1.0261 | 1.0265 | 1.0258 | 1.027 | 1.0243
123 | 1.0215 | 1.0212 | 1.0212 | 1.0211 | 1.0195 | 1.021 | 1.0223 | 1.0233 | 1.0235 | 1.0251 | 1.0244 | 1.0249 | 1.0253 | 1.0242 | 1.022 | 1.0223 | 1.0251 | 1.025 | 1.0266 | 1.0261 | 1.0265 | 1.0258 | 1.027 | 1.0243
124 | 1.016 | 1.0154 | 1.0152 | 1.0147 | 1.0145 | 1.0144 | 1.0134 | 1.0132 | 1.0198 | 1.0225 | 1.0254 | 1.0248 | 1.023 | 1.0249 | 1.0278 | 1.0255 | 1.026 | 1.0238 | 1.0207 | 1.0201 | 1.0201 | 1.02 | 1.0222 | 1.0176
124 | 1.016 | 1.0154 | 1.0152 | 1.0147 | 1.0145 | 1.0144 | 1.0134 | 1.0132 | 1.0198 | 1.0225 | 1.0254 | 1.0248 | 1.023 | 1.0249 | 1.0278 | 1.0255 | 1.026 | 1.0238 | 1.0207 | 1.0201 | 1.0201 | 1.02 | 1.0222 | 1.0176
124 | 1.016 | 1.0154 | 1.0152 | 1.0147 | 1.0145 | 1.0144 | 1.0134 | 1.0132 | 1.0198 | 1.0225 | 1.0254 | 1.0248 | 1.023 | 1.0249 | 1.0278 | 1.0255 | 1.026 | 1.0238 | 1.0207 | 1.0201 | 1.0201 | 1.02 | 1.0222 | 1.0176
125 | 1.0141 | 1.0122 | 1.0129 | 1.0127 | 1.0128 | 1.0126 | 1.0125 | 1.0135 | 1.0188 | 1.02 | 1.0203 | 1.0209 | 1.0194 | 1.0209 | 1.0217 | 1.0217 | 1.021 | 1.0207 | 1.0186 | 1.0179 | 1.0183 | 1.018 | 1.0181 | 1.0152
126 | 1.0272 | 1.0287 | 1.0284 | 1.0282 | 1.028 | 1.0281 | 1.0279 | 1.0327 | 1.0294 | 1.0288 | 1.0312 | 1.0309 | 1.0289 | 1.0308 | 1.0298 | 1.0304 | 1.0313 | 1.0312 | 1.0317 | 1.0305 | 1.0312 | 1.0304 | 1.0306 | 1.033
126 | 1.0272 | 1.0287 | 1.0284 | 1.0282 | 1.028 | 1.0281 | 1.0279 | 1.0327 | 1.0294 | 1.0288 | 1.0312 | 1.0309 | 1.0289 | 1.0308 | 1.0298 | 1.0304 | 1.0313 | 1.0312 | 1.0317 | 1.0305 | 1.0312 | 1.0304 | 1.0306 | 1.033
126 | 1.0272 | 1.0287 | 1.0284 | 1.0282 | 1.028 | 1.0281 | 1.0279 | 1.0327 | 1.0294 | 1.0288 | 1.0312 | 1.0309 | 1.0289 | 1.0308 | 1.0298 | 1.0304 | 1.0313 | 1.0312 | 1.0317 | 1.0305 | 1.0312 | 1.0304 | 1.0306 | 1.033
127 | 1.008 | 1.0068 | 1.0068 | 1.0066 | 1.0063 | 1.0065 | 1.0066 | 1.0113 | 1.016 | 1.0174 | 1.0177 | 1.0202 | 1.0197 | 1.0188 | 1.0189 | 1.0206 | 1.0182 | 1.0168 | 1.0221 | 1.0193 | 1.0196 | 1.0191 | 1.013 | 1.0125
127 | 1.008 | 1.0068 | 1.0068 | 1.0066 | 1.0063 | 1.0065 | 1.0066 | 1.0113 | 1.016 | 1.0174 | 1.0177 | 1.0202 | 1.0197 | 1.0188 | 1.0189 | 1.0206 | 1.0182 | 1.0168 | 1.0221 | 1.0193 | 1.0196 | 1.0191 | 1.013 | 1.0125
127 | 1.008 | 1.0068 | 1.0068 | 1.0066 | 1.0063 | 1.0065 | 1.0066 | 1.0113 | 1.016 | 1.0174 | 1.0177 | 1.0202 | 1.0197 | 1.0188 | 1.0189 | 1.0206 | 1.0182 | 1.0168 | 1.0221 | 1.0193 | 1.0196 | 1.0191 | 1.013 | 1.0125
127 | 1.008 | 1.0068 | 1.0068 | 1.0066 | 1.0063 | 1.0065 | 1.0066 | 1.0113 | 1.016 | 1.0174 | 1.0177 | 1.0202 | 1.0197 | 1.0188 | 1.0189 | 1.0206 | 1.0182 | 1.0168 | 1.0221 | 1.0193 | 1.0196 | 1.0191 | 1.013 | 1.0125
128 | 1.0172 | 1.0166 | 1.0166 | 1.0162 | 1.0164 | 1.0159 | 1.0175 | 1.02 | 1.0265 | 1.0246 | 1.0254 | 1.0263 | 1.0267 | 1.0255 | 1.028 | 1.0278 | 1.0281 | 1.0269 | 1.0297 | 1.028 | 1.0294 | 1.0272 | 1.023 | 1.0269
128 | 1.0172 | 1.0166 | 1.0166 | 1.0162 | 1.0164 | 1.0159 | 1.0175 | 1.02 | 1.0265 | 1.0246 | 1.0254 | 1.0263 | 1.0267 | 1.0255 | 1.028 | 1.0278 | 1.0281 | 1.0269 | 1.0297 | 1.028 | 1.0294 | 1.0272 | 1.023 | 1.0269
128 | 1.0172 | 1.0166 | 1.0166 | 1.0162 | 1.0164 | 1.0159 | 1.0175 | 1.02 | 1.0265 | 1.0246 | 1.0254 | 1.0263 | 1.0267 | 1.0255 | 1.028 | 1.0278 | 1.0281 | 1.0269 | 1.0297 | 1.028 | 1.0294 | 1.0272 | 1.023 | 1.0269
128 | 1.0172 | 1.0166 | 1.0166 | 1.0162 | 1.0164 | 1.0159 | 1.0175 | 1.02 | 1.0265 | 1.0246 | 1.0254 | 1.0263 | 1.0267 | 1.0255 | 1.028 | 1.0278 | 1.0281 | 1.0269 | 1.0297 | 1.028 | 1.0294 | 1.0272 | 1.023 | 1.0269
129 | 1.011 | 1.0097 | 1.0103 | 1.0104 | 1.0087 | 1.0103 | 1.01 | 1.0123 | 1.0186 | 1.0214 | 1.0211 | 1.0234 | 1.0225 | 1.0216 | 1.0219 | 1.0225 | 1.0233 | 1.0227 | 1.0227 | 1.0229 | 1.022 | 1.0222 | 1.0147 | 1.0164
129 | 1.011 | 1.0097 | 1.0103 | 1.0104 | 1.0087 | 1.0103 | 1.01 | 1.0123 | 1.0186 | 1.0214 | 1.0211 | 1.0234 | 1.0225 | 1.0216 | 1.0219 | 1.0225 | 1.0233 | 1.0227 | 1.0227 | 1.0229 | 1.022 | 1.0222 | 1.0147 | 1.0164
129 | 1.011 | 1.0097 | 1.0103 | 1.0104 | 1.0087 | 1.0103 | 1.01 | 1.0123 | 1.0186 | 1.0214 | 1.0211 | 1.0234 | 1.0225 | 1.0216 | 1.0219 | 1.0225 | 1.0233 | 1.0227 | 1.0227 | 1.0229 | 1.022 | 1.0222 | 1.0147 | 1.0164
129 | 1.011 | 1.0097 | 1.0103 | 1.0104 | 1.0087 | 1.0103 | 1.01 | 1.0123 | 1.0186 | 1.0214 | 1.0211 | 1.0234 | 1.0225 | 1.0216 | 1.0219 | 1.0225 | 1.0233 | 1.0227 | 1.0227 | 1.0229 | 1.022 | 1.0222 | 1.0147 | 1.0164
130 | 1.0065 | 1.0072 | 1.0055 | 1.0057 | 1.0055 | 1.0064 | 1.0052 | 1.0092 | 1.0125 | 1.013 | 1.0126 | 1.0129 | 1.0107 | 1.0113 | 1.011 | 1.0126 | 1.0127 | 1.0118 | 1.0145 | 1.0132 | 1.0132 | 1.014 | 1.0099 | 1.0089
131 | 1.0235 | 1.0238 | 1.024 | 1.0239 | 1.0241 | 1.0238 | 1.0249 | 1.0252 | 1.0234 | 1.0246 | 1.0251 | 1.0253 | 1.0252 | 1.025 | 1.0255 | 1.0258 | 1.026 | 1.0256 | 1.0262 | 1.0259 | 1.0259 | 1.0259 | 1.0232 | 1.0256
131 | 1.0235 | 1.0238 | 1.024 | 1.0239 | 1.0241 | 1.0238 | 1.0249 | 1.0252 | 1.0234 | 1.0246 | 1.0251 | 1.0253 | 1.0252 | 1.025 | 1.0255 | 1.0258 | 1.026 | 1.0256 | 1.0262 | 1.0259 | 1.0259 | 1.0259 | 1.0232 | 1.0256
131 | 1.0235 | 1.0238 | 1.024 | 1.0239 | 1.0241 | 1.0238 | 1.0249 | 1.0252 | 1.0234 | 1.0246 | 1.0251 | 1.0253 | 1.0252 | 1.025 | 1.0255 | 1.0258 | 1.026 | 1.0256 | 1.0262 | 1.0259 | 1.0259 | 1.0259 | 1.0232 | 1.0256
132 | 1.0092 | 1.0091 | 1.0093 | 1.0091 | 1.0089 | 1.0088 | 1.0094 | 1.01 | 1.0092 | 1.0104 | 1.0107 | 1.0113 | 1.011 | 1.0113 | 1.0117 | 1.0115 | 1.0116 | 1.0104 | 1.0122 | 1.0106 | 1.0113 | 1.0106 | 1.01 | 1.0095
132 | 1.0092 | 1.0091 | 1.0093 | 1.0091 | 1.0089 | 1.0088 | 1.0094 | 1.01 | 1.0092 | 1.0104 | 1.0107 | 1.0113 | 1.011 | 1.0113 | 1.0117 | 1.0115 | 1.0116 | 1.0104 | 1.0122 | 1.0106 | 1.0113 | 1.0106 | 1.01 | 1.0095
133 | 1.0026 | 1.0017 | 1.0018 | 1.0014 | 1.0015 | 1.0009 | 1.0023 | 1.0047 | 1.0066 | 1.0058 | 1.0064 | 1.0072 | 1.006 | 1.0066 | 1.0089 | 1.0083 | 1.0082 | 1.0066 | 1.0055 | 1.0063 | 1.0061 | 1.005 | 1.005 | 1.0056
133 | 1.0026 | 1.0017 | 1.0018 | 1.0014 | 1.0015 | 1.0009 | 1.0023 | 1.0047 | 1.0066 | 1.0058 | 1.0064 | 1.0072 | 1.006 | 1.0066 | 1.0089 | 1.0083 | 1.0082 | 1.0066 | 1.0055 | 1.0063 | 1.0061 | 1.005 | 1.005 | 1.0056
133 | 1.0026 | 1.0017 | 1.0018 | 1.0014 | 1.0015 | 1.0009 | 1.0023 | 1.0047 | 1.0066 | 1.0058 | 1.0064 | 1.0072 | 1.006 | 1.0066 | 1.0089 | 1.0083 | 1.0082 | 1.0066 | 1.0055 | 1.0063 | 1.0061 | 1.005 | 1.005 | 1.0056
293 | 1.008 | 1.0071 | 1.0072 | 1.0068 | 1.0069 | 1.0063 | 1.0078 | 1.0102 | 1.0121 | 1.0113 | 1.0118 | 1.0127 | 1.0115 | 1.0121 | 1.0144 | 1.0138 | 1.0137 | 1.0121 | 1.011 | 1.0118 | 1.0116 | 1.0104 | 1.0104 | 1.0111
134 | 1.0074 | 1.0063 | 1.0063 | 1.0059 | 1.0058 | 1.0058 | 1.0064 | 1.0107 | 1.0176 | 1.0194 | 1.0194 | 1.0192 | 1.0185 | 1.0189 | 1.0195 | 1.0215 | 1.0203 | 1.0193 | 1.0205 | 1.0178 | 1.0181 | 1.0201 | 1.0149 | 1.0145
134 | 1.0074 | 1.0063 | 1.0063 | 1.0059 | 1.0058 | 1.0058 | 1.0064 | 1.0107 | 1.0176 | 1.0194 | 1.0194 | 1.0192 | 1.0185 | 1.0189 | 1.0195 | 1.0215 | 1.0203 | 1.0193 | 1.0205 | 1.0178 | 1.0181 | 1.0201 | 1.0149 | 1.0145
136 | 1.0195 | 1.0187 | 1.0195 | 1.0194 | 1.0197 | 1.0193 | 1.0188 | 1.0166 | 1.0183 | 1.0191 | 1.0207 | 1.0232 | 1.0224 | 1.0194 | 1.0222 | 1.0219 | 1.0234 | 1.0232 | 1.02 | 1.0194 | 1.02 | 1.0192 | 1.0206 | 1.0183
136 | 1.0195 | 1.0187 | 1.0195 | 1.0194 | 1.0197 | 1.0193 | 1.0188 | 1.0166 | 1.0183 | 1.0191 | 1.0207 | 1.0232 | 1.0224 | 1.0194 | 1.0222 | 1.0219 | 1.0234 | 1.0232 | 1.02 | 1.0194 | 1.02 | 1.0192 | 1.0206 | 1.0183
137 | 1.0196 | 1.02 | 1.0201 | 1.0196 | 1.0198 | 1.0193 | 1.0215 | 1.0233 | 1.0178 | 1.0208 | 1.0191 | 1.02 | 1.0223 | 1.0197 | 1.0184 | 1.0179 | 1.0206 | 1.0204 | 1.0228 | 1.0211 | 1.0222 | 1.0191 | 1.0242 | 1.0258
137 | 1.0196 | 1.02 | 1.0201 | 1.0196 | 1.0198 | 1.0193 | 1.0215 | 1.0233 | 1.0178 | 1.0208 | 1.0191 | 1.02 | 1.0223 | 1.0197 | 1.0184 | 1.0179 | 1.0206 | 1.0204 | 1.0228 | 1.0211 | 1.0222 | 1.0191 | 1.0242 | 1.0258
137 | 1.0196 | 1.02 | 1.0201 | 1.0196 | 1.0198 | 1.0193 | 1.0215 | 1.0233 | 1.0178 | 1.0208 | 1.0191 | 1.02 | 1.0223 | 1.0197 | 1.0184 | 1.0179 | 1.0206 | 1.0204 | 1.0228 | 1.0211 | 1.0222 | 1.0191 | 1.0242 | 1.0258
138 | 1.0081 | 1.007 | 1.0072 | 1.0072 | 1.0069 | 1.0077 | 1.0079 | 1.0122 | 1.0166 | 1.0179 | 1.0175 | 1.0191 | 1.0187 | 1.017 | 1.0169 | 1.0192 | 1.0202 | 1.0174 | 1.0207 | 1.0208 | 1.021 | 1.0188 | 1.0151 | 1.015
138 | 1.0081 | 1.007 | 1.0072 | 1.0072 | 1.0069 | 1.0077 | 1.0079 | 1.0122 | 1.0166 | 1.0179 | 1.0175 | 1.0191 | 1.0187 | 1.017 | 1.0169 | 1.0192 | 1.0202 | 1.0174 | 1.0207 | 1.0208 | 1.021 | 1.0188 | 1.0151 | 1.015
138 | 1.0081 | 1.007 | 1.0072 | 1.0072 | 1.0069 | 1.0077 | 1.0079 | 1.0122 | 1.0166 | 1.0179 | 1.0175 | 1.0191 | 1.0187 | 1.017 | 1.0169 | 1.0192 | 1.0202 | 1.0174 | 1.0207 | 1.0208 | 1.021 | 1.0188 | 1.0151 | 1.015
139 | 1.0181 | 1.0171 | 1.0177 | 1.0176 | 1.0179 | 1.0176 | 1.0174 | 1.0153 | 1.0145 | 1.0194 | 1.021 | 1.0188 | 1.018 | 1.0195 | 1.0223 | 1.0218 | 1.0188 | 1.0187 | 1.0155 | 1.0149 | 1.0156 | 1.0147 | 1.0195 | 1.0169
140 | 1.0109 | 1.0103 | 1.011 | 1.0115 | 1.0114 | 1.0116 | 1.0188 | 1.023 | 1.0197 | 1.021 | 1.0217 | 1.0225 | 1.0237 | 1.0216 | 1.0208 | 1.021 | 1.0219 | 1.0206 | 1.0223 | 1.0233 | 1.0226 | 1.0113 | 1.0104 | 1.0157
140 | 1.0109 | 1.0103 | 1.011 | 1.0115 | 1.0114 | 1.0116 | 1.0188 | 1.023 | 1.0197 | 1.021 | 1.0217 | 1.0225 | 1.0237 | 1.0216 | 1.0208 | 1.021 | 1.0219 | 1.0206 | 1.0223 | 1.0233 | 1.0226 | 1.0113 | 1.0104 | 1.0157
141 | 1.0145 | 1.0147 | 1.015 | 1.015 | 1.0134 | 1.015 | 1.0166 | 1.0167 | 1.0171 | 1.0156 | 1.0144 | 1.0144 | 1.0152 | 1.014 | 1.0156 | 1.0157 | 1.0142 | 1.0144 | 1.021 | 1.0205 | 1.0168 | 1.02 | 1.0176 | 1.0161
142 | 1.0133 | 1.0119 | 1.0118 | 1.0113 | 1.0114 | 1.0108 | 1.0125 | 1.016 | 1.0172 | 1.0166 | 1.0198 | 1.0187 | 1.017 | 1.0183 | 1.0213 | 1.0218 | 1.021 | 1.0198 | 1.0202 | 1.0186 | 1.0185 | 1.0202 | 1.019 | 1.0198
142 | 1.0133 | 1.0119 | 1.0118 | 1.0113 | 1.0114 | 1.0108 | 1.0125 | 1.016 | 1.0172 | 1.0166 | 1.0198 | 1.0187 | 1.017 | 1.0183 | 1.0213 | 1.0218 | 1.021 | 1.0198 | 1.0202 | 1.0186 | 1.0185 | 1.0202 | 1.019 | 1.0198
142 | 1.0133 | 1.0119 | 1.0118 | 1.0113 | 1.0114 | 1.0108 | 1.0125 | 1.016 | 1.0172 | 1.0166 | 1.0198 | 1.0187 | 1.017 | 1.0183 | 1.0213 | 1.0218 | 1.021 | 1.0198 | 1.0202 | 1.0186 | 1.0185 | 1.0202 | 1.019 | 1.0198
142 | 1.0133 | 1.0119 | 1.0118 | 1.0113 | 1.0114 | 1.0108 | 1.0125 | 1.016 | 1.0172 | 1.0166 | 1.0198 | 1.0187 | 1.017 | 1.0183 | 1.0213 | 1.0218 | 1.021 | 1.0198 | 1.0202 | 1.0186 | 1.0185 | 1.0202 | 1.019 | 1.0198
144 | 1.0085 | 1.0073 | 1.0073 | 1.0072 | 1.0069 | 1.0074 | 1.0074 | 1.0121 | 1.0154 | 1.0169 | 1.0171 | 1.0174 | 1.0169 | 1.0158 | 1.0161 | 1.0178 | 1.0184 | 1.0166 | 1.0198 | 1.0192 | 1.0193 | 1.0179 | 1.0127 | 1.0123
144 | 1.0085 | 1.0073 | 1.0073 | 1.0072 | 1.0069 | 1.0074 | 1.0074 | 1.0121 | 1.0154 | 1.0169 | 1.0171 | 1.0174 | 1.0169 | 1.0158 | 1.0161 | 1.0178 | 1.0184 | 1.0166 | 1.0198 | 1.0192 | 1.0193 | 1.0179 | 1.0127 | 1.0123
145 | 1.0125 | 1.0124 | 1.0125 | 1.0124 | 1.0122 | 1.0119 | 1.0133 | 1.0145 | 1.0198 | 1.0227 | 1.0238 | 1.0235 | 1.0236 | 1.0237 | 1.0239 | 1.0244 | 1.0243 | 1.0208 | 1.0239 | 1.0227 | 1.0227 | 1.0211 | 1.0148 | 1.0148
145 | 1.0125 | 1.0124 | 1.0125 | 1.0124 | 1.0122 | 1.0119 | 1.0133 | 1.0145 | 1.0198 | 1.0227 | 1.0238 | 1.0235 | 1.0236 | 1.0237 | 1.0239 | 1.0244 | 1.0243 | 1.0208 | 1.0239 | 1.0227 | 1.0227 | 1.0211 | 1.0148 | 1.0148
146 | 1.0151 | 1.0145 | 1.0145 | 1.0143 | 1.0142 | 1.0142 | 1.0161 | 1.0184 | 1.0173 | 1.0185 | 1.0192 | 1.0194 | 1.015 | 1.0194 | 1.0147 | 1.0151 | 1.0151 | 1.0187 | 1.0153 | 1.0161 | 1.016 | 1.0152 | 1.016 | 1.0137
147 | 1.0189 | 1.0192 | 1.0195 | 1.0195 | 1.0197 | 1.0194 | 1.0212 | 1.0217 | 1.0229 | 1.0212 | 1.0204 | 1.02 | 1.0209 | 1.02 | 1.0236 | 1.0235 | 1.0198 | 1.0201 | 1.0224 | 1.0218 | 1.0222 | 1.0212 | 1.02 | 1.0203
147 | 1.0189 | 1.0192 | 1.0195 | 1.0195 | 1.0197 | 1.0194 | 1.0212 | 1.0217 | 1.0229 | 1.0212 | 1.0204 | 1.02 | 1.0209 | 1.02 | 1.0236 | 1.0235 | 1.0198 | 1.0201 | 1.0224 | 1.0218 | 1.0222 | 1.0212 | 1.02 | 1.0203
149 | 1.0086 | 1.0074 | 1.0083 | 1.0082 | 1.0086 | 1.0083 | 1.0063 | 1.0033 | 1.0011 | 1.0015 | 1.0035 | 1.0003 | 0.9989 | 1.003 | 1.0026 | 1.0017 | 1.0005 | 1.0008 | 0.9945 | 0.9985 | 0.9995 | 1.0014 | 1.009 | 1.0038
149 | 1.0086 | 1.0074 | 1.0083 | 1.0082 | 1.0086 | 1.0083 | 1.0063 | 1.0033 | 1.0011 | 1.0015 | 1.0035 | 1.0003 | 0.9989 | 1.003 | 1.0026 | 1.0017 | 1.0005 | 1.0008 | 0.9945 | 0.9985 | 0.9995 | 1.0014 | 1.009 | 1.0038
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
150 | 1.0126 | 1.0136 | 1.013 | 1.0122 | 1.012 | 1.012 | 1.0118 | 1.0117 | 1.0162 | 1.0193 | 1.0161 | 1.0195 | 1.0171 | 1.0171 | 1.0167 | 1.0178 | 1.0199 | 1.0177 | 1.0173 | 1.0171 | 1.0169 | 1.0179 | 1.0168 | 1.0131
151 | 1.0034 | 1.0029 | 1.0036 | 1.0035 | 1.0039 | 1.0032 | 1.0048 | 1.0074 | 1.0139 | 1.0119 | 1.0136 | 1.0141 | 1.013 | 1.0135 | 1.0185 | 1.0189 | 1.016 | 1.0158 | 1.0147 | 1.0141 | 1.0154 | 1.0139 | 1.0078 | 1.0132
151 | 1.0034 | 1.0029 | 1.0036 | 1.0035 | 1.0039 | 1.0032 | 1.0048 | 1.0074 | 1.0139 | 1.0119 | 1.0136 | 1.0141 | 1.013 | 1.0135 | 1.0185 | 1.0189 | 1.016 | 1.0158 | 1.0147 | 1.0141 | 1.0154 | 1.0139 | 1.0078 | 1.0132
152 | 1.013 | 1.0143 | 1.015 | 1.0144 | 1.0141 | 1.014 | 1.0115 | 1.0085 | 1.0105 | 1.012 | 1.0156 | 1.0149 | 1.0123 | 1.0163 | 1.018 | 1.0171 | 1.0163 | 1.0154 | 1.0149 | 1.0147 | 1.0152 | 1.0163 | 1.0163 | 1.0128
152 | 1.013 | 1.0143 | 1.015 | 1.0144 | 1.0141 | 1.014 | 1.0115 | 1.0085 | 1.0105 | 1.012 | 1.0156 | 1.0149 | 1.0123 | 1.0163 | 1.018 | 1.0171 | 1.0163 | 1.0154 | 1.0149 | 1.0147 | 1.0152 | 1.0163 | 1.0163 | 1.0128
152 | 1.013 | 1.0143 | 1.015 | 1.0144 | 1.0141 | 1.014 | 1.0115 | 1.0085 | 1.0105 | 1.012 | 1.0156 | 1.0149 | 1.0123 | 1.0163 | 1.018 | 1.0171 | 1.0163 | 1.0154 | 1.0149 | 1.0147 | 1.0152 | 1.0163 | 1.0163 | 1.0128
152 | 1.013 | 1.0143 | 1.015 | 1.0144 | 1.0141 | 1.014 | 1.0115 | 1.0085 | 1.0105 | 1.012 | 1.0156 | 1.0149 | 1.0123 | 1.0163 | 1.018 | 1.0171 | 1.0163 | 1.0154 | 1.0149 | 1.0147 | 1.0152 | 1.0163 | 1.0163 | 1.0128
152 | 1.013 | 1.0143 | 1.015 | 1.0144 | 1.0141 | 1.014 | 1.0115 | 1.0085 | 1.0105 | 1.012 | 1.0156 | 1.0149 | 1.0123 | 1.0163 | 1.018 | 1.0171 | 1.0163 | 1.0154 | 1.0149 | 1.0147 | 1.0152 | 1.0163 | 1.0163 | 1.0128
153 | 1.0108 | 1.0092 | 1.0092 | 1.0109 | 1.0109 | 1.0107 | 1.0096 | 1.0098 | 1.0157 | 1.0175 | 1.0165 | 1.0215 | 1.0188 | 1.0198 | 1.0203 | 1.0208 | 1.0209 | 1.0209 | 1.0238 | 1.0204 | 1.0192 | 1.0188 | 1.0157 | 1.0149
153 | 1.0108 | 1.0092 | 1.0092 | 1.0109 | 1.0109 | 1.0107 | 1.0096 | 1.0098 | 1.0157 | 1.0175 | 1.0165 | 1.0215 | 1.0188 | 1.0198 | 1.0203 | 1.0208 | 1.0209 | 1.0209 | 1.0238 | 1.0204 | 1.0192 | 1.0188 | 1.0157 | 1.0149
154 | 1.0067 | 1.0061 | 1.0066 | 1.0067 | 1.0069 | 1.0071 | 1.0059 | 1.0068 | 1.0123 | 1.0125 | 1.0126 | 1.0123 | 1.0109 | 1.0116 | 1.0131 | 1.0131 | 1.0133 | 1.0135 | 1.0121 | 1.0109 | 1.0116 | 1.0112 | 1.0086 | 1.0073
154 | 1.0067 | 1.0061 | 1.0066 | 1.0067 | 1.0069 | 1.0071 | 1.0059 | 1.0068 | 1.0123 | 1.0125 | 1.0126 | 1.0123 | 1.0109 | 1.0116 | 1.0131 | 1.0131 | 1.0133 | 1.0135 | 1.0121 | 1.0109 | 1.0116 | 1.0112 | 1.0086 | 1.0073
155 | 1.0093 | 1.0106 | 1.0108 | 1.0103 | 1.0099 | 1.0099 | 1.0081 | 1.0076 | 1.0109 | 1.0123 | 1.0148 | 1.0166 | 1.0152 | 1.0153 | 1.0145 | 1.0156 | 1.0146 | 1.0139 | 1.0145 | 1.0134 | 1.0138 | 1.0153 | 1.0152 | 1.0147
155 | 1.0093 | 1.0106 | 1.0108 | 1.0103 | 1.0099 | 1.0099 | 1.0081 | 1.0076 | 1.0109 | 1.0123 | 1.0148 | 1.0166 | 1.0152 | 1.0153 | 1.0145 | 1.0156 | 1.0146 | 1.0139 | 1.0145 | 1.0134 | 1.0138 | 1.0153 | 1.0152 | 1.0147
155 | 1.0093 | 1.0106 | 1.0108 | 1.0103 | 1.0099 | 1.0099 | 1.0081 | 1.0076 | 1.0109 | 1.0123 | 1.0148 | 1.0166 | 1.0152 | 1.0153 | 1.0145 | 1.0156 | 1.0146 | 1.0139 | 1.0145 | 1.0134 | 1.0138 | 1.0153 | 1.0152 | 1.0147
155 | 1.0093 | 1.0106 | 1.0108 | 1.0103 | 1.0099 | 1.0099 | 1.0081 | 1.0076 | 1.0109 | 1.0123 | 1.0148 | 1.0166 | 1.0152 | 1.0153 | 1.0145 | 1.0156 | 1.0146 | 1.0139 | 1.0145 | 1.0134 | 1.0138 | 1.0153 | 1.0152 | 1.0147
156 | 1.0099 | 1.0082 | 1.008 | 1.0077 | 1.0073 | 1.0076 | 1.0072 | 1.01 | 1.015 | 1.0172 | 1.0179 | 1.0189 | 1.018 | 1.0186 | 1.0176 | 1.0174 | 1.0177 | 1.0161 | 1.0214 | 1.0181 | 1.018 | 1.0193 | 1.0155 | 1.0143
156 | 1.0099 | 1.0082 | 1.008 | 1.0077 | 1.0073 | 1.0076 | 1.0072 | 1.01 | 1.015 | 1.0172 | 1.0179 | 1.0189 | 1.018 | 1.0186 | 1.0176 | 1.0174 | 1.0177 | 1.0161 | 1.0214 | 1.0181 | 1.018 | 1.0193 | 1.0155 | 1.0143
157 | 1.0102 | 1.0089 | 1.0091 | 1.0093 | 1.0089 | 1.0099 | 1.0095 | 1.0099 | 1.0108 | 1.0111 | 1.0103 | 1.0115 | 1.0115 | 1.0098 | 1.0137 | 1.0137 | 1.0122 | 1.01 | 1.0165 | 1.0135 | 1.0137 | 1.0118 | 1.0155 | 1.0128
158 | 1.0192 | 1.02 | 1.0201 | 1.0198 | 1.02 | 1.0195 | 1.0211 | 1.0219 | 1.0198 | 1.0235 | 1.0228 | 1.0235 | 1.0249 | 1.0233 | 1.0226 | 1.0224 | 1.0237 | 1.024 | 1.0249 | 1.0233 | 1.0239 | 1.022 | 1.0219 | 1.0223
158 | 1.0192 | 1.02 | 1.0201 | 1.0198 | 1.02 | 1.0195 | 1.0211 | 1.0219 | 1.0198 | 1.0235 | 1.0228 | 1.0235 | 1.0249 | 1.0233 | 1.0226 | 1.0224 | 1.0237 | 1.024 | 1.0249 | 1.0233 | 1.0239 | 1.022 | 1.0219 | 1.0223
159 | 1.0255 | 1.0251 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0249 | 1.0217 | 1.0191 | 1.0237 | 1.0236 | 1.0236 | 1.0221 | 1.0206 | 1.0205 | 1.0202 | 1.0236 | 1.0203 | 1.0168 | 1.0159 | 1.0166 | 1.0199 | 1.0252 | 1.0221
159 | 1.0255 | 1.0251 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0249 | 1.0217 | 1.0191 | 1.0237 | 1.0236 | 1.0236 | 1.0221 | 1.0206 | 1.0205 | 1.0202 | 1.0236 | 1.0203 | 1.0168 | 1.0159 | 1.0166 | 1.0199 | 1.0252 | 1.0221
159 | 1.0255 | 1.0251 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0249 | 1.0217 | 1.0191 | 1.0237 | 1.0236 | 1.0236 | 1.0221 | 1.0206 | 1.0205 | 1.0202 | 1.0236 | 1.0203 | 1.0168 | 1.0159 | 1.0166 | 1.0199 | 1.0252 | 1.0221
159 | 1.0255 | 1.0251 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0249 | 1.0217 | 1.0191 | 1.0237 | 1.0236 | 1.0236 | 1.0221 | 1.0206 | 1.0205 | 1.0202 | 1.0236 | 1.0203 | 1.0168 | 1.0159 | 1.0166 | 1.0199 | 1.0252 | 1.0221
160 | 1.0171 | 1.0175 | 1.0174 | 1.0169 | 1.017 | 1.0164 | 1.0183 | 1.0183 | 1.0225 | 1.0233 | 1.0238 | 1.0252 | 1.0257 | 1.0243 | 1.0253 | 1.0252 | 1.0254 | 1.0261 | 1.0267 | 1.0238 | 1.0242 | 1.0225 | 1.0218 | 1.0248
160 | 1.0171 | 1.0175 | 1.0174 | 1.0169 | 1.017 | 1.0164 | 1.0183 | 1.0183 | 1.0225 | 1.0233 | 1.0238 | 1.0252 | 1.0257 | 1.0243 | 1.0253 | 1.0252 | 1.0254 | 1.0261 | 1.0267 | 1.0238 | 1.0242 | 1.0225 | 1.0218 | 1.0248
160 | 1.0171 | 1.0175 | 1.0174 | 1.0169 | 1.017 | 1.0164 | 1.0183 | 1.0183 | 1.0225 | 1.0233 | 1.0238 | 1.0252 | 1.0257 | 1.0243 | 1.0253 | 1.0252 | 1.0254 | 1.0261 | 1.0267 | 1.0238 | 1.0242 | 1.0225 | 1.0218 | 1.0248
161 | 1.0133 | 1.0122 | 1.0121 | 1.0115 | 1.0112 | 1.0111 | 1.0105 | 1.0091 | 1.012 | 1.0128 | 1.0147 | 1.0174 | 1.0163 | 1.0155 | 1.0172 | 1.0174 | 1.0171 | 1.0171 | 1.02 | 1.0167 | 1.0174 | 1.0174 | 1.0157 | 1.016
162 | 1.012 | 1.0133 | 1.0126 | 1.012 | 1.0118 | 1.0117 | 1.013 | 1.0126 | 1.0121 | 1.0142 | 1.0127 | 1.0142 | 1.0149 | 1.0127 | 1.0131 | 1.0142 | 1.0148 | 1.0118 | 1.0164 | 1.0149 | 1.0152 | 1.0164 | 1.0164 | 1.014
162 | 1.012 | 1.0133 | 1.0126 | 1.012 | 1.0118 | 1.0117 | 1.013 | 1.0126 | 1.0121 | 1.0142 | 1.0127 | 1.0142 | 1.0149 | 1.0127 | 1.0131 | 1.0142 | 1.0148 | 1.0118 | 1.0164 | 1.0149 | 1.0152 | 1.0164 | 1.0164 | 1.014
162 | 1.012 | 1.0133 | 1.0126 | 1.012 | 1.0118 | 1.0117 | 1.013 | 1.0126 | 1.0121 | 1.0142 | 1.0127 | 1.0142 | 1.0149 | 1.0127 | 1.0131 | 1.0142 | 1.0148 | 1.0118 | 1.0164 | 1.0149 | 1.0152 | 1.0164 | 1.0164 | 1.014
163 | 1.0125 | 1.0117 | 1.0113 | 1.0106 | 1.0106 | 1.0102 | 1.0121 | 1.0179 | 1.0206 | 1.0212 | 1.0207 | 1.0238 | 1.0218 | 1.0231 | 1.0229 | 1.0252 | 1.0241 | 1.0252 | 1.0261 | 1.023 | 1.0227 | 1.0256 | 1.0185 | 1.0238
163 | 1.0125 | 1.0117 | 1.0113 | 1.0106 | 1.0106 | 1.0102 | 1.0121 | 1.0179 | 1.0206 | 1.0212 | 1.0207 | 1.0238 | 1.0218 | 1.0231 | 1.0229 | 1.0252 | 1.0241 | 1.0252 | 1.0261 | 1.023 | 1.0227 | 1.0256 | 1.0185 | 1.0238
164 | 1.0241 | 1.0246 | 1.0251 | 1.025 | 1.025 | 1.025 | 1.0254 | 1.0271 | 1.0224 | 1.0219 | 1.0214 | 1.0213 | 1.022 | 1.0234 | 1.0251 | 1.0251 | 1.0256 | 1.0255 | 1.0226 | 1.0249 | 1.0249 | 1.0246 | 1.0234 | 1.0265
164 | 1.0241 | 1.0246 | 1.0251 | 1.025 | 1.025 | 1.025 | 1.0254 | 1.0271 | 1.0224 | 1.0219 | 1.0214 | 1.0213 | 1.022 | 1.0234 | 1.0251 | 1.0251 | 1.0256 | 1.0255 | 1.0226 | 1.0249 | 1.0249 | 1.0246 | 1.0234 | 1.0265
165 | 1.0039 | 1.0024 | 1.0025 | 1.0021 | 1.0022 | 1.002 | 1.001 | 1.0046 | 1.0042 | 1.0049 | 1.0056 | 1.0071 | 1.0053 | 1.0059 | 1.0061 | 1.0064 | 1.0073 | 1.0072 | 1.0095 | 1.0074 | 1.0073 | 1.0068 | 1.0061 | 1.0056
165 | 1.0039 | 1.0024 | 1.0025 | 1.0021 | 1.0022 | 1.002 | 1.001 | 1.0046 | 1.0042 | 1.0049 | 1.0056 | 1.0071 | 1.0053 | 1.0059 | 1.0061 | 1.0064 | 1.0073 | 1.0072 | 1.0095 | 1.0074 | 1.0073 | 1.0068 | 1.0061 | 1.0056
166 | 1.0053 | 1.004 | 1.0045 | 1.004 | 1.0039 | 1.0036 | 1.0023 | 1.0062 | 1.0097 | 1.0126 | 1.016 | 1.0157 | 1.0137 | 1.0157 | 1.0148 | 1.0155 | 1.0132 | 1.012 | 1.0142 | 1.0096 | 1.0136 | 1.0096 | 1.0102 | 1.0054
166 | 1.0053 | 1.004 | 1.0045 | 1.004 | 1.0039 | 1.0036 | 1.0023 | 1.0062 | 1.0097 | 1.0126 | 1.016 | 1.0157 | 1.0137 | 1.0157 | 1.0148 | 1.0155 | 1.0132 | 1.012 | 1.0142 | 1.0096 | 1.0136 | 1.0096 | 1.0102 | 1.0054
166 | 1.0053 | 1.004 | 1.0045 | 1.004 | 1.0039 | 1.0036 | 1.0023 | 1.0062 | 1.0097 | 1.0126 | 1.016 | 1.0157 | 1.0137 | 1.0157 | 1.0148 | 1.0155 | 1.0132 | 1.012 | 1.0142 | 1.0096 | 1.0136 | 1.0096 | 1.0102 | 1.0054
167 | 1.0049 | 1.0038 | 1.0038 | 1.0036 | 1.0033 | 1.0033 | 1.0025 | 1.006 | 1.0062 | 1.0072 | 1.0053 | 1.0073 | 1.007 | 1.0069 | 1.0064 | 1.0077 | 1.0087 | 1.0085 | 1.0108 | 1.0104 | 1.0105 | 1.0099 | 1.0061 | 1.0077
167 | 1.0049 | 1.0038 | 1.0038 | 1.0036 | 1.0033 | 1.0033 | 1.0025 | 1.006 | 1.0062 | 1.0072 | 1.0053 | 1.0073 | 1.007 | 1.0069 | 1.0064 | 1.0077 | 1.0087 | 1.0085 | 1.0108 | 1.0104 | 1.0105 | 1.0099 | 1.0061 | 1.0077
167 | 1.0049 | 1.0038 | 1.0038 | 1.0036 | 1.0033 | 1.0033 | 1.0025 | 1.006 | 1.0062 | 1.0072 | 1.0053 | 1.0073 | 1.007 | 1.0069 | 1.0064 | 1.0077 | 1.0087 | 1.0085 | 1.0108 | 1.0104 | 1.0105 | 1.0099 | 1.0061 | 1.0077
168 | 1.0219 | 1.0207 | 1.0212 | 1.0202 | 1.0204 | 1.0205 | 1.02 | 1.0192 | 1.0179 | 1.0198 | 1.0209 | 1.0199 | 1.0189 | 1.0204 | 1.0235 | 1.0233 | 1.0204 | 1.02 | 1.0198 | 1.0192 | 1.0197 | 1.0189 | 1.0198 | 1.0169
169 | 1.0244 | 1.0245 | 1.0243 | 1.0236 | 1.0236 | 1.0235 | 1.025 | 1.022 | 1.0216 | 1.024 | 1.027 | 1.0251 | 1.0233 | 1.0267 | 1.0235 | 1.0234 | 1.0253 | 1.0248 | 1.0203 | 1.0198 | 1.02 | 1.0235 | 1.0255 | 1.0234
169 | 1.0244 | 1.0245 | 1.0243 | 1.0236 | 1.0236 | 1.0235 | 1.025 | 1.022 | 1.0216 | 1.024 | 1.027 | 1.0251 | 1.0233 | 1.0267 | 1.0235 | 1.0234 | 1.0253 | 1.0248 | 1.0203 | 1.0198 | 1.02 | 1.0235 | 1.0255 | 1.0234
170 | 1.009 | 1.0092 | 1.0094 | 1.0091 | 1.0089 | 1.0109 | 1.0082 | 1.0097 | 1.0128 | 1.0127 | 1.0127 | 1.0159 | 1.0147 | 1.0145 | 1.0156 | 1.0156 | 1.0164 | 1.0172 | 1.0192 | 1.0166 | 1.0175 | 1.0177 | 1.0145 | 1.0151
170 | 1.009 | 1.0092 | 1.0094 | 1.0091 | 1.0089 | 1.0109 | 1.0082 | 1.0097 | 1.0128 | 1.0127 | 1.0127 | 1.0159 | 1.0147 | 1.0145 | 1.0156 | 1.0156 | 1.0164 | 1.0172 | 1.0192 | 1.0166 | 1.0175 | 1.0177 | 1.0145 | 1.0151
171 | 1.0084 | 1.0109 | 1.011 | 1.0105 | 1.0105 | 1.0105 | 1.0108 | 1.0077 | 1.0029 | 1.007 | 1.003 | 1.006 | 1.0035 | 1.0028 | 1.0026 | 1.0077 | 1.0051 | 1.0028 | 1.0055 | 1.004 | 1.0042 | 1.0022 | 1.0128 | 1.0094
171 | 1.0084 | 1.0109 | 1.011 | 1.0105 | 1.0105 | 1.0105 | 1.0108 | 1.0077 | 1.0029 | 1.007 | 1.003 | 1.006 | 1.0035 | 1.0028 | 1.0026 | 1.0077 | 1.0051 | 1.0028 | 1.0055 | 1.004 | 1.0042 | 1.0022 | 1.0128 | 1.0094
172 | 1.004 | 1.0029 | 1.0029 | 1.0027 | 1.0025 | 1.0025 | 1.0016 | 1.0049 | 1.0046 | 1.0055 | 1.0055 | 1.0063 | 1.0051 | 1.0054 | 1.0054 | 1.0063 | 1.0072 | 1.007 | 1.0089 | 1.0083 | 1.0084 | 1.0078 | 1.0063 | 1.0062
172 | 1.004 | 1.0029 | 1.0029 | 1.0027 | 1.0025 | 1.0025 | 1.0016 | 1.0049 | 1.0046 | 1.0055 | 1.0055 | 1.0063 | 1.0051 | 1.0054 | 1.0054 | 1.0063 | 1.0072 | 1.007 | 1.0089 | 1.0083 | 1.0084 | 1.0078 | 1.0063 | 1.0062
173 | 1.0163 | 1.0148 | 1.0147 | 1.0142 | 1.0143 | 1.0137 | 1.0167 | 1.0231 | 1.03 | 1.0301 | 1.03 | 1.0329 | 1.0309 | 1.0319 | 1.0358 | 1.0381 | 1.0377 | 1.0343 | 1.0352 | 1.0323 | 1.0358 | 1.0346 | 1.0225 | 1.0334
173 | 1.0163 | 1.0148 | 1.0147 | 1.0142 | 1.0143 | 1.0137 | 1.0167 | 1.0231 | 1.03 | 1.0301 | 1.03 | 1.0329 | 1.0309 | 1.0319 | 1.0358 | 1.0381 | 1.0377 | 1.0343 | 1.0352 | 1.0323 | 1.0358 | 1.0346 | 1.0225 | 1.0334
173 | 1.0163 | 1.0148 | 1.0147 | 1.0142 | 1.0143 | 1.0137 | 1.0167 | 1.0231 | 1.03 | 1.0301 | 1.03 | 1.0329 | 1.0309 | 1.0319 | 1.0358 | 1.0381 | 1.0377 | 1.0343 | 1.0352 | 1.0323 | 1.0358 | 1.0346 | 1.0225 | 1.0334
173 | 1.0163 | 1.0148 | 1.0147 | 1.0142 | 1.0143 | 1.0137 | 1.0167 | 1.0231 | 1.03 | 1.0301 | 1.03 | 1.0329 | 1.0309 | 1.0319 | 1.0358 | 1.0381 | 1.0377 | 1.0343 | 1.0352 | 1.0323 | 1.0358 | 1.0346 | 1.0225 | 1.0334
174 | 1.0161 | 1.0146 | 1.0145 | 1.014 | 1.0141 | 1.0135 | 1.0164 | 1.0225 | 1.0293 | 1.0294 | 1.0295 | 1.0321 | 1.0302 | 1.031 | 1.0351 | 1.0374 | 1.0371 | 1.0337 | 1.0345 | 1.0318 | 1.0351 | 1.0339 | 1.0224 | 1.0329
174 | 1.0161 | 1.0146 | 1.0145 | 1.014 | 1.0141 | 1.0135 | 1.0164 | 1.0225 | 1.0293 | 1.0294 | 1.0295 | 1.0321 | 1.0302 | 1.031 | 1.0351 | 1.0374 | 1.0371 | 1.0337 | 1.0345 | 1.0318 | 1.0351 | 1.0339 | 1.0224 | 1.0329
175 | 1.0209 | 1.02 | 1.0041 | 1.004 | 1.004 | 1.0139 | 1.0413 | 1.0433 | 1.0427 | 1.0423 | 1.0415 | 1.0415 | 1.0341 | 1.0206 | 1.016 | 1.0071 | 1.0093 | 1.0057 | 1.0328 | 1.0349 | 1.0434 | 1.0432 | 1.0169 | 1.0427
175 | 1.0209 | 1.02 | 1.0041 | 1.004 | 1.004 | 1.0139 | 1.0413 | 1.0433 | 1.0427 | 1.0423 | 1.0415 | 1.0415 | 1.0341 | 1.0206 | 1.016 | 1.0071 | 1.0093 | 1.0057 | 1.0328 | 1.0349 | 1.0434 | 1.0432 | 1.0169 | 1.0427
176 | 1.0182 | 1.0174 | 1.004 | 1.004 | 1.004 | 1.0121 | 1.0365 | 1.0381 | 1.0376 | 1.0374 | 1.0363 | 1.0367 | 1.03 | 1.0182 | 1.0141 | 1.007 | 1.0092 | 1.0057 | 1.0291 | 1.0313 | 1.0385 | 1.0383 | 1.0149 | 1.0369
176 | 1.0182 | 1.0174 | 1.004 | 1.004 | 1.004 | 1.0121 | 1.0365 | 1.0381 | 1.0376 | 1.0374 | 1.0363 | 1.0367 | 1.03 | 1.0182 | 1.0141 | 1.007 | 1.0092 | 1.0057 | 1.0291 | 1.0313 | 1.0385 | 1.0383 | 1.0149 | 1.0369
177 | 1.0164 | 1.015 | 1.0149 | 1.0143 | 1.0144 | 1.0139 | 1.017 | 1.0235 | 1.0304 | 1.0306 | 1.0304 | 1.0333 | 1.0313 | 1.0323 | 1.0362 | 1.0428 | 1.0413 | 1.0347 | 1.0356 | 1.0326 | 1.0362 | 1.0349 | 1.0226 | 1.0337
177 | 1.0164 | 1.015 | 1.0149 | 1.0143 | 1.0144 | 1.0139 | 1.017 | 1.0235 | 1.0304 | 1.0306 | 1.0304 | 1.0333 | 1.0313 | 1.0323 | 1.0362 | 1.0428 | 1.0413 | 1.0347 | 1.0356 | 1.0326 | 1.0362 | 1.0349 | 1.0226 | 1.0337
178 | 1.0036 | 1.0024 | 1.0025 | 1.0023 | 1.002 | 1.0024 | 1.0023 | 1.0029 | 1.0079 | 1.0091 | 1.0093 | 1.0075 | 1.0071 | 1.006 | 1.0057 | 1.0076 | 1.0086 | 1.0072 | 1.0093 | 1.0107 | 1.011 | 1.0094 | 1.0081 | 1.008
178 | 1.0036 | 1.0024 | 1.0025 | 1.0023 | 1.002 | 1.0024 | 1.0023 | 1.0029 | 1.0079 | 1.0091 | 1.0093 | 1.0075 | 1.0071 | 1.006 | 1.0057 | 1.0076 | 1.0086 | 1.0072 | 1.0093 | 1.0107 | 1.011 | 1.0094 | 1.0081 | 1.008
179 | 1.0157 | 1.0141 | 1.0141 | 1.0135 | 1.0136 | 1.0131 | 1.0156 | 1.0214 | 1.0281 | 1.028 | 1.0284 | 1.0307 | 1.0289 | 1.0295 | 1.0368 | 1.0391 | 1.0393 | 1.0355 | 1.0364 | 1.0339 | 1.0384 | 1.0371 | 1.0236 | 1.0362
179 | 1.0157 | 1.0141 | 1.0141 | 1.0135 | 1.0136 | 1.0131 | 1.0156 | 1.0214 | 1.0281 | 1.028 | 1.0284 | 1.0307 | 1.0289 | 1.0295 | 1.0368 | 1.0391 | 1.0393 | 1.0355 | 1.0364 | 1.0339 | 1.0384 | 1.0371 | 1.0236 | 1.0362
181 | 1.0178 | 1.0193 | 1.0188 | 1.0179 | 1.0178 | 1.0178 | 1.0173 | 1.0156 | 1.0198 | 1.0234 | 1.0258 | 1.0253 | 1.0223 | 1.0257 | 1.0269 | 1.0287 | 1.0264 | 1.0236 | 1.0276 | 1.0261 | 1.0255 | 1.0281 | 1.0229 | 1.0175
181 | 1.0178 | 1.0193 | 1.0188 | 1.0179 | 1.0178 | 1.0178 | 1.0173 | 1.0156 | 1.0198 | 1.0234 | 1.0258 | 1.0253 | 1.0223 | 1.0257 | 1.0269 | 1.0287 | 1.0264 | 1.0236 | 1.0276 | 1.0261 | 1.0255 | 1.0281 | 1.0229 | 1.0175
181 | 1.0178 | 1.0193 | 1.0188 | 1.0179 | 1.0178 | 1.0178 | 1.0173 | 1.0156 | 1.0198 | 1.0234 | 1.0258 | 1.0253 | 1.0223 | 1.0257 | 1.0269 | 1.0287 | 1.0264 | 1.0236 | 1.0276 | 1.0261 | 1.0255 | 1.0281 | 1.0229 | 1.0175
182 | 1.0163 | 1.0149 | 1.0148 | 1.0142 | 1.0143 | 1.0137 | 1.017 | 1.0237 | 1.0308 | 1.0309 | 1.0306 | 1.0337 | 1.0317 | 1.0327 | 1.0366 | 1.0389 | 1.0384 | 1.0351 | 1.036 | 1.0328 | 1.0365 | 1.0353 | 1.0225 | 1.034
182 | 1.0163 | 1.0149 | 1.0148 | 1.0142 | 1.0143 | 1.0137 | 1.017 | 1.0237 | 1.0308 | 1.0309 | 1.0306 | 1.0337 | 1.0317 | 1.0327 | 1.0366 | 1.0389 | 1.0384 | 1.0351 | 1.036 | 1.0328 | 1.0365 | 1.0353 | 1.0225 | 1.034
183 | 1.0429 | 1.0412 | 1.0407 | 1.0404 | 1.0401 | 1.0403 | 1.0428 | 1.0469 | 1.0474 | 1.0472 | 1.0463 | 1.0465 | 1.0472 | 1.0461 | 1.0452 | 1.0458 | 1.0472 | 1.0471 | 1.0486 | 1.0482 | 1.0483 | 1.0482 | 1.0463 | 1.0476
187 | 1.0087 | 1.0082 | 1.0076 | 1.0075 | 1.0075 | 1.0083 | 1.0111 | 1.0123 | 1.0162 | 1.0163 | 1.0143 | 1.0154 | 1.014 | 1.0135 | 1.0145 | 1.0148 | 1.0131 | 1.0135 | 1.0184 | 1.0164 | 1.0172 | 1.0171 | 1.0113 | 1.0143
188 | 1.0087 | 1.0082 | 1.0076 | 1.0075 | 1.0075 | 1.0083 | 1.011 | 1.0122 | 1.0161 | 1.0162 | 1.0143 | 1.0154 | 1.014 | 1.0135 | 1.0145 | 1.0148 | 1.0131 | 1.0135 | 1.0182 | 1.0163 | 1.0171 | 1.017 | 1.0112 | 1.0141
189 | 1.0087 | 1.0082 | 1.0076 | 1.0075 | 1.0075 | 1.0083 | 1.011 | 1.0122 | 1.0161 | 1.0162 | 1.0143 | 1.0154 | 1.014 | 1.0135 | 1.0145 | 1.0148 | 1.0131 | 1.0135 | 1.0182 | 1.0163 | 1.0171 | 1.017 | 1.0112 | 1.0141
191 | 1.015 | 1.0129 | 1.0128 | 1.0124 | 1.0123 | 1.0121 | 1.0108 | 1.0158 | 1.021 | 1.0231 | 1.0244 | 1.0332 | 1.0303 | 1.032 | 1.0326 | 1.0329 | 1.033 | 1.0336 | 1.0408 | 1.0312 | 1.0293 | 1.0287 | 1.0217 | 1.0205
191 | 1.015 | 1.0129 | 1.0128 | 1.0124 | 1.0123 | 1.0121 | 1.0108 | 1.0158 | 1.021 | 1.0231 | 1.0244 | 1.0332 | 1.0303 | 1.032 | 1.0326 | 1.0329 | 1.033 | 1.0336 | 1.0408 | 1.0312 | 1.0293 | 1.0287 | 1.0217 | 1.0205
191 | 1.015 | 1.0129 | 1.0128 | 1.0124 | 1.0123 | 1.0121 | 1.0108 | 1.0158 | 1.021 | 1.0231 | 1.0244 | 1.0332 | 1.0303 | 1.032 | 1.0326 | 1.0329 | 1.033 | 1.0336 | 1.0408 | 1.0312 | 1.0293 | 1.0287 | 1.0217 | 1.0205
191 | 1.015 | 1.0129 | 1.0128 | 1.0124 | 1.0123 | 1.0121 | 1.0108 | 1.0158 | 1.021 | 1.0231 | 1.0244 | 1.0332 | 1.0303 | 1.032 | 1.0326 | 1.0329 | 1.033 | 1.0336 | 1.0408 | 1.0312 | 1.0293 | 1.0287 | 1.0217 | 1.0205
192 | 1.0142 | 1.0119 | 1.0118 | 1.0113 | 1.0113 | 1.011 | 1.0097 | 1.0145 | 1.0194 | 1.0214 | 1.0227 | 1.0303 | 1.027 | 1.0295 | 1.0299 | 1.0301 | 1.0299 | 1.0301 | 1.0364 | 1.0273 | 1.0263 | 1.0263 | 1.0209 | 1.0194
192 | 1.0142 | 1.0119 | 1.0118 | 1.0113 | 1.0113 | 1.011 | 1.0097 | 1.0145 | 1.0194 | 1.0214 | 1.0227 | 1.0303 | 1.027 | 1.0295 | 1.0299 | 1.0301 | 1.0299 | 1.0301 | 1.0364 | 1.0273 | 1.0263 | 1.0263 | 1.0209 | 1.0194
192 | 1.0142 | 1.0119 | 1.0118 | 1.0113 | 1.0113 | 1.011 | 1.0097 | 1.0145 | 1.0194 | 1.0214 | 1.0227 | 1.0303 | 1.027 | 1.0295 | 1.0299 | 1.0301 | 1.0299 | 1.0301 | 1.0364 | 1.0273 | 1.0263 | 1.0263 | 1.0209 | 1.0194
194 | 1.0133 | 1.0127 | 1.0128 | 1.0125 | 1.0123 | 1.0123 | 1.0118 | 1.0158 | 1.0209 | 1.0226 | 1.0237 | 1.0284 | 1.0263 | 1.0255 | 1.0262 | 1.0272 | 1.0274 | 1.0263 | 1.0334 | 1.029 | 1.0287 | 1.028 | 1.0235 | 1.023
194 | 1.0133 | 1.0127 | 1.0128 | 1.0125 | 1.0123 | 1.0123 | 1.0118 | 1.0158 | 1.0209 | 1.0226 | 1.0237 | 1.0284 | 1.0263 | 1.0255 | 1.0262 | 1.0272 | 1.0274 | 1.0263 | 1.0334 | 1.029 | 1.0287 | 1.028 | 1.0235 | 1.023
194 | 1.0133 | 1.0127 | 1.0128 | 1.0125 | 1.0123 | 1.0123 | 1.0118 | 1.0158 | 1.0209 | 1.0226 | 1.0237 | 1.0284 | 1.0263 | 1.0255 | 1.0262 | 1.0272 | 1.0274 | 1.0263 | 1.0334 | 1.029 | 1.0287 | 1.028 | 1.0235 | 1.023
195 | 1.0121 | 1.0119 | 1.0121 | 1.0119 | 1.0117 | 1.0117 | 1.0116 | 1.0163 | 1.0201 | 1.0192 | 1.0166 | 1.0241 | 1.0231 | 1.0206 | 1.0211 | 1.0191 | 1.0236 | 1.0248 | 1.0268 | 1.0217 | 1.0228 | 1.0225 | 1.017 | 1.022
195 | 1.0121 | 1.0119 | 1.0121 | 1.0119 | 1.0117 | 1.0117 | 1.0116 | 1.0163 | 1.0201 | 1.0192 | 1.0166 | 1.0241 | 1.0231 | 1.0206 | 1.0211 | 1.0191 | 1.0236 | 1.0248 | 1.0268 | 1.0217 | 1.0228 | 1.0225 | 1.017 | 1.022
195 | 1.0121 | 1.0119 | 1.0121 | 1.0119 | 1.0117 | 1.0117 | 1.0116 | 1.0163 | 1.0201 | 1.0192 | 1.0166 | 1.0241 | 1.0231 | 1.0206 | 1.0211 | 1.0191 | 1.0236 | 1.0248 | 1.0268 | 1.0217 | 1.0228 | 1.0225 | 1.017 | 1.022
196 | 1.0128 | 1.0153 | 1.0151 | 1.0148 | 1.0146 | 1.0149 | 1.0126 | 1.0124 | 1.0159 | 1.0178 | 1.0202 | 1.0228 | 1.0216 | 1.0229 | 1.0242 | 1.0253 | 1.0229 | 1.0231 | 1.0241 | 1.0233 | 1.0234 | 1.025 | 1.025 | 1.0206
196 | 1.0128 | 1.0153 | 1.0151 | 1.0148 | 1.0146 | 1.0149 | 1.0126 | 1.0124 | 1.0159 | 1.0178 | 1.0202 | 1.0228 | 1.0216 | 1.0229 | 1.0242 | 1.0253 | 1.0229 | 1.0231 | 1.0241 | 1.0233 | 1.0234 | 1.025 | 1.025 | 1.0206
196 | 1.0128 | 1.0153 | 1.0151 | 1.0148 | 1.0146 | 1.0149 | 1.0126 | 1.0124 | 1.0159 | 1.0178 | 1.0202 | 1.0228 | 1.0216 | 1.0229 | 1.0242 | 1.0253 | 1.0229 | 1.0231 | 1.0241 | 1.0233 | 1.0234 | 1.025 | 1.025 | 1.0206
198 | 1.013 | 1.0155 | 1.0153 | 1.015 | 1.0148 | 1.0151 | 1.0131 | 1.0135 | 1.0171 | 1.019 | 1.0213 | 1.0241 | 1.0229 | 1.0241 | 1.0253 | 1.0265 | 1.0241 | 1.0243 | 1.0254 | 1.0245 | 1.0246 | 1.0262 | 1.0262 | 1.0218
198 | 1.013 | 1.0155 | 1.0153 | 1.015 | 1.0148 | 1.0151 | 1.0131 | 1.0135 | 1.0171 | 1.019 | 1.0213 | 1.0241 | 1.0229 | 1.0241 | 1.0253 | 1.0265 | 1.0241 | 1.0243 | 1.0254 | 1.0245 | 1.0246 | 1.0262 | 1.0262 | 1.0218
200 | 1.0148 | 1.0128 | 1.0127 | 1.0122 | 1.0122 | 1.0119 | 1.0106 | 1.0156 | 1.0207 | 1.0227 | 1.024 | 1.0323 | 1.0292 | 1.031 | 1.0316 | 1.0319 | 1.032 | 1.0325 | 1.0397 | 1.0302 | 1.0287 | 1.0283 | 1.0216 | 1.0203
201 | 1.0148 | 1.0128 | 1.0127 | 1.0122 | 1.0122 | 1.0119 | 1.0106 | 1.0156 | 1.0207 | 1.0227 | 1.024 | 1.0323 | 1.0293 | 1.031 | 1.0316 | 1.0319 | 1.032 | 1.0325 | 1.0397 | 1.0302 | 1.0287 | 1.0284 | 1.0216 | 1.0203
202 | 1.0148 | 1.0128 | 1.0127 | 1.0122 | 1.0122 | 1.0119 | 1.0106 | 1.0156 | 1.0207 | 1.0228 | 1.024 | 1.0323 | 1.0293 | 1.031 | 1.0316 | 1.0319 | 1.032 | 1.0325 | 1.0397 | 1.0302 | 1.0287 | 1.0284 | 1.0216 | 1.0204
203 | 1.0148 | 1.0128 | 1.0127 | 1.0122 | 1.0122 | 1.0119 | 1.0106 | 1.0156 | 1.0207 | 1.0227 | 1.024 | 1.0323 | 1.0292 | 1.031 | 1.0316 | 1.0319 | 1.032 | 1.0325 | 1.0397 | 1.0302 | 1.0287 | 1.0283 | 1.0216 | 1.0203
206 | 1.01 | 1.009 | 1.0091 | 1.009 | 1.0087 | 1.0092 | 1.0092 | 1.014 | 1.019 | 1.0203 | 1.0204 | 1.0228 | 1.0231 | 1.0219 | 1.021 | 1.0228 | 1.0237 | 1.0219 | 1.0278 | 1.0248 | 1.025 | 1.0235 | 1.0184 | 1.0184
207 | 1.01 | 1.009 | 1.0091 | 1.009 | 1.0087 | 1.0092 | 1.0092 | 1.014 | 1.019 | 1.0203 | 1.0204 | 1.0228 | 1.0232 | 1.0219 | 1.021 | 1.0228 | 1.0237 | 1.0219 | 1.0278 | 1.0248 | 1.025 | 1.0235 | 1.0184 | 1.0184
218 | 1.01 | 1.0092 | 1.0094 | 1.0093 | 1.009 | 1.0094 | 1.0093 | 1.0139 | 1.0188 | 1.02 | 1.0202 | 1.0231 | 1.0223 | 1.0213 | 1.0213 | 1.0228 | 1.0236 | 1.0223 | 1.0283 | 1.025 | 1.0252 | 1.0241 | 1.019 | 1.0189
218 | 1.01 | 1.0092 | 1.0094 | 1.0093 | 1.009 | 1.0094 | 1.0093 | 1.0139 | 1.0188 | 1.02 | 1.0202 | 1.0231 | 1.0223 | 1.0213 | 1.0213 | 1.0228 | 1.0236 | 1.0223 | 1.0283 | 1.025 | 1.0252 | 1.0241 | 1.019 | 1.0189
218 | 1.01 | 1.0092 | 1.0094 | 1.0093 | 1.009 | 1.0094 | 1.0093 | 1.0139 | 1.0188 | 1.02 | 1.0202 | 1.0231 | 1.0223 | 1.0213 | 1.0213 | 1.0228 | 1.0236 | 1.0223 | 1.0283 | 1.025 | 1.0252 | 1.0241 | 1.019 | 1.0189
220 | 1.0115 | 1.0101 | 1.0102 | 1.0101 | 1.0098 | 1.0109 | 1.0118 | 1.0173 | 1.0243 | 1.0259 | 1.026 | 1.0278 | 1.0273 | 1.0259 | 1.0265 | 1.0284 | 1.0291 | 1.0265 | 1.0321 | 1.0294 | 1.0294 | 1.0273 | 1.0209 | 1.02
220 | 1.0115 | 1.0101 | 1.0102 | 1.0101 | 1.0098 | 1.0109 | 1.0118 | 1.0173 | 1.0243 | 1.0259 | 1.026 | 1.0278 | 1.0273 | 1.0259 | 1.0265 | 1.0284 | 1.0291 | 1.0265 | 1.0321 | 1.0294 | 1.0294 | 1.0273 | 1.0209 | 1.02
220 | 1.0115 | 1.0101 | 1.0102 | 1.0101 | 1.0098 | 1.0109 | 1.0118 | 1.0173 | 1.0243 | 1.0259 | 1.026 | 1.0278 | 1.0273 | 1.0259 | 1.0265 | 1.0284 | 1.0291 | 1.0265 | 1.0321 | 1.0294 | 1.0294 | 1.0273 | 1.0209 | 1.02
222 | 1.0186 | 1.0164 | 1.0169 | 1.0166 | 1.0166 | 1.0165 | 1.0165 | 1.0166 | 1.0203 | 1.0219 | 1.024 | 1.0233 | 1.0216 | 1.0231 | 1.0257 | 1.0258 | 1.0236 | 1.0231 | 1.0208 | 1.0201 | 1.0203 | 1.0201 | 1.0198 | 1.0163
225 | 1.0277 | 1.0286 | 1.0285 | 1.028 | 1.0279 | 1.0277 | 1.0266 | 1.0283 | 1.033 | 1.0346 | 1.0357 | 1.0398 | 1.0399 | 1.0381 | 1.0388 | 1.0388 | 1.0393 | 1.0427 | 1.045 | 1.0405 | 1.04 | 1.0402 | 1.0349 | 1.0369
227 | 1.0381 | 1.0382 | 1.0386 | 1.0385 | 1.0384 | 1.0384 | 1.0396 | 1.0418 | 1.0436 | 1.0434 | 1.0431 | 1.0432 | 1.0437 | 1.0415 | 1.0428 | 1.0429 | 1.0434 | 1.0432 | 1.0443 | 1.0431 | 1.043 | 1.0421 | 1.0387 | 1.0413
227 | 1.0381 | 1.0382 | 1.0386 | 1.0385 | 1.0384 | 1.0384 | 1.0396 | 1.0418 | 1.0436 | 1.0434 | 1.0431 | 1.0432 | 1.0437 | 1.0415 | 1.0428 | 1.0429 | 1.0434 | 1.0432 | 1.0443 | 1.0431 | 1.043 | 1.0421 | 1.0387 | 1.0413
228 | 1.0381 | 1.0383 | 1.0386 | 1.0385 | 1.0384 | 1.0384 | 1.0396 | 1.0418 | 1.0437 | 1.0434 | 1.0431 | 1.0432 | 1.0438 | 1.0415 | 1.0428 | 1.0429 | 1.0435 | 1.0433 | 1.0444 | 1.0431 | 1.043 | 1.0421 | 1.0387 | 1.0413
228 | 1.0381 | 1.0383 | 1.0386 | 1.0385 | 1.0384 | 1.0384 | 1.0396 | 1.0418 | 1.0437 | 1.0434 | 1.0431 | 1.0432 | 1.0438 | 1.0415 | 1.0428 | 1.0429 | 1.0435 | 1.0433 | 1.0444 | 1.0431 | 1.043 | 1.0421 | 1.0387 | 1.0413
229 | 1.0238 | 1.0241 | 1.0241 | 1.0234 | 1.0236 | 1.023 | 1.0249 | 1.0296 | 1.0363 | 1.0368 | 1.0344 | 1.0362 | 1.039 | 1.0326 | 1.029 | 1.0296 | 1.038 | 1.0352 | 1.045 | 1.0432 | 1.0441 | 1.0382 | 1.0283 | 1.0416
229 | 1.0238 | 1.0241 | 1.0241 | 1.0234 | 1.0236 | 1.023 | 1.0249 | 1.0296 | 1.0363 | 1.0368 | 1.0344 | 1.0362 | 1.039 | 1.0326 | 1.029 | 1.0296 | 1.038 | 1.0352 | 1.045 | 1.0432 | 1.0441 | 1.0382 | 1.0283 | 1.0416
230 | 1.0238 | 1.0241 | 1.0241 | 1.0234 | 1.0236 | 1.023 | 1.0249 | 1.0301 | 1.0365 | 1.0371 | 1.0346 | 1.0364 | 1.0392 | 1.0333 | 1.0291 | 1.0296 | 1.0379 | 1.035 | 1.0451 | 1.0433 | 1.0442 | 1.038 | 1.0283 | 1.0418
231 | 1.0284 | 1.0281 | 1.0281 | 1.0276 | 1.0276 | 1.0273 | 1.0282 | 1.03 | 1.0347 | 1.0356 | 1.035 | 1.0379 | 1.0393 | 1.0353 | 1.0351 | 1.0352 | 1.0366 | 1.0379 | 1.0423 | 1.0401 | 1.0403 | 1.0389 | 1.0341 | 1.038
231 | 1.0284 | 1.0281 | 1.0281 | 1.0276 | 1.0276 | 1.0273 | 1.0282 | 1.03 | 1.0347 | 1.0356 | 1.035 | 1.0379 | 1.0393 | 1.0353 | 1.0351 | 1.0352 | 1.0366 | 1.0379 | 1.0423 | 1.0401 | 1.0403 | 1.0389 | 1.0341 | 1.038
232 | 1.0275 | 1.0273 | 1.027 | 1.0263 | 1.0264 | 1.0258 | 1.0272 | 1.0303 | 1.0359 | 1.0366 | 1.0345 | 1.0362 | 1.0385 | 1.0346 | 1.0342 | 1.0349 | 1.0386 | 1.0348 | 1.0433 | 1.0415 | 1.0428 | 1.0383 | 1.0322 | 1.0407
233 | 1.0275 | 1.0273 | 1.027 | 1.0263 | 1.0264 | 1.0258 | 1.0272 | 1.0303 | 1.0359 | 1.0366 | 1.0345 | 1.0362 | 1.0385 | 1.0346 | 1.0342 | 1.0349 | 1.0386 | 1.0348 | 1.0433 | 1.0415 | 1.0428 | 1.0383 | 1.0322 | 1.0407
234 | 1.0421 | 1.0418 | 1.0411 | 1.0409 | 1.0408 | 1.0407 | 1.0428 | 1.0458 | 1.0472 | 1.0467 | 1.0463 | 1.046 | 1.0471 | 1.0456 | 1.046 | 1.0462 | 1.0468 | 1.0466 | 1.0488 | 1.0481 | 1.0481 | 1.0472 | 1.0426 | 1.0459
235 | 1.0421 | 1.0418 | 1.0411 | 1.0409 | 1.0408 | 1.0408 | 1.0428 | 1.0458 | 1.0473 | 1.0467 | 1.0463 | 1.046 | 1.0471 | 1.0456 | 1.046 | 1.0462 | 1.0468 | 1.0466 | 1.0488 | 1.0481 | 1.0481 | 1.0472 | 1.0426 | 1.0459
236 | 1.0421 | 1.0418 | 1.0411 | 1.0409 | 1.0408 | 1.0408 | 1.0428 | 1.0458 | 1.0473 | 1.0467 | 1.0463 | 1.046 | 1.0471 | 1.0456 | 1.046 | 1.0462 | 1.0468 | 1.0466 | 1.0488 | 1.0481 | 1.0481 | 1.0472 | 1.0426 | 1.0459
237 | 1.0409 | 1.0422 | 1.042 | 1.0409 | 1.0408 | 1.0409 | 1.0419 | 1.0445 | 1.0475 | 1.0475 | 1.048 | 1.0478 | 1.0478 | 1.048 | 1.0484 | 1.0484 | 1.048 | 1.048 | 1.0493 | 1.049 | 1.049 | 1.0487 | 1.0477 | 1.0462
238 | 1.0409 | 1.0422 | 1.042 | 1.0409 | 1.0408 | 1.0409 | 1.0419 | 1.0445 | 1.0475 | 1.0475 | 1.048 | 1.0478 | 1.0478 | 1.048 | 1.0484 | 1.0484 | 1.048 | 1.048 | 1.0493 | 1.049 | 1.049 | 1.0487 | 1.0477 | 1.0462
239 | 1.0428 | 1.0427 | 1.0426 | 1.0423 | 1.0425 | 1.0422 | 1.0442 | 1.0457 | 1.0449 | 1.0438 | 1.0433 | 1.0432 | 1.0438 | 1.0431 | 1.0426 | 1.0427 | 1.0432 | 1.0434 | 1.0457 | 1.0451 | 1.0453 | 1.0446 | 1.0431 | 1.0457
240 | 1.0428 | 1.0427 | 1.0427 | 1.0423 | 1.0425 | 1.0422 | 1.0442 | 1.0457 | 1.0449 | 1.0438 | 1.0433 | 1.0432 | 1.0438 | 1.0431 | 1.0427 | 1.0427 | 1.0432 | 1.0434 | 1.0457 | 1.0451 | 1.0453 | 1.0446 | 1.0431 | 1.0457
241 | 1.0356 | 1.036 | 1.0359 | 1.0355 | 1.0357 | 1.035 | 1.0373 | 1.0389 | 1.0427 | 1.0426 | 1.0426 | 1.0429 | 1.0435 | 1.0427 | 1.0429 | 1.0429 | 1.0433 | 1.0431 | 1.0469 | 1.0459 | 1.0459 | 1.0443 | 1.0397 | 1.0431
242 | 1.0355 | 1.0359 | 1.0357 | 1.0353 | 1.0355 | 1.0348 | 1.0371 | 1.0388 | 1.0425 | 1.0424 | 1.0424 | 1.0427 | 1.0433 | 1.0426 | 1.0427 | 1.0427 | 1.0431 | 1.043 | 1.0468 | 1.0457 | 1.0457 | 1.0442 | 1.0393 | 1.0429
243 | 1.0409 | 1.0422 | 1.042 | 1.0409 | 1.0408 | 1.0409 | 1.0419 | 1.0445 | 1.0475 | 1.0475 | 1.048 | 1.0478 | 1.0478 | 1.048 | 1.0484 | 1.0484 | 1.048 | 1.048 | 1.0493 | 1.049 | 1.049 | 1.0487 | 1.0477 | 1.0462
244 | 1.0409 | 1.0422 | 1.042 | 1.0409 | 1.0408 | 1.0409 | 1.0419 | 1.0445 | 1.0475 | 1.0475 | 1.048 | 1.0478 | 1.0478 | 1.048 | 1.0484 | 1.0484 | 1.048 | 1.048 | 1.0493 | 1.049 | 1.049 | 1.0487 | 1.0477 | 1.0462
250 | 1.0382 | 1.0368 | 1.0364 | 1.0361 | 1.0359 | 1.036 | 1.0385 | 1.0436 | 1.0439 | 1.0435 | 1.0416 | 1.0431 | 1.0437 | 1.0413 | 1.0404 | 1.041 | 1.0436 | 1.0434 | 1.0463 | 1.0453 | 1.0459 | 1.0453 | 1.0424 | 1.0443
251 | 1.0157 | 1.0145 | 1.0145 | 1.0139 | 1.014 | 1.0134 | 1.015 | 1.0184 | 1.0238 | 1.0237 | 1.0252 | 1.0266 | 1.0248 | 1.0261 | 1.0293 | 1.0302 | 1.0295 | 1.0282 | 1.0285 | 1.0269 | 1.0289 | 1.0285 | 1.0216 | 1.0265
252 | 1.0207 | 1.0219 | 1.0212 | 1.0203 | 1.02 | 1.0198 | 1.0192 | 1.0177 | 1.0213 | 1.0242 | 1.0251 | 1.0246 | 1.022 | 1.0253 | 1.0265 | 1.0281 | 1.0266 | 1.0248 | 1.0282 | 1.0275 | 1.0276 | 1.0297 | 1.0264 | 1.0214
253 | 1.0168 | 1.018 | 1.0171 | 1.0163 | 1.016 | 1.0158 | 1.0155 | 1.015 | 1.0179 | 1.0203 | 1.0206 | 1.0208 | 1.0189 | 1.021 | 1.0218 | 1.0232 | 1.0226 | 1.0213 | 1.026 | 1.0248 | 1.025 | 1.0265 | 1.0227 | 1.0195
254 | 1.0197 | 1.0181 | 1.0179 | 1.0172 | 1.0172 | 1.0164 | 1.018 | 1.0222 | 1.0283 | 1.0281 | 1.029 | 1.0307 | 1.0293 | 1.03 | 1.0335 | 1.035 | 1.0351 | 1.0333 | 1.0351 | 1.0335 | 1.0358 | 1.0349 | 1.0265 | 1.0329
255 | 1.039 | 1.0375 | 1.0371 | 1.0368 | 1.0365 | 1.0366 | 1.0391 | 1.0445 | 1.0453 | 1.0449 | 1.0432 | 1.0444 | 1.0451 | 1.0428 | 1.0419 | 1.0425 | 1.0449 | 1.0447 | 1.0477 | 1.0467 | 1.0471 | 1.0467 | 1.0434 | 1.0454
262 | 1.0139 | 1.014 | 1.0141 | 1.0137 | 1.0133 | 1.0132 | 1.0125 | 1.0141 | 1.0167 | 1.0165 | 1.0165 | 1.0198 | 1.0188 | 1.0186 | 1.0199 | 1.0201 | 1.0213 | 1.0223 | 1.0246 | 1.0222 | 1.0232 | 1.0236 | 1.0204 | 1.0207
263 | 1.0168 | 1.0181 | 1.0186 | 1.018 | 1.0176 | 1.0174 | 1.0151 | 1.0123 | 1.0146 | 1.0162 | 1.0195 | 1.0193 | 1.0167 | 1.0207 | 1.0232 | 1.0243 | 1.0213 | 1.0214 | 1.02 | 1.0202 | 1.0206 | 1.0229 | 1.024 | 1.0174
264 | 1.0106 | 1.0094 | 1.0095 | 1.0093 | 1.0089 | 1.0093 | 1.0092 | 1.014 | 1.0191 | 1.0203 | 1.0205 | 1.0231 | 1.0226 | 1.0216 | 1.0214 | 1.0233 | 1.0244 | 1.023 | 1.0295 | 1.0266 | 1.0269 | 1.0255 | 1.0196 | 1.0194
265 | 1.0127 | 1.0129 | 1.013 | 1.0126 | 1.0123 | 1.0123 | 1.0117 | 1.0133 | 1.016 | 1.016 | 1.0159 | 1.0193 | 1.0181 | 1.0179 | 1.0191 | 1.0192 | 1.0203 | 1.0212 | 1.0234 | 1.0209 | 1.0218 | 1.0221 | 1.019 | 1.0195
266 | 1.0165 | 1.0177 | 1.0183 | 1.0177 | 1.0173 | 1.0172 | 1.0149 | 1.0121 | 1.0145 | 1.0161 | 1.0194 | 1.0192 | 1.0166 | 1.0206 | 1.0231 | 1.0241 | 1.021 | 1.0211 | 1.0196 | 1.0197 | 1.0201 | 1.0224 | 1.0236 | 1.017
267 | 1.0108 | 1.0096 | 1.0096 | 1.0094 | 1.009 | 1.0091 | 1.0081 | 1.012 | 1.0166 | 1.0178 | 1.0185 | 1.0222 | 1.021 | 1.0209 | 1.0212 | 1.0227 | 1.0237 | 1.0234 | 1.0293 | 1.0253 | 1.0255 | 1.0248 | 1.0192 | 1.0181
268 | 1.0274 | 1.0276 | 1.0275 | 1.027 | 1.027 | 1.0267 | 1.0276 | 1.0295 | 1.0336 | 1.0343 | 1.0337 | 1.0365 | 1.0378 | 1.0349 | 1.0348 | 1.0348 | 1.0363 | 1.0375 | 1.0419 | 1.0396 | 1.0398 | 1.0384 | 1.0336 | 1.0375
273 | 1.0102 | 1.0075 | 1.0058 | 1.0059 | 1.0058 | 1.0065 | 1.0057 | 1.0094 | 1.0122 | 1.0126 | 1.0124 | 1.017 | 1.0152 | 1.0157 | 1.0145 | 1.0158 | 1.0174 | 1.0171 | 1.0194 | 1.0193 | 1.0132 | 1.0137 | 1.0102 | 1.0125
273 | 1.0102 | 1.0075 | 1.0058 | 1.0059 | 1.0058 | 1.0065 | 1.0057 | 1.0094 | 1.0122 | 1.0126 | 1.0124 | 1.017 | 1.0152 | 1.0157 | 1.0145 | 1.0158 | 1.0174 | 1.0171 | 1.0194 | 1.0193 | 1.0132 | 1.0137 | 1.0102 | 1.0125
273 | 1.0102 | 1.0075 | 1.0058 | 1.0059 | 1.0058 | 1.0065 | 1.0057 | 1.0094 | 1.0122 | 1.0126 | 1.0124 | 1.017 | 1.0152 | 1.0157 | 1.0145 | 1.0158 | 1.0174 | 1.0171 | 1.0194 | 1.0193 | 1.0132 | 1.0137 | 1.0102 | 1.0125
293 | 1.008 | 1.0071 | 1.0072 | 1.0068 | 1.0069 | 1.0063 | 1.0078 | 1.0102 | 1.0121 | 1.0113 | 1.0118 | 1.0127 | 1.0115 | 1.0121 | 1.0144 | 1.0138 | 1.0137 | 1.0121 | 1.011 | 1.0118 | 1.0116 | 1.0104 | 1.0104 | 1.0111

## Transf Tap Ratio
fbus | tbus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
8 | 36 | 1.0042 | 1.0042 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1 | 0.99583 | 0.99167 | 0.99583 | 0.99167 | 1.0042 | 1.0083 | 1.0125 | 1.0125 | 1 | 1.0125
8 | 109 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 0.99583 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583 | 1 | 1 | 0.9875 | 1
9 | 112 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167
9 | 112 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167
9 | 112 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167
9 | 112 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583
10 | 80 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083
10 | 80 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083
10 | 113 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 0.99583 | 0.99583
10 | 113 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 0.99583 | 1
10 | 113 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 0.9875 | 0.99167
11 | 117 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1
11 | 117 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1
12 | 121 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875
12 | 121 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875
12 | 121 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
12 | 121 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875
13 | 84 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
13 | 123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042
13 | 123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042
13 | 123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042
13 | 123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042
14 | 86 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583
14 | 86 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583
15 | 87 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
15 | 87 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1 | 1
15 | 126 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
15 | 126 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
15 | 126 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
16 | 47 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875
17 | 88 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 1 | 1.0042 | 1.0042 | 1 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.9875
17 | 88 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 1 | 1.0042 | 1.0042 | 1 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.9875
17 | 128 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
17 | 128 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
18 | 133 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0167
18 | 133 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0083 | 1.0167
18 | 133 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0083 | 1.0167
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 0.9875 | 0.99167 | 0.99167
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 0.9875 | 0.99167 | 0.99167
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 0.9875 | 0.99167 | 0.99167
20 | 141 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1.0042
20 | 141 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1.0042
21 | 142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042
21 | 142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1.0042
22 | 146 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0125
23 | 149 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97917 | 0.97917
23 | 149 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.97917
23 | 149 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97917 | 0.97917
24 | 98 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.97917
24 | 98 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.97917
24 | 150 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
24 | 150 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
25 | 151 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167
25 | 151 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167
25 | 151 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875
29 | 102 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 1 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1 | 1 | 1 | 1.0083 | 1.0083 | 1
29 | 159 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
29 | 159 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
31 | 72 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.99583
31 | 72 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 1 | 1 | 1 | 0.99583 | 0.99167 | 0.99583
31 | 162 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
31 | 162 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
32 | 104 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583
32 | 104 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583
32 | 108 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1 | 1.0042
33 | 163 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0042 | 1.0083
33 | 163 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0042 | 1.0083
34 | 107 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0083 | 1.0125 | 1.0208 | 1.0167 | 1.0125 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0083 | 1.0083 | 1.0083 | 1.0167 | 1.025 | 1.0125
34 | 107 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 0.99583 | 1 | 1.0083 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1 | 1 | 1 | 1.0083 | 1.0167 | 1.0042
34 | 169 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083
34 | 169 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083
35 | 171 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
35 | 171 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
36 | 109 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875
36 | 109 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 1 | 1
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 1 | 1
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 1 | 1
39 | 114 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
39 | 114 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583
39 | 114 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
40 | 115 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125
40 | 115 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125
41 | 81 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.97917 | 0.98333 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.97917
41 | 81 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.98333 | 0.97917
41 | 116 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583
41 | 116 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583
42 | 118 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
43 | 82 | 0.96667 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.97083 | 0.97083 | 0.975 | 0.975 | 0.97083 | 0.975 | 0.97917 | 0.97917 | 0.975 | 0.975 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.95833
43 | 82 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.95833 | 0.96667 | 0.97083 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.975 | 0.975 | 0.97083 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625 | 0.95833
43 | 119 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
44 | 120 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
44 | 120 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167
44 | 120 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875
44 | 120 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
45 | 85 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97917 | 0.975
45 | 85 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97917 | 0.975
45 | 124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1
45 | 124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
45 | 124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1
46 | 125 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167
46 | 125 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
46 | 125 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
47 | 127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
47 | 127 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1
47 | 127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
48 | 129 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
48 | 129 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.99167 | 0.99167
48 | 129 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
49 | 130 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583
49 | 130 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1
49 | 130 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 0.99583 | 0.99583 | 1
49 | 130 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583
50 | 89 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.95833 | 0.9625 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.97083 | 0.97083 | 0.96667 | 0.96667 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.95833
50 | 89 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625 | 0.9625 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.975 | 0.97083 | 0.97083 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625
50 | 89 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625 | 0.9625 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.975 | 0.97083 | 0.97083 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625
51 | 90 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.975
52 | 132 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1.0042 | 1.0042
53 | 134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1
53 | 134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1
53 | 134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1
55 | 135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
55 | 135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
55 | 135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
55 | 135 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
56 | 136 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
56 | 136 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
56 | 136 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
57 | 93 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
57 | 93 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
57 | 138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
57 | 138 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
57 | 138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583
59 | 143 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042
59 | 143 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042
60 | 144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
60 | 144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
62 | 152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
62 | 152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1
62 | 152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
63 | 153 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
63 | 153 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
64 | 154 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.99167
64 | 154 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.9875
65 | 155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1
65 | 155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1
65 | 155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1
66 | 156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042
66 | 156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
68 | 157 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
68 | 157 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
69 | 101 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
71 | 161 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
71 | 161 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
73 | 165 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
73 | 165 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
74 | 166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1
74 | 166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1
75 | 167 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
75 | 167 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083
75 | 167 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083
76 | 168 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583
76 | 168 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 1 | 0.99583 | 0.99167 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583
76 | 168 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917
78 | 170 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
78 | 170 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
79 | 172 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
79 | 172 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
81 | 116 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0083 | 1.0125 | 1.0083 | 1.0042 | 1.0125
81 | 116 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0083 | 1.0125 | 1.0083 | 1.0042 | 1.0125
82 | 119 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
82 | 119 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
82 | 119 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1 | 1
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1 | 1
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1 | 1
88 | 128 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042
88 | 128 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042
89 | 131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1
89 | 131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1
89 | 131 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042
92 | 137 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1.0042 | 1.0083
92 | 137 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1.0042 | 1.0083
95 | 145 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.025
95 | 145 | 1.0125 | 1.0167 | 1.0167 | 1.0125 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167
95 | 145 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0125 | 1.0167 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208
97 | 147 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0125
101 | 158 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083
101 | 158 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083
103 | 160 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
103 | 160 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083
105 | 164 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
105 | 164 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083

## Transf Data
fbus | tbus | Manufacture year | Commissioning year | Annual maximum loading [MVA] | Voltage ratio [kV] | Insulation medium | Cooling system | Transformer type | Indoor/Outdoor | Criticallity indicator | Time over rating 50% [%] | Clients affected [MVA] | ENS in fault [MWh] | Mean load [%] | Value of lost load [k€/MWh]
8 | 36 | 2016 | 2018 | 69.9 | 220/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 18.1 | Between 2 and 5
8 | 109 | 2001 | 2003 | 54 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.295 | 0 | 24.9 | Between 2 and 5
9 | 112 | 2007 | 2007 | 36.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.325 | 0 | 20.9 | Between 2 and 5
9 | 112 | 2004 | 2005 | 36 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.665 | 0 | 20.4 | Between 2 and 5
9 | 112 | 2010 | 2010 | 35 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.925 | 0 | 19.8 | Between 2 and 5
9 | 112 | 1978 | 1978 | 34.1 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.12 | 0 | 20.1 | Between 2 and 5
10 | 80 | 1999 | 2009 | 81.7 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 19.2 | Between 2 and 5
10 | 80 | 2002 | 2002 | 82 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 19.2 | Between 2 and 5
10 | 113 | 1981 | 1983 | 17 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.635 | 0 | 25.3 | Between 2 and 5
10 | 113 | 1974 | 2005 | 23.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.485 | 0 | 27.8 | Between 2 and 5
10 | 113 | 2011 | 2011 | 40.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.26 | 0 | 24 | Between 2 and 5
11 | 117 | 2016 | 2016 | 29.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.11 | 0 | 16 | Between 2 and 5
11 | 117 | 1996 | 2016 | 30.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.93 | 0 | 16.6 | Between 2 and 5
12 | 121 | 1991 | 1991 | 50.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.705 | 0 | 31.5 | Between 2 and 5
12 | 121 | 2003 | 2004 | 38.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.95 | 0 | 23.8 | Between 2 and 5
12 | 121 | 1982 | 1983 | 23.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.045 | 0 | 28.6 | Between 2 and 5
12 | 121 | 1993 | 2015 | 38.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.4 | 0 | 23.3 | Between 2 and 5
13 | 84 | 2003 | 2014 | 212.7 | 400/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 28.9 | Between 2 and 5
13 | 123 | 1975 | 1980 | 49.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.74 | 0 | 22 | Between 2 and 5
13 | 123 | 1975 | 1980 | 50.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 28.495 | 0 | 22.6 | Between 2 and 5
13 | 123 | 1992 | 1992 | 48.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.515 | 0 | 21.8 | Between 2 and 5
13 | 123 | 2011 | 2011 | 48.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.5 | 0 | 21.8 | Between 2 and 5
14 | 86 | 1977 | 1979 | 162.8 | 400/150 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 23.1 | Between 2 and 5
14 | 86 | 1977 | 1981 | 162.6 | 400/150 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 23 | Between 2 and 5
15 | 87 | 1985 | 1986 | 67.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.4 | Between 2 and 5
15 | 87 | 1993 | 1994 | 68.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.5 | Between 2 and 5
15 | 126 | 2017 | 2019 | 54.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 44.525 | 0 | 35.3 | Between 2 and 5
15 | 126 | 1978 | 1980 | 19.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.59 | 0 | 13 | Between 2 and 5
15 | 126 | 1978 | 1981 | 19.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.66 | 0 | 13.1 | Between 2 and 5
16 | 47 | 2011 | 2011 | 54.9 | 220/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 15 | - | 0 | 11 | Between 2 and 5
17 | 88 | 1987 | 1988 | 70.1 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.4 | Between 2 and 5
17 | 88 | 1986 | 1987 | 70.1 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.4 | Between 2 and 5
17 | 128 | 1982 | 1984 | 71.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 51.11 | 0 | 42.6 | Between 2 and 5
17 | 128 | 1980 | 1980 | 71.1 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 50.565 | 0 | 40.1 | Between 2 and 5
18 | 133 | 2004 | 2005 | 28.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.23 | 0 | 10.1 | Between 2 and 5
18 | 133 | 1986 | 1987 | 26.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.9 | 0 | 12.7 | Between 2 and 5
18 | 133 | 1986 | 1987 | 26.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.58 | 0 | 12.4 | Between 2 and 5
19 | 140 | 1968 | 1999 | 34.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 20.94 | 0 | 33.2 | Between 2 and 5
19 | 140 | 1985 | 1986 | 29.1 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.485 | 0 | 27.7 | Between 2 and 5
19 | 140 | 1976 | 1992 | 32.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 19.465 | 0 | 30.9 | Between 2 and 5
20 | 141 | 2005 | 2008 | 60.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.745 | 0 | 20.4 | Between 2 and 5
20 | 141 | 2007 | 2007 | 60.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.45 | 0 | 20.3 | Between 2 and 5
21 | 142 | 2014 | 2014 | 67.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.505 | 0 | 18.5 | Between 2 and 5
21 | 142 | 2007 | 2015 | 72.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 33.93 | 0 | 20 | Between 2 and 5
22 | 146 | 2016 | 2017 | 16.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | 7.885 | 16 | 6.3 | Between 2 and 5
23 | 149 | 2006 | 2007 | 54.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.115 | 0 | 30.3 | Between 2 and 5
23 | 149 | 1995 | 1995 | 53.9 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.49 | 0 | 29.8 | Between 2 and 5
23 | 149 | 1992 | 1992 | 53.2 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.57 | 0 | 29 | Between 2 and 5
24 | 98 | 2005 | 2006 | 86.3 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.6 | Between 2 and 5
24 | 98 | 2009 | 2009 | 88.2 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
24 | 150 | 1982 | 2004 | 20.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.74 | 0 | 13.9 | Between 2 and 5
24 | 150 | 1982 | 1992 | 15.7 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 6.635 | 0 | 10.5 | Between 2 and 5
25 | 151 | 1993 | 1996 | 74.7 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 50.345 | 0 | 40 | Between 2 and 5
25 | 151 | 1996 | 1996 | 77.8 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 52.225 | 0 | 41.4 | Between 2 and 5
25 | 151 | 2007 | 2007 | 82.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 54.86 | 0 | 32.3 | Between 2 and 5
29 | 102 | 2009 | 2009 | 108.2 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 16.3 | Between 2 and 5
29 | 159 | 2008 | 2008 | 45.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.185 | 0 | 14.2 | Between 2 and 5
29 | 159 | 2004 | 2006 | 43.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 23.085 | 0 | 13.6 | Between 2 and 5
31 | 72 | 2007 | 2007 | 61.4 | 220/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 18.3 | Between 2 and 5
31 | 72 | 2010 | 2011 | 56.9 | 220/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 17 | Between 2 and 5
31 | 162 | 1986 | 2007 | 17.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.15 | 0 | 14.5 | Between 2 and 5
31 | 162 | 2009 | 2010 | 28.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.405 | 0 | 12.2 | Between 2 and 5
32 | 104 | 2008 | 2008 | 118.5 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 15.2 | Between 2 and 5
32 | 104 | 2008 | 2008 | 118.5 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 15.2 | Between 2 and 5
32 | 108 | 2009 | 2009 | 26.1 | 150/130 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | - | 11.8 | 8.1 | Between 2 and 5
33 | 163 | 2008 | 2008 | 94 | 150/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 10 | 33.935 | 0 | 19.9 | Between 2 and 5
33 | 163 | 2011 | 2011 | 94 | 150/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 10 | 33.91 | 0 | 19.9 | Between 2 and 5
34 | 107 | 2010 | 2011 | 79.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12 | Between 2 and 5
34 | 107 | 2016 | 2017 | 61.9 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.3 | Between 2 and 5
34 | 169 | 2010 | 2011 | 18.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.165 | 0 | 7.3 | Between 2 and 5
34 | 169 | 2011 | 2011 | 18.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.09 | 0 | 7.2 | Between 2 and 5
35 | 171 | 1974 | 2009 | 32.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | B | 15 | 21.205 | 0 | 33.7 | Between 2 and 5
35 | 171 | 1972 | 2014 | 34.7 | 150/63 | Oil | ONAN | Transformer (1 three-phase unit) | Outdoor | B | 15 | 22.05 | 0 | 35 | Between 2 and 5
36 | 109 | 2003 | 2003 | 61.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 46.66 | 0 | 27.4 | Between 2 and 5
36 | 109 | 2009 | 2009 | 60.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 46.125 | 0 | 27.1 | Between 2 and 5
37 | 110 | 1997 | 1998 | 62.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.87 | 0 | 25.2 | Between 2 and 5
37 | 110 | 2002 | 2002 | 62.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.63 | 0 | 25.1 | Between 2 and 5
37 | 110 | 2009 | 2009 | 54.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.485 | 0 | 22 | Between 2 and 5
38 | 111 | 2010 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.715 | 0 | 22.2 | Between 2 and 5
38 | 111 | 2011 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.715 | 0 | 22.2 | Between 2 and 5
38 | 111 | 2010 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.675 | 0 | 22.2 | Between 2 and 5
39 | 114 | 1981 | 1982 | 53.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.48 | 0 | 25.8 | Between 2 and 5
39 | 114 | 2015 | 2015 | 47.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.425 | 0 | 17.3 | Between 2 and 5
39 | 114 | 2006 | 2009 | 50.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.385 | 0 | 24.1 | Between 2 and 5
40 | 115 | 1973 | 2014 | 19 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 8.89 | 0 | 7.4 | Between 2 and 5
40 | 115 | 2016 | 2016 | 16.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.98 | 0 | 6.3 | Between 2 and 5
41 | 81 | 2014 | 2014 | 74.8 | 400/220 | Oil | ONAF | Autotransformer (1 three-phase unit) | Indoor | C | 0 | - | 0 | 6.9 | Between 2 and 5
41 | 81 | 2011 | 2013 | 74.5 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Indoor | C | 0 | - | 0 | 6.9 | Between 2 and 5
41 | 116 | 2008 | 2008 | 67.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 51.32 | 0 | 30.2 | Between 2 and 5
41 | 116 | 2007 | 2007 | 66.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.44 | 0 | 29.7 | Between 2 and 5
42 | 118 | 1989 | 2003 | 23.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.29 | 0 | 13.7 | Between 2 and 5
42 | 118 | 1983 | 2016 | 11.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.61 | 0 | 13.7 | Between 2 and 5
42 | 118 | 1992 | 2016 | 11.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.36 | 0 | 13.3 | Between 2 and 5
42 | 118 | 1983 | 2002 | 22.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.11 | 0 | 12.8 | Between 2 and 5
43 | 82 | 2002 | 2003 | 205.5 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 34.4 | Between 2 and 5
43 | 82 | 2008 | 2008 | 157.6 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 26 | Between 2 and 5
43 | 119 | 2011 | 2012 | 25.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.885 | 0 | 10.5 | Between 2 and 5
44 | 120 | 2007 | 2008 | 51.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.145 | 0 | 21.8 | Between 2 and 5
44 | 120 | 1982 | 1983 | 55.6 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.815 | 0 | 31.6 | Between 2 and 5
44 | 120 | 1994 | 1994 | 54.8 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.48 | 0 | 31.3 | Between 2 and 5
44 | 120 | 1993 | 1994 | 52.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.57 | 0 | 30.6 | Between 2 and 5
45 | 85 | 1977 | 1981 | 199 | 400/220 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 26.8 | Between 2 and 5
45 | 85 | 1977 | 1979 | 197.5 | 400/220 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 26.6 | Between 2 and 5
45 | 124 | 1989 | 1991 | 47.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.085 | 0 | 19.1 | Between 2 and 5
45 | 124 | 1980 | 1981 | 50.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.145 | 0 | 20 | Between 2 and 5
45 | 124 | 2016 | 2016 | 47.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.73 | 0 | 19.6 | Between 2 and 5
46 | 125 | 2016 | 2016 | 40.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.89 | 0 | 17.6 | Between 2 and 5
46 | 125 | 1973 | 1973 | 49.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.165 | 0 | 30.2 | Between 2 and 5
46 | 125 | 1979 | 1980 | 50.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.12 | 0 | 31 | Between 2 and 5
47 | 127 | 1980 | 1982 | 57.8 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 33.94 | 0 | 26.9 | Between 2 and 5
47 | 127 | 2015 | 2015 | 47.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 28.24 | 0 | 16.6 | Between 2 and 5
47 | 127 | 2000 | 2013 | 55.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.475 | 0 | 25.8 | Between 2 and 5
48 | 129 | 1983 | 1984 | 64.4 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 44.47 | 0 | 37.1 | Between 2 and 5
48 | 129 | 1981 | 1983 | 67 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 46.255 | 0 | 36.7 | Between 2 and 5
48 | 129 | 2008 | 2008 | 56.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.89 | 0 | 22.9 | Between 2 and 5
49 | 130 | 1985 | 1986 | 67.4 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 52.255 | 0 | 43.5 | Between 2 and 5
49 | 130 | 1983 | 1984 | 68.2 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 52.525 | 0 | 43.8 | Between 2 and 5
49 | 130 | 1985 | 1986 | 67 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 51.395 | 0 | 42.8 | Between 2 and 5
49 | 130 | 1993 | 1994 | 67.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 51.985 | 0 | 41.2 | Between 2 and 5
50 | 89 | 2011 | 2011 | 150 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 21.1 | Between 2 and 5
50 | 89 | 1991 | 1992 | 187.4 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 26.4 | Between 2 and 5
50 | 89 | 1984 | 1986 | 182.2 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 25.9 | Between 2 and 5
51 | 90 | 2010 | 2010 | 70.9 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 8.3 | Between 2 and 5
52 | 132 | 2001 | 2001 | 38.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.515 | 0 | 17.9 | Between 2 and 5
53 | 134 | 2010 | 2011 | 38.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.735 | 0 | 11 | Between 2 and 5
53 | 134 | 1995 | 1996 | 43.1 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.83 | 0 | 16.5 | Between 2 and 5
53 | 134 | 2007 | 2007 | 38.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.635 | 0 | 11 | Between 2 and 5
55 | 135 | 1994 | 1994 | 70.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 44.18 | 0 | 26 | Between 2 and 5
55 | 135 | 1979 | 1995 | 50.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.49 | 0 | 26.3 | Between 2 and 5
55 | 135 | 1982 | 1995 | 51.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.05 | 0 | 26.7 | Between 2 and 5
55 | 135 | 2011 | 2012 | 49.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.69 | 0 | 18.1 | Between 2 and 5
56 | 136 | 2002 | 2002 | 84.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.855 | 0 | 31.7 | Between 2 and 5
56 | 136 | 2003 | 2003 | 83.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.535 | 0 | 31.5 | Between 2 and 5
56 | 136 | 2003 | 2003 | 84.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.965 | 0 | 31.8 | Between 2 and 5
57 | 93 | 1991 | 1991 | 112.6 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
57 | 93 | 1989 | 1990 | 111.7 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
57 | 138 | 2000 | 2001 | 26.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.11 | 0 | 14.4 | Between 2 and 5
57 | 138 | 2009 | 2009 | 25.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.13 | 0 | 10.1 | Between 2 and 5
57 | 138 | 2017 | 2019 | 97.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 66.675 | 0 | 39.2 | Between 2 and 5
58 | 139 | 1998 | 1999 | 68.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.52 | 0 | 25 | Between 2 and 5
58 | 139 | 2004 | 2005 | 69.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.615 | 0 | 25.1 | Between 2 and 5
58 | 139 | 2006 | 2006 | 70.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 43.285 | 0 | 25.4 | Between 2 and 5
59 | 143 | 2015 | 2015 | 25.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.69 | 0 | 9.8 | Between 2 and 5
59 | 143 | 2015 | 2015 | 25.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.665 | 0 | 9.8 | Between 2 and 5
60 | 144 | 2008 | 2008 | 35.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.105 | 0 | 10.6 | Between 2 and 5
60 | 144 | 1993 | 1993 | 39.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.03 | 0 | 15.9 | Between 2 and 5
62 | 152 | 2010 | 2010 | 23.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.32 | 0 | 9.8 | Between 2 and 5
62 | 152 | 1992 | 2011 | 24 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.36 | 0 | 9.8 | Between 2 and 5
62 | 152 | 1983 | 2002 | 12.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 6.53 | 0 | 10.4 | Between 2 and 5
63 | 153 | 1994 | 1995 | 5.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 3.13 | 0 | 4.9 | Between 2 and 5
63 | 153 | 1992 | 1993 | 5.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 3.045 | 0 | 4.8 | Between 2 and 5
64 | 154 | 1990 | 2005 | 49.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.545 | 0 | 27.4 | Between 2 and 5
64 | 154 | 2006 | 2006 | 49.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.795 | 0 | 27.6 | Between 2 and 5
65 | 155 | 2009 | 2010 | 35.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.735 | 0 | 14.1 | Between 2 and 5
65 | 155 | 2015 | 2015 | 44.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.96 | 0 | 17.4 | Between 2 and 5
65 | 155 | 2016 | 2016 | 43.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.59 | 0 | 17.2 | Between 2 and 5
66 | 156 | 2006 | 2008 | 78.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.855 | 0 | 21.7 | Between 2 and 5
66 | 156 | 2012 | 2012 | 77.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.3 | 0 | 21.4 | Between 2 and 5
68 | 157 | 2011 | 2011 | 43.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.03 | 0 | 18.3 | Between 2 and 5
68 | 157 | 2011 | 2012 | 44.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.175 | 0 | 18.3 | Between 2 and 5
69 | 101 | 2007 | 2007 | 138.8 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 14.5 | Between 2 and 5
71 | 161 | 2006 | 2007 | 82.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.03 | 0 | 15.9 | Between 2 and 5
71 | 161 | 2010 | 2010 | 78.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.895 | 0 | 15.2 | Between 2 and 5
73 | 165 | 2005 | 2011 | 20.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.95 | 0 | 7.1 | Between 2 and 5
73 | 165 | 2007 | 2008 | 21.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.47 | 0 | 7.5 | Between 2 and 5
74 | 166 | 2010 | 2010 | 62.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.465 | 0 | 13.2 | Between 2 and 5
74 | 166 | 2008 | 2008 | 62 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.36 | 0 | 13.1 | Between 2 and 5
75 | 167 | 2015 | 2015 | 15.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.875 | 0 | 4.6 | Between 2 and 5
75 | 167 | 1969 | 2009 | 19.7 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 9.505 | 0 | 7.9 | Between 2 and 5
75 | 167 | 1973 | 2008 | 19.1 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 9.25 | 0 | 7.7 | Between 2 and 5
76 | 168 | 2010 | 2011 | 20.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.98 | 0 | 7.6 | Between 2 and 5
76 | 168 | 2010 | 2011 | 20.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 13.125 | 0 | 7.7 | Between 2 and 5
76 | 168 | 2017 | 2019 | 127.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 60 | 86.385 | 0 | 50.8 | Between 2 and 5
77 | 106 | 2011 | 2011 | 130.2 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.3 | Between 2 and 5
77 | 106 | 2009 | 2010 | 132 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.5 | Between 2 and 5
77 | 106 | 2010 | 2010 | 129.9 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.3 | Between 2 and 5
78 | 170 | 2016 | 2018 | 30.4 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 10.49 | 0 | 8.3 | Between 2 and 5
78 | 170 | 2009 | 2009 | 31 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 10.675 | 0 | 8.5 | Between 2 and 5
79 | 172 | 2007 | 2012 | 12.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.025 | 0 | 5.6 | Between 2 and 5
79 | 172 | 1990 | 2012 | 13.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.425 | 0 | 5.9 | Between 2 and 5
81 | 116 | 2012 | 2013 | 76.5 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Indoor | C | 0 | 64.33 | 0 | 37.8 | Between 2 and 5
81 | 116 | 2012 | 2013 | 76.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Indoor | C | 0 | 64.43 | 0 | 37.9 | Between 2 and 5
82 | 119 | 1995 | 2003 | 83.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.84 | 0 | 29.9 | Between 2 and 5
82 | 119 | 2002 | 2003 | 82.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.235 | 0 | 29.6 | Between 2 and 5
82 | 119 | 2009 | 2009 | 82.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.595 | 0 | 29.8 | Between 2 and 5
83 | 122 | 2005 | 2006 | 81.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.345 | 0 | 32.6 | Between 2 and 5
83 | 122 | 2008 | 2008 | 82.2 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.56 | 0 | 32.7 | Between 2 and 5
83 | 122 | 2010 | 2011 | 81.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.155 | 0 | 32.5 | Between 2 and 5
88 | 128 | 1988 | 1989 | 85.7 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 58.295 | 0 | 34.3 | Between 2 and 5
88 | 128 | 1993 | 1993 | 85.7 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 58.31 | 0 | 34.3 | Between 2 and 5
89 | 131 | 2011 | 2012 | 42.5 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.925 | 0 | 12.9 | Between 2 and 5
89 | 131 | 1995 | 1996 | 42.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.1 | 0 | 13 | Between 2 and 5
89 | 131 | 1992 | 1993 | 41.1 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.205 | 0 | 12.5 | Between 2 and 5
92 | 137 | 2011 | 2013 | 66.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 40.425 | 0 | 23.8 | Between 2 and 5
92 | 137 | 2013 | 2013 | 64.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.97 | 0 | 23.5 | Between 2 and 5
95 | 145 | 2018 | 2019 | 59.4 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 33.465 | 0 | 19.7 | Between 2 and 5
95 | 145 | 2008 | 2008 | 14.2 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.415 | 0 | 5.5 | Between 2 and 5
95 | 145 | 2001 | 2002 | 13.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.485 | 0 | 5 | Between 2 and 5
97 | 147 | 2016 | 2017 | 81.9 | 400/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | 51.65 | 81 | 30.4 | Between 2 and 5
101 | 158 | 2006 | 2006 | 51.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.245 | 0 | 18.4 | Between 2 and 5
101 | 158 | 2011 | 2011 | 50.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.025 | 0 | 18.2 | Between 2 and 5
103 | 160 | 2009 | 2010 | 43.4 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.38 | 0 | 15.5 | Between 2 and 5
103 | 160 | 2009 | 2010 | 43.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.46 | 0 | 15.6 | Between 2 and 5
105 | 164 | 2007 | 2007 | 36.6 | 400/63 | Oil | ODAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 18.275 | 0 | 10.8 | Between 2 and 5
105 | 164 | 2011 | 2011 | 36.1 | 400/63 | Oil | ODAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 18.03 | 0 | 10.6 | Between 2 and 5

## Lines_Cables Data
fbus | tbus | Length (km) | Type of installation | Summer rating [MVA] | Spring rating [MVA] | Autumn rating [MVA] | Winter rating [MVA] | Conductor cross-sectional area [mm2] | Rated voltage [kV] | Conductor material | Criticallity indicator | Time over rating 50% [%] | Clients affected | ENS in fault [MWh] | Mean load [%] | Value of lost load [k€/MWh]
8 | 24 | 54 | overhead | 91 | 123 | 130 | 130 | Bear | 150 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
8 | 176 | 36.6 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 9.8 | Between 2 and 5
8 | 176 | 36.7 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 9.8 | Between 2 and 5
9 | 14 | 4.3 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
9 | 14 | 4.2 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
9 | 14 | 4.1 | overhead | 124 | 162 | 183 | 203 | Zebra | 150 | Al | C | 0 | - | 0 | 20.8 | Between 2 and 5
10 | 19 | 61.3 | overhead | 218 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 17.4 | Between 2 and 5
10 | 22 | 44.5 | overhead | 164 | 186 | 196 | 206 | Bear | 150 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
10 | 26 | 26 | overhead | 260 | 260 | 260 | 260 | 570 | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
11 | 14 | 36.7 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
11 | 14 | 36.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
12 | 22 | 61.6 | overhead | 189 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
12 | 23 | 49.8 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 5.5 | Between 2 and 5
12 | 29 | 27.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
12 | 29 | 27.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
12 | 29 | 42.8 | overhead | 260 | 260 | 260 | 260 | Zambeze | 150 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
12 | 34 | 68.7 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 5.2 | Between 2 and 5
13 | 14 | 23.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
13 | 14 | 23.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
13 | 20 | 13.6 | overhead | 195 | 204 | 214 | 221 | Bear | 150 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
13 | 20 | 13.6 | overhead | 195 | 204 | 214 | 221 | Bear | 150 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
13 | 180 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 5.4 | Between 2 and 5
13 | 246 | 12.2 | overhead | 260 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 3.5 | Between 2 and 5
14 | 180 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.9 | Between 2 and 5
14 | 185 | 20.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
14 | 186 | 48.4 | overhead | 185 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
14 | 246 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
15 | 22 | 63.4 | overhead | 224 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
15 | 22 | 63.4 | overhead | 224 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
15 | 26 | 32.6 | overhead | 260 | 260 | 260 | 260 | 570 | 150 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
15 | 27 | 50.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
15 | 28 | 60.7 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.3 | Between 2 and 5
15 | 29 | 95.6 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.2 | Between 2 and 5
15 | 183 | 12.8 | overhead | 340 | 340 | 340 | 340 | Zambeze | 150 | Al | B | 60 | - | 0 | 53.6 | Between 2 and 5
15 | 250 | 5.4 | overhead | 130 | 130 | 130 | 130 | Zebra | 150 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
15 | 250 | 5.5 | overhead | 130 | 130 | 130 | 130 | Zebra | 150 | Al | C | 0 | - | 0 | 10.1 | Between 2 and 5
15 | 255 | 5.9 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | A | 0 | 1 | 33.7 | 11.7 | Between 2 and 5
16 | 178 | 19 | overhead | 104 | 123 | 130 | 130 | Bear | 150 | Al | C | 0 | - | 0 | 6.8 | Between 2 and 5
17 | 21 | 37.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
17 | 21 | 35 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 8.8 | Between 2 and 5
17 | 25 | 35.2 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 21.5 | Between 2 and 5
17 | 184 | 16.6 | overhead | 91 | 108 | 121 | 134 | Panther | 150 | Al | C | 55 | - | 0 | 61.9 | Between 2 and 5
18 | 25 | 23.6 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 12.7 | Between 2 and 5
18 | 25 | 23.6 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 12.7 | Between 2 and 5
18 | 32 | 41.7 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 11.1 | Between 2 and 5
19 | 186 | 48.4 | overhead | 185 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
21 | 30 | 33.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
21 | 251 | 26.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
22 | 34 | 57.9 | overhead | 337 | 372 | 392 | 411 | Bear | 150 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
22 | 245 | 22 | overhead | 81 | 123 | 130 | 130 | Bear | 150 | Al | A | 0 | 1 | 36.2 | 31.4 | Between 2 and 5
23 | 34 | 35.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
23 | 34 | 35.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
23 | 34 | 42.7 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 11.3 | Between 2 and 5
24 | 31 | 46.5 | overhead | 520 | 520 | 520 | 520 | Zambeze | 150 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
24 | 35 | 88.8 | overhead | 253 | 273 | 285 | 296 | Zebra | 150 | Al | A | 0 | - | 66.3 | 15.5 | Between 2 and 5
24 | 181 | 7.8 | overhead | 189 | 195 | 195 | 195 | Bear | 150 | Al | C | 15 | - | 0 | 12.7 | Between 2 and 5
24 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
24 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
24 | 252 | 36.3 | overhead | 253 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.5 | Between 2 and 5
25 | 32 | 19.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 22.5 | Between 2 and 5
25 | 32 | 19.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 22.5 | Between 2 and 5
25 | 32 | 18 | overhead | 233 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 25.1 | Between 2 and 5
27 | 185 | 20.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
28 | 29 | 35.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
30 | 32 | 13.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
30 | 32 | 13.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
30 | 32 | 15.4 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
30 | 33 | 19.8 | overhead | 520 | 520 | 520 | 520 | Zambeze | 150 | Al | C | 0 | - | 0 | 9.5 | Between 2 and 5
30 | 174 | 13.8 | overhead | 260 | 260 | 260 | 260 | Zambeze | 150 | Al | C | 0 | - | 0 | 12.4 | Between 2 and 5
30 | 179 | 7.3 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 15 | - | 0 | 10.3 | Between 2 and 5
30 | 184 | 16.6 | overhead | 91 | 108 | 121 | 134 | Panther | 150 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
31 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
31 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
31 | 253 | 31.9 | overhead | 253 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
32 | 33 | 32.2 | overhead | 504 | 520 | 520 | 520 | Rail | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
32 | 254 | 53.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
32 | 254 | 53.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
33 | 173 | 3 | overhead | 306 | 321 | 335 | 348 | Zambeze | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
33 | 177 | 15.3 | overhead | 104 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 8.3 | Between 2 and 5
33 | 182 | 0.9 | overhead | 306 | 321 | 335 | 348 | Zambeze | 150 | Al | C | 45 | - | 0 | 29.5 | Between 2 and 5
33 | 184 | 19.3 | overhead | 274 | 291 | 307 | 322 | Zambeze | 150 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
36 | 64 | 52.3 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 17.3 | Between 2 and 5
36 | 71 | 48.9 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 24 | Between 2 and 5
36 | 187 | 0.7 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 2.4 | Between 2 and 5
36 | 188 | 0.7 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 5.7 | Between 2 and 5
36 | 189 | 0.8 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 5.8 | Between 2 and 5
37 | 59 | 10.4 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 11.9 | Between 2 and 5
37 | 213 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
37 | 214 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
37 | 215 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 5.7 | Between 2 and 5
37 | 216 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 20.8 | Between 2 and 5
38 | 208 | 3.2 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 12.9 | Between 2 and 5
38 | 209 | 3.2 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 15.2 | Between 2 and 5
39 | 45 | 106.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 19.9 | Between 2 and 5
39 | 69 | 43 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
39 | 69 | 43 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
39 | 71 | 22.2 | overhead | 684 | 727 | 762 | 762 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
39 | 78 | 41.1 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
39 | 195 | 30.4 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
39 | 199 | 54.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 18 | Between 2 and 5
39 | 258 | 20.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7.6 | Between 2 and 5
39 | 258 | 15.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 17 | Between 2 and 5
40 | 51 | 54.7 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.9 | Between 2 and 5
40 | 65 | 61.9 | overhead | 333 | 364 | 381 | 381 | Zebra | 220 | Al | C | 15 | - | 0 | 16.9 | Between 2 and 5
40 | 65 | 61.8 | overhead | 333 | 364 | 381 | 381 | Zebra | 220 | Al | C | 15 | - | 0 | 17.2 | Between 2 and 5
40 | 196 | 1 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
40 | 198 | 19.6 | overhead | 439 | 471 | 491 | 511 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
40 | 5 | 41.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.5 | Between 2 and 5
40 | 5 | 41.4 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
40 | 6 | 30.2 | overhead | 360 | 390 | 418 | 430 | Zebra | 220 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
41 | 53 | 10.4 | overhead | 381 | 381 | 381 | 381 | Zambeze | 220 | Al | C | 0 | - | 0 | 4.9 | Between 2 and 5
41 | 53 | 6.5 | overhead | 381 | 381 | 381 | 381 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.5 | Between 2 and 5
41 | 57 | 20.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.6 | Between 2 and 5
41 | 68 | 7 | overhead | 401 | 426 | 450 | 472 | Zambeze | 220 | Al | C | 0 | - | 0 | 6.1 | Between 2 and 5
41 | 68 | 10.7 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 9.2 | Between 2 and 5
41 | 210 | 9.4 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 9 | Between 2 and 5
41 | 211 | 37 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
42 | 78 | 28 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
42 | 78 | 28 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
42 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
42 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.7 | Between 2 and 5
43 | 58 | 12.6 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 11.7 | Between 2 and 5
43 | 76 | 11.1 | underground | 446 | 446 | 446 | 446 | 1600 | 220 | Cu | C | 0 | - | 0 | 14.2 | Between 2 and 5
43 | 76 | 11.1 | underground | 446 | 446 | 446 | 446 | 1600 | 220 | Cu | C | 0 | - | 0 | 14.2 | Between 2 and 5
43 | 204 | 9.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 2.3 | Between 2 and 5
43 | 205 | 3.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 12.1 | Between 2 and 5
43 | 219 | 5.4 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
44 | 48 | 24.9 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
44 | 66 | 50.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
44 | 66 | 50.7 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.4 | Between 2 and 5
44 | 193 | 31.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 21.4 | Between 2 and 5
45 | 46 | 40.2 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 14.2 | Between 2 and 5
45 | 46 | 38.8 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 15.8 | Between 2 and 5
45 | 46 | 38.8 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
45 | 74 | 36.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 21.7 | Between 2 and 5
45 | 199 | 54.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 19.5 | Between 2 and 5
46 | 50 | 25.4 | overhead | 381 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 18.9 | Between 2 and 5
46 | 64 | 34.8 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
46 | 214 | 30 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
46 | 216 | 28.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 16.8 | Between 2 and 5
46 | 222 | 0.8 | overhead | 438 | 438 | 438 | 438 | Zebra | 220 | Al | B | 55 | - | 0 | 44.6 | Between 2 and 5
46 | 260 | 56.8 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | A | 0 | 1 | 109.6 | 27 | Between 2 and 5
47 | 57 | 65 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
47 | 61 | 2.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
47 | 66 | 33.4 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.4 | Between 2 and 5
47 | 67 | 50 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
47 | 75 | 45 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.2 | Between 2 and 5
47 | 197 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
47 | 211 | 37 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
47 | 224 | 6.4 | overhead | 750 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
48 | 66 | 69.5 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.2 | Between 2 and 5
48 | 69 | 22.6 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 14.4 | Between 2 and 5
48 | 69 | 22 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.6 | Between 2 and 5
49 | 57 | 21.4 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
49 | 193 | 9.2 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 5.5 | Between 2 and 5
49 | 221 | 13.7 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 16.1 | Between 2 and 5
50 | 55 | 19.5 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13 | Between 2 and 5
50 | 55 | 15.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.6 | Between 2 and 5
50 | 56 | 27 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
50 | 204 | 9.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 22 | Between 2 and 5
50 | 213 | 13.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
50 | 215 | 19.7 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 4.9 | Between 2 and 5
50 | 217 | 11.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 8.8 | Between 2 and 5
51 | 66 | 45.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 66 | 46 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 194 | 29.4 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
51 | 194 | 29.5 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 197 | 2.2 | overhead | 825 | 864 | 902 | 938 | Rail | 220 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
51 | 224 | 6.4 | overhead | 750 | 762 | 762 | 762 | Zambeze | 220 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
52 | 199 | 3.6 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
53 | 68 | 6.6 | overhead | 401 | 426 | 450 | 472 | Zambeze | 220 | Al | C | 0 | - | 0 | 1.4 | Between 2 and 5
53 | 190 | 14.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
54 | 63 | 25.7 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
54 | 77 | 39.5 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.1 | Between 2 and 5
54 | 77 | 46.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
54 | 191 | 14.9 | overhead | 182 | 229 | 229 | 229 | Zebra | 220 | Al | C | 0 | - | 0 | 19.7 | Between 2 and 5
54 | 191 | 15.5 | overhead | 229 | 229 | 229 | 229 | Zambeze | 220 | Al | C | 0 | - | 0 | 19 | Between 2 and 5
54 | 192 | 19.4 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
54 | 200 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 0.2 | Between 2 and 5
54 | 201 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 6.8 | Between 2 and 5
54 | 202 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
54 | 203 | 0.2 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 15 | - | 0 | 21.9 | Between 2 and 5
55 | 58 | 7.8 | underground | 364 | 364 | 364 | 364 | 1240 | 220 | Cu | C | 0 | - | 0 | 15.5 | Between 2 and 5
55 | 204 | 2.6 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 20.3 | Between 2 and 5
55 | 205 | 3.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
56 | 74 | 46 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
56 | 205 | 8.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.5 | Between 2 and 5
57 | 60 | 20.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.8 | Between 2 and 5
57 | 67 | 15.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
57 | 190 | 14.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 22.8 | Between 2 and 5
57 | 210 | 9.4 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
57 | 220 | 10.4 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 13.4 | Between 2 and 5
57 | 221 | 13.7 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 14.7 | Between 2 and 5
58 | 219 | 6.2 | underground | 364 | 364 | 364 | 364 | 1200 | 220 | Cu | C | 0 | - | 0 | 10.7 | Between 2 and 5
59 | 217 | 12.5 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 7 | Between 2 and 5
60 | 66 | 12.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.4 | Between 2 and 5
60 | 206 | 0.2 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 7.1 | Between 2 and 5
60 | 207 | 0.3 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
62 | 212 | 12.5 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
62 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
62 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
62 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
62 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
63 | 194 | 74.1 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 11.3 | Between 2 and 5
65 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
65 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.8 | Between 2 and 5
65 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.2 | Between 2 and 5
65 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.2 | Between 2 and 5
66 | 218 | 0.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
69 | 70 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
70 | 197 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
71 | 78 | 66.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
71 | 78 | 66.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
72 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
72 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
73 | 77 | 45.6 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
73 | 79 | 52.6 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 4.5 | Between 2 and 5
75 | 79 | 34.2 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 3.2 | Between 2 and 5
75 | 267 | 0.4 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
77 | 192 | 26.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
77 | 192 | 26.2 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 10 | Between 2 and 5
78 | 223 | 13.2 | overhead | 342 | 364 | 383 | 402 | Zebra | 220 | Al | C | 10 | - | 0 | 21.5 | Between 2 and 5
78 | 258 | 20.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.9 | Between 2 and 5
80 | 87 | 59.4 | overhead | 1361 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 7.3 | Between 2 and 5
80 | 105 | 64.1 | overhead | 1361 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | A | 0 | - | 31.3 | 7.7 | Between 2 and 5
81 | 93 | 18.9 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.2 | Between 2 and 5
81 | 94 | 37 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3 | Between 2 and 5
82 | 85 | 69.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 22.4 | Between 2 and 5
82 | 89 | 18.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
82 | 100 | 40.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11.6 | Between 2 and 5
83 | 95 | 52.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
83 | 99 | 65.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
83 | 100 | 80.9 | overhead | 1363 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 24.1 | Between 2 and 5
83 | 101 | 101.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
84 | 86 | 28.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
84 | 100 | 83.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.9 | Between 2 and 5
85 | 95 | 86.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 18.8 | Between 2 and 5
85 | 99 | 81.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 21.1 | Between 2 and 5
86 | 87 | 96 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
86 | 97 | 15.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
86 | 226 | 48.1 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 8.3 | Between 2 and 5
87 | 102 | 97.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 14.7 | Between 2 and 5
87 | 226 | 48.1 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 18.9 | Between 2 and 5
87 | 234 | 12.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
87 | 235 | 12 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
87 | 236 | 12 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
88 | 93 | 29.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 23.8 | Between 2 and 5
88 | 93 | 34.1 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.3 | Between 2 and 5
88 | 96 | 59.6 | overhead | 1631 | 1711 | 1786 | 1856 | Zambeze | 400 | Al | C | 0 | - | 0 | 15.3 | Between 2 and 5
88 | 104 | 21.2 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
89 | 97 | 53.6 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
89 | 100 | 24.6 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
89 | 226 | 94.6 | overhead | 1386 | 1386 | 1386 | 1386 | 570 | 400 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
90 | 93 | 74.8 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 6.5 | Between 2 and 5
90 | 103 | 61.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
90 | 106 | 87.6 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
90 | 231 | 39.8 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
90 | 268 | 15.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3.9 | Between 2 and 5
91 | 104 | 33 | overhead | 1386 | 1386 | 1386 | 1386 | Zebra | 400 | Al | C | 0 | - | 0 | 12.2 | Between 2 and 5
91 | 104 | 33.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zebra | 400 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
91 | 229 | 3.2 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
91 | 229 | 3.1 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
91 | 230 | 6.6 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 5.8 | Between 2 and 5
92 | 93 | 23.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
92 | 95 | 111.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
93 | 94 | 46.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 2.9 | Between 2 and 5
93 | 101 | 85.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
95 | 101 | 63.7 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 13.6 | Between 2 and 5
95 | 241 | 12.7 | overhead | 528 | 528 | 528 | 528 | Zambeze | 400 | Al | B | 45 | - | 0 | 47.8 | Between 2 and 5
95 | 242 | 9.9 | overhead | 528 | 528 | 528 | 528 | Zambeze | 400 | Al | B | 30 | - | 0 | 25.9 | Between 2 and 5
96 | 104 | 39.1 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 21.2 | Between 2 and 5
96 | 232 | 0.4 | overhead | 350 | 350 | 350 | 350 | 1144 | 400 | Al | C | 15 | - | 0 | 20.3 | Between 2 and 5
96 | 233 | 0.4 | overhead | 350 | 350 | 350 | 350 | 1144 | 400 | Al | C | 45 | - | 0 | 30.6 | Between 2 and 5
96 | 1 | 1.1 | overhead | 1390 | 1400 | 1500 | 1660 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
96 | 1 | 1.1 | overhead | 1390 | 1400 | 1500 | 1660 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
98 | 99 | 40.9 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 12.4 | Between 2 and 5
98 | 3 | 25.7 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
99 | 237 | 0.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 40 | - | 0 | 36.1 | Between 2 and 5
99 | 238 | 0.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 40 | - | 0 | 36.1 | Between 2 and 5
99 | 243 | 0.2 | overhead | 505 | 505 | 505 | 505 | Zambeze | 400 | Al | C | 30 | - | 0 | 26.4 | Between 2 and 5
99 | 244 | 0.2 | overhead | 505 | 505 | 505 | 505 | Zambeze | 400 | Al | C | 30 | - | 0 | 19.8 | Between 2 and 5
100 | 239 | 0.3 | overhead | 438 | 438 | 438 | 438 | Zambeze | 400 | Al | B | 50 | - | 0 | 45.3 | Between 2 and 5
100 | 240 | 0.2 | overhead | 438 | 438 | 438 | 438 | Zambeze | 400 | Al | C | 25 | - | 0 | 34.1 | Between 2 and 5
101 | 103 | 60.6 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
102 | 107 | 81.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
105 | 227 | 1.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 12.9 | Between 2 and 5
105 | 228 | 0.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9 | Between 2 and 5
105 | 4 | 39.9 | overhead | 1280 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 14.8 | Between 2 and 5
106 | 225 | 29.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3.7 | Between 2 and 5
106 | 2 | 4.7 | overhead | 1469 | 1571 | 1641 | 1706 | Rail | 400 | Al | C | 0 | - | 0 | 13.9 | Between 2 and 5
107 | 7 | 33.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 8.6 | Between 2 and 5
115 | 269 | 27.1 | overhead | 68.4 | 95.7 | 95.7 | 95.7 | 235 | 63 | Al | C | 0 | - | 0 | 6.6 | Between 2 and 5
116 | 279 | 0.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
130 | 280 | 5.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
130 | 280 | 4.9 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 11.7 | Between 2 and 5
132 | 283 | 0.04 | overhead | 98.2 | 105.2 | 105.2 | 105.2 | 300 | 63 | Cu | C | 0 | - | 0 | 20.5 | Between 2 and 5
133 | 287 | 6.8 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 2.7 | Between 2 and 5
133 | 288 | 6.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 2.7 | Between 2 and 5
145 | 286 | 0.3 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
148 | 172 | 7.6 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.9 | Between 2 and 5
148 | 294 | 12.4 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 325 | 63 | Al | C | 0 | - | 0 | 2.9 | Between 2 and 5
165 | 272 | 12.9 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
165 | 298 | 39.8 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 0 | - | 0 | 2 | Between 2 and 5
165 | 300 | 34.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.6 | Between 2 and 5
167 | 297 | 2 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.2 | Between 2 and 5
172 | 304 | 11.8 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.6 | Between 2 and 5
173 | 174 | 8 | overhead | 274 | 291 | 307 | 322 | Zambeze | 150 | Al | C | 0 | - | 0 | 10.8 | Between 2 and 5
175 | 176 | 10.5 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 12 | Between 2 and 5
180 | 249 | 4.5 | overhead | 136 | 162 | 183 | 203 | Zebra | 150 | Al | A | 0 | 1 | 4 | 2.7 | Between 2 and 5
185 | 247 | 8.5 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
186 | 247 | 6.9 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | A | 0 | 1 | 1.8 | 0.6 | Between 2 and 5
190 | 256 | 1.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | A | 0 | 1 | 7.6 | 19.6 | Between 2 and 5
193 | 220 | 9.2 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
195 | 258 | 15.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 18.3 | Between 2 and 5
208 | 210 | 2.6 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 6.7 | Between 2 and 5
209 | 211 | 2.6 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.5 | Between 2 and 5
212 | 263 | 12.5 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10 | Between 2 and 5
212 | 266 | 0.3 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7 | Between 2 and 5
220 | 221 | 0.8 | overhead | 1204 | 1279 | 1350 | 1416 | Zambeze | 220 | Al | C | 0 | - | 0 | 17.3 | Between 2 and 5
223 | 262 | 13.2 | overhead | 342 | 364 | 383 | 402 | Zebra | 220 | Al | C | 0 | - | 0 | 13.3 | Between 2 and 5
223 | 265 | 0.1 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
224 | 264 | 3.6 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 17.7 | Between 2 and 5
269 | 270 | 0.1 | overhead | 68.4 | 95.7 | 95.7 | 95.7 | 235 | 63 | Al | C | 0 | - | 0 | 6.5 | Between 2 and 5
270 | 271 | 11 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
271 | 272 | 23.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
273 | 274 | 0.7 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 22 | Between 2 and 5
273 | 282 | 0.9 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | B | 0 | - | 0 | 16.2 | Between 2 and 5
274 | 275 | 1 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 22 | Between 2 and 5
275 | 276 | 18.9 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
276 | 277 | 0.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
277 | 278 | 1.6 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 21.9 | Between 2 and 5
278 | 279 | 6.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 10.9 | Between 2 and 5
280 | 281 | 3.9 | overhead | 126 | 142.6 | 142.6 | 142.6 | 325 | 63 | Al | B | 15 | - | 0 | 16.9 | Between 2 and 5
281 | 282 | 1.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | B | 0 | - | 0 | 16.2 | Between 2 and 5
283 | 284 | 18.1 | overhead | 89.5 | 127.8 | 127.8 | 127.8 | 400 | 63 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
284 | 285 | 0.3 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
285 | 286 | 6.2 | overhead | 89.5 | 127.8 | 127.8 | 127.8 | 400 | 63 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
287 | 288 | 0.1 | overhead | 128.1 | 158.8 | 158.8 | 158.8 | 1000 | 63 | Al | C | 0 | - | 0 | 1.7 | Between 2 and 5
287 | 289 | 3.5 | overhead | 53.2 | 60.1 | 60.1 | 60.1 | 235 | 63 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
289 | 290 | 3.2 | overhead | 60.6 | 68.5 | 68.5 | 68.5 | 288 | 63 | Al | C | 0 | - | 0 | 7.6 | Between 2 and 5
290 | 291 | 1 | overhead | 62.2 | 76.9 | 76.9 | 76.9 | 630 | 63 | Al | C | 0 | - | 0 | 6.7 | Between 2 and 5
291 | 292 | 0.2 | overhead | 62.2 | 76.9 | 76.9 | 76.9 | 630 | 63 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
292 | 293 | 18 | submarine | 80 | 80 | 80 | 80 | 1000 | 63 | Cu | C | 0 | - | 0 | 5.7 | Between 2 and 5
294 | 295 | 15.9 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
295 | 296 | 3.3 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 225 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
296 | 297 | 1.2 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
298 | 299 | 0.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.1 | Between 2 and 5
299 | 300 | 0.9 | overhead | 75.3 | 93.4 | 93.4 | 93.4 | 1000 | 63 | Al | C | 0 | - | 0 | 1 | Between 2 and 5
299 | 301 | 17.9 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.3 | Between 2 and 5
301 | 302 | 16.8 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.4 | Between 2 and 5
302 | 303 | 19.3 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.5 | Between 2 and 5
303 | 304 | 0.02 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.5 | Between 2 and 5

## Auxiliary Data
Downward | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
Urban | 0.1812% | 0.1129% | 0.06787% | 0.06991% | 0.07075% | 0.1147% | 0.2841% | 0.338% | 0.3094% | 0.2587% | 0.2719% | 0.2362% | 0.3118% | 0.3008% | 0.2268% | 0.2043% | 0.194% | 0.2214% | 0.1995% | 0.1947% | 0.1907% | 0.177% | 0.1853% | 0.1836%
Semi-urban | 0.1757% | 0.1583% | 0.1514% | 0.1585% | 0.1425% | 0.2051% | 0.3837% | 0.4028% | 0.344% | 0.1931% | 0.209% | 0.2298% | 0.3622% | 0.3385% | 0.1957% | 0.1863% | 0.2177% | 0.2639% | 0.1834% | 0.1943% | 0.1769% | 0.1553% | 0.1545% | 0.1402%
Rural | 0.2298% | 0.1194% | 0.03063% | 0.03207% | 0.03307% | 0.06153% | 0.1571% | 0.1814% | 0.2264% | 0.3104% | 0.2939% | 0.2207% | 0.2579% | 0.2898% | 0.2494% | 0.2176% | 0.1895% | 0.1967% | 0.2671% | 0.2743% | 0.2632% | 0.2403% | 0.2888% | 0.2594%
Upward | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
Urban | 0.2343% | 0.2258% | 0.1651% | 0.1699% | 0.1699% | 0.1929% | 0.2685% | 0.2152% | 0.1114% | 0.1593% | 0.1678% | 0.1916% | 0.1075% | 0.08918% | 0.1599% | 0.1595% | 0.1277% | 0.05462% | 0.02146% | 0.0212% | 0.04645% | 0.1553% | 0.2605% | 0.2629%
Semi-urban | 0.06505% | 0.06579% | 0.0606% | 0.06304% | 0.05822% | 0.0648% | 0.08405% | 0.07974% | 0.1064% | 0.2306% | 0.2413% | 0.1852% | 0.057% | 0.098% | 0.2258% | 0.2201% | 0.177% | 0.04429% | 0.04073% | 0.04443% | 0.04839% | 0.06203% | 0.07203% | 0.05832%
Rural | 0.3082% | 0.3331% | 0.3172% | 0.3286% | 0.3358% | 0.3446% | 0.368% | 0.2727% | 0.09782% | 0.05652% | 0.09736% | 0.2216% | 0.167% | 0.1115% | 0.1473% | 0.1485% | 0.137% | 0.0792% | 0.008639% | 0.007898% | 0.04642% | 0.2162% | 0.3727% | 0.3952%
Load per transmission node
Urban | 40%
Semi-urban | 40%
Rural | 20%

## Downward flexibility
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.050536 | 0.033805 | 0.023228 | 0.023718 | 0.022047 | 0.033774 | 0.073101 | 0.090363 | 0.097553 | 0.081594 | 0.08653 | 0.081641 | 0.11184 | 0.10902 | 0.078408 | 0.072629 | 0.073683 | 0.083536 | 0.072246 | 0.074007 | 0.069073 | 0.063471 | 0.063967 | 0.055081
109 | 0.30563 | 0.20444 | 0.14048 | 0.14344 | 0.13334 | 0.20425 | 0.44209 | 0.54647 | 0.53867 | 0.45055 | 0.4778 | 0.45082 | 0.61755 | 0.60196 | 0.43295 | 0.40104 | 0.40687 | 0.46127 | 0.39893 | 0.40865 | 0.38141 | 0.35048 | 0.38685 | 0.33311
110 | 0.2223 | 0.1487 | 0.10218 | 0.10433 | 0.096984 | 0.14857 | 0.32156 | 0.39748 | 0.42566 | 0.35602 | 0.37756 | 0.35624 | 0.48799 | 0.47567 | 0.34212 | 0.31691 | 0.32151 | 0.3645 | 0.31524 | 0.32292 | 0.30139 | 0.27695 | 0.28138 | 0.24229
111 | 0.15913 | 0.10645 | 0.073142 | 0.074683 | 0.069424 | 0.10635 | 0.23018 | 0.28453 | 0.31211 | 0.26105 | 0.27685 | 0.26121 | 0.35782 | 0.34879 | 0.25086 | 0.23237 | 0.23575 | 0.26727 | 0.23115 | 0.23678 | 0.221 | 0.20307 | 0.20142 | 0.17344
112 | 0.42535 | 0.28453 | 0.19551 | 0.19963 | 0.18557 | 0.28427 | 0.61527 | 0.76054 | 0.64395 | 0.5386 | 0.57119 | 0.53893 | 0.73825 | 0.71962 | 0.51757 | 0.47943 | 0.48639 | 0.55143 | 0.4769 | 0.48852 | 0.45595 | 0.41898 | 0.53839 | 0.4636
113 | 0.18921 | 0.12657 | 0.086968 | 0.088802 | 0.082548 | 0.12645 | 0.27369 | 0.33832 | 0.24521 | 0.2051 | 0.21751 | 0.20522 | 0.28112 | 0.27403 | 0.19709 | 0.18256 | 0.18521 | 0.20998 | 0.1816 | 0.18603 | 0.17363 | 0.15954 | 0.2395 | 0.20623
114 | 0.23524 | 0.15736 | 0.10812 | 0.1104 | 0.10263 | 0.15721 | 0.34027 | 0.42061 | 0.41899 | 0.35045 | 0.37165 | 0.35066 | 0.48035 | 0.46823 | 0.33676 | 0.31195 | 0.31648 | 0.35879 | 0.3103 | 0.31787 | 0.29667 | 0.27261 | 0.29775 | 0.25639
115 | 0.034593 | 0.023141 | 0.0159 | 0.016235 | 0.015092 | 0.023119 | 0.050038 | 0.061856 | 0.060503 | 0.050606 | 0.053667 | 0.050637 | 0.069364 | 0.067614 | 0.048629 | 0.045046 | 0.0457 | 0.05181 | 0.044808 | 0.045899 | 0.042841 | 0.039366 | 0.043786 | 0.037704
116 | 0.39407 | 0.2636 | 0.18113 | 0.18494 | 0.17192 | 0.26336 | 0.57001 | 0.70461 | 0.69912 | 0.58475 | 0.62013 | 0.5851 | 0.8015 | 0.78127 | 0.56192 | 0.5205 | 0.52806 | 0.59867 | 0.51776 | 0.53038 | 0.49502 | 0.45488 | 0.49879 | 0.4295
117 | 0.080619 | 0.053928 | 0.037055 | 0.037835 | 0.035171 | 0.053878 | 0.11661 | 0.14415 | 0.1442 | 0.12061 | 0.1279 | 0.12068 | 0.16531 | 0.16114 | 0.1159 | 0.10736 | 0.10891 | 0.12348 | 0.10679 | 0.10939 | 0.1021 | 0.09382 | 0.10204 | 0.087868
118 | 0.13567 | 0.090752 | 0.062358 | 0.063672 | 0.059187 | 0.090668 | 0.19624 | 0.24258 | 0.23535 | 0.19685 | 0.20876 | 0.19697 | 0.26982 | 0.26301 | 0.18916 | 0.17522 | 0.17777 | 0.20154 | 0.1743 | 0.17855 | 0.16664 | 0.15313 | 0.17172 | 0.14787
119 | 0.25569 | 0.17104 | 0.11752 | 0.12 | 0.11155 | 0.17088 | 0.36986 | 0.45719 | 0.4763 | 0.39838 | 0.42248 | 0.39862 | 0.54605 | 0.53227 | 0.38282 | 0.35461 | 0.35976 | 0.40786 | 0.35274 | 0.36134 | 0.33725 | 0.3099 | 0.32364 | 0.27868
120 | 0.35015 | 0.23422 | 0.16094 | 0.16433 | 0.15276 | 0.23401 | 0.50649 | 0.62608 | 0.62316 | 0.52122 | 0.55275 | 0.52153 | 0.71441 | 0.69638 | 0.50086 | 0.46395 | 0.47069 | 0.53362 | 0.4615 | 0.47275 | 0.44124 | 0.40545 | 0.4432 | 0.38163
121 | 0.24005 | 0.16058 | 0.11034 | 0.11266 | 0.10473 | 0.16043 | 0.34723 | 0.42922 | 0.42406 | 0.35469 | 0.37614 | 0.3549 | 0.48616 | 0.47389 | 0.34083 | 0.31571 | 0.3203 | 0.36313 | 0.31405 | 0.32171 | 0.30026 | 0.27591 | 0.30385 | 0.26164
122 | 0.31255 | 0.20907 | 0.14366 | 0.14668 | 0.13635 | 0.20888 | 0.4521 | 0.55884 | 0.53973 | 0.45144 | 0.47875 | 0.45171 | 0.61877 | 0.60315 | 0.43381 | 0.40184 | 0.40767 | 0.46219 | 0.39972 | 0.40946 | 0.38217 | 0.35117 | 0.39561 | 0.34065
123 | 0.18771 | 0.12556 | 0.086278 | 0.088096 | 0.081892 | 0.12545 | 0.27152 | 0.33563 | 0.3481 | 0.29115 | 0.30876 | 0.29132 | 0.39907 | 0.389 | 0.27978 | 0.25916 | 0.26292 | 0.29808 | 0.2578 | 0.26408 | 0.24647 | 0.22649 | 0.23759 | 0.20459
124 | 0.16094 | 0.10765 | 0.073971 | 0.07553 | 0.070212 | 0.10755 | 0.23279 | 0.28776 | 0.29185 | 0.24411 | 0.25888 | 0.24426 | 0.3346 | 0.32615 | 0.23458 | 0.21729 | 0.22045 | 0.24992 | 0.21615 | 0.22141 | 0.20665 | 0.18989 | 0.2037 | 0.17541
125 | 0.16936 | 0.11329 | 0.077843 | 0.079483 | 0.073886 | 0.11318 | 0.24498 | 0.30282 | 0.32997 | 0.27599 | 0.29269 | 0.27616 | 0.37829 | 0.36874 | 0.26521 | 0.24567 | 0.24924 | 0.28256 | 0.24437 | 0.25033 | 0.23364 | 0.21469 | 0.21437 | 0.18459
126 | 0.17447 | 0.11671 | 0.080194 | 0.081884 | 0.076117 | 0.1166 | 0.25237 | 0.31196 | 0.24548 | 0.20532 | 0.21774 | 0.20544 | 0.28143 | 0.27432 | 0.1973 | 0.18276 | 0.18542 | 0.21021 | 0.1818 | 0.18623 | 0.17381 | 0.15972 | 0.22084 | 0.19016
127 | 0.12514 | 0.083708 | 0.057518 | 0.05873 | 0.054594 | 0.083632 | 0.18101 | 0.22375 | 0.24255 | 0.20287 | 0.21514 | 0.20299 | 0.27806 | 0.27105 | 0.19495 | 0.18058 | 0.1832 | 0.2077 | 0.17963 | 0.18401 | 0.17174 | 0.15781 | 0.1584 | 0.13639
128 | 0.30172 | 0.20183 | 0.13868 | 0.1416 | 0.13163 | 0.20164 | 0.43643 | 0.53948 | 0.69859 | 0.58431 | 0.61965 | 0.58466 | 0.80089 | 0.78067 | 0.56149 | 0.52011 | 0.52766 | 0.59822 | 0.51737 | 0.52998 | 0.49464 | 0.45453 | 0.3819 | 0.32885
129 | 0.26923 | 0.1801 | 0.12375 | 0.12635 | 0.11746 | 0.17993 | 0.38944 | 0.48139 | 0.5464 | 0.45701 | 0.48466 | 0.45729 | 0.62641 | 0.6106 | 0.43917 | 0.4068 | 0.41271 | 0.46789 | 0.40465 | 0.41452 | 0.38688 | 0.35551 | 0.34078 | 0.29344
130 | 0.29811 | 0.19941 | 0.13702 | 0.13991 | 0.13006 | 0.19923 | 0.43121 | 0.53302 | 0.60583 | 0.50673 | 0.53738 | 0.50703 | 0.69455 | 0.67702 | 0.48694 | 0.45105 | 0.4576 | 0.51879 | 0.44867 | 0.45961 | 0.42897 | 0.39418 | 0.37733 | 0.32491
131 | 0.23795 | 0.15917 | 0.10937 | 0.11167 | 0.10381 | 0.15902 | 0.34418 | 0.42545 | 0.37341 | 0.31233 | 0.33122 | 0.31251 | 0.4281 | 0.41729 | 0.30013 | 0.27801 | 0.28205 | 0.31976 | 0.27655 | 0.28329 | 0.2644 | 0.24296 | 0.30118 | 0.25934
132 | 0.038806 | 0.025958 | 0.017836 | 0.018212 | 0.016929 | 0.025933 | 0.056132 | 0.069383 | 0.17724 | 0.14825 | 0.15722 | 0.14834 | 0.2032 | 0.19807 | 0.14246 | 0.13196 | 0.13388 | 0.15178 | 0.13127 | 0.13447 | 0.1255 | 0.11532 | 0.049118 | 0.042295
133 | 0.23163 | 0.15494 | 0.10646 | 0.10871 | 0.10105 | 0.1548 | 0.33505 | 0.41416 | 0.42939 | 0.35915 | 0.38087 | 0.35936 | 0.49227 | 0.47984 | 0.34512 | 0.31968 | 0.32433 | 0.36769 | 0.318 | 0.32575 | 0.30403 | 0.27938 | 0.29318 | 0.25246
134 | 0.20155 | 0.13482 | 0.092637 | 0.094589 | 0.087928 | 0.1347 | 0.29153 | 0.36037 | 0.38301 | 0.32036 | 0.33973 | 0.32055 | 0.4391 | 0.42801 | 0.30784 | 0.28516 | 0.2893 | 0.32798 | 0.28365 | 0.29057 | 0.2712 | 0.2492 | 0.25511 | 0.21967
135 | 0.21809 | 0.14589 | 0.10024 | 0.10235 | 0.095146 | 0.14575 | 0.31547 | 0.38995 | 0.42699 | 0.35714 | 0.37874 | 0.35735 | 0.48952 | 0.47716 | 0.34319 | 0.3179 | 0.32252 | 0.36564 | 0.31622 | 0.32393 | 0.30233 | 0.27782 | 0.27605 | 0.2377
136 | 0.24727 | 0.1654 | 0.11365 | 0.11605 | 0.10788 | 0.16525 | 0.35767 | 0.44213 | 0.48882 | 0.40886 | 0.43359 | 0.4091 | 0.56041 | 0.54627 | 0.39289 | 0.36394 | 0.36922 | 0.41859 | 0.36202 | 0.37084 | 0.34612 | 0.31805 | 0.31298 | 0.2695
137 | 0.15642 | 0.10464 | 0.071898 | 0.073413 | 0.068243 | 0.10454 | 0.22626 | 0.27969 | 0.34037 | 0.28469 | 0.30191 | 0.28485 | 0.39021 | 0.38036 | 0.27357 | 0.25341 | 0.25709 | 0.29146 | 0.25207 | 0.25821 | 0.241 | 0.22146 | 0.19799 | 0.17049
138 | 0.13597 | 0.090954 | 0.062496 | 0.063812 | 0.059319 | 0.090868 | 0.19668 | 0.24312 | 0.31878 | 0.26663 | 0.28276 | 0.26679 | 0.36546 | 0.35623 | 0.25621 | 0.23733 | 0.24078 | 0.27297 | 0.23608 | 0.24184 | 0.22571 | 0.20741 | 0.1721 | 0.1482
139 | 0.23584 | 0.15776 | 0.1084 | 0.11068 | 0.10289 | 0.15761 | 0.34114 | 0.42169 | 0.53734 | 0.44943 | 0.47662 | 0.4497 | 0.61602 | 0.60047 | 0.43188 | 0.40005 | 0.40586 | 0.46013 | 0.39794 | 0.40764 | 0.38047 | 0.34961 | 0.29851 | 0.25704
140 | 0.10408 | 0.069623 | 0.04784 | 0.048847 | 0.045407 | 0.069558 | 0.15055 | 0.1861 | 0.18631 | 0.15583 | 0.16526 | 0.15592 | 0.21359 | 0.2082 | 0.14974 | 0.13871 | 0.14072 | 0.15954 | 0.13798 | 0.14134 | 0.13192 | 0.12122 | 0.13174 | 0.11344
141 | 0.11732 | 0.078478 | 0.053923 | 0.055059 | 0.051182 | 0.078405 | 0.1697 | 0.20977 | 0.21829 | 0.18258 | 0.19363 | 0.18269 | 0.25026 | 0.24394 | 0.17545 | 0.16252 | 0.16488 | 0.18693 | 0.16167 | 0.1656 | 0.15457 | 0.14203 | 0.1485 | 0.12787
142 | 0.14078 | 0.094172 | 0.064707 | 0.066072 | 0.061419 | 0.094085 | 0.20364 | 0.25172 | 0.29639 | 0.2479 | 0.2629 | 0.24805 | 0.33979 | 0.33121 | 0.23822 | 0.22066 | 0.22387 | 0.2538 | 0.2195 | 0.22485 | 0.20986 | 0.19284 | 0.17819 | 0.15344
143 | 0.098366 | 0.065801 | 0.045212 | 0.046165 | 0.042914 | 0.06574 | 0.14228 | 0.17588 | 0.2039 | 0.17054 | 0.18086 | 0.17065 | 0.23376 | 0.22786 | 0.16388 | 0.1518 | 0.15401 | 0.1746 | 0.151 | 0.15469 | 0.14437 | 0.13267 | 0.12451 | 0.10721
144 | 0.077009 | 0.051513 | 0.035396 | 0.036142 | 0.033597 | 0.051466 | 0.11139 | 0.13769 | 0.16285 | 0.13621 | 0.14445 | 0.13629 | 0.1867 | 0.18199 | 0.13089 | 0.12125 | 0.12301 | 0.13945 | 0.12061 | 0.12355 | 0.11531 | 0.10596 | 0.097473 | 0.083933
145 | 0.29871 | 0.19981 | 0.1373 | 0.14019 | 0.13032 | 0.19963 | 0.43208 | 0.5341 | 0.43232 | 0.3616 | 0.38347 | 0.36181 | 0.49563 | 0.48312 | 0.34748 | 0.32187 | 0.32654 | 0.3702 | 0.32017 | 0.32798 | 0.30611 | 0.28129 | 0.37809 | 0.32557
146 | 0.012333 | 0.0082497 | 0.0056689 | 0.0057885 | 0.0053809 | 0.008242 | 0.017841 | 0.022053 | 0.025321 | 0.02118 | 0.022459 | 0.021191 | 0.029028 | 0.028295 | 0.020352 | 0.018852 | 0.019125 | 0.021683 | 0.018753 | 0.01921 | 0.017928 | 0.016475 | 0.01561 | 0.013442
147 | 0.071595 | 0.047892 | 0.032907 | 0.033601 | 0.031234 | 0.047846 | 0.10356 | 0.12801 | 0.14819 | 0.12395 | 0.13145 | 0.12403 | 0.1699 | 0.16561 | 0.11911 | 0.11033 | 0.11193 | 0.1269 | 0.10975 | 0.11242 | 0.10493 | 0.096421 | 0.090621 | 0.078032
149 | 0.24667 | 0.165 | 0.11338 | 0.11577 | 0.10761 | 0.16485 | 0.3568 | 0.44105 | 0.45657 | 0.38188 | 0.40499 | 0.38211 | 0.52344 | 0.51023 | 0.36697 | 0.33993 | 0.34486 | 0.39097 | 0.33813 | 0.34637 | 0.32328 | 0.29707 | 0.31222 | 0.26885
150 | 0.057756 | 0.038635 | 0.026546 | 0.027106 | 0.025197 | 0.038599 | 0.083544 | 0.10327 | 0.087158 | 0.072898 | 0.077308 | 0.072943 | 0.099921 | 0.097399 | 0.070051 | 0.064889 | 0.065832 | 0.074634 | 0.064548 | 0.066122 | 0.061714 | 0.056708 | 0.073105 | 0.06295
151 | 0.22501 | 0.15051 | 0.10342 | 0.1056 | 0.098165 | 0.15038 | 0.32547 | 0.40232 | 0.48376 | 0.40462 | 0.4291 | 0.40486 | 0.5546 | 0.54061 | 0.38882 | 0.36017 | 0.3654 | 0.41426 | 0.35827 | 0.367 | 0.34253 | 0.31475 | 0.28481 | 0.24524
152 | 0.081521 | 0.054532 | 0.037469 | 0.03826 | 0.035565 | 0.054481 | 0.11792 | 0.14576 | 0.16152 | 0.1351 | 0.14327 | 0.13518 | 0.18517 | 0.1805 | 0.12982 | 0.12025 | 0.122 | 0.13831 | 0.11962 | 0.12254 | 0.11437 | 0.10509 | 0.10318 | 0.088851
153 | 0.012032 | 0.0080485 | 0.0055309 | 0.0056467 | 0.0052495 | 0.0080415 | 0.017405 | 0.021515 | 0.021323 | 0.017834 | 0.018913 | 0.017846 | 0.024445 | 0.023828 | 0.017138 | 0.015874 | 0.016105 | 0.018258 | 0.015791 | 0.016175 | 0.015097 | 0.013874 | 0.015231 | 0.013114
154 | 0.13416 | 0.089745 | 0.061666 | 0.062966 | 0.058531 | 0.089662 | 0.19407 | 0.23989 | 0.23002 | 0.19239 | 0.20403 | 0.19251 | 0.26371 | 0.25705 | 0.18488 | 0.17125 | 0.17374 | 0.19697 | 0.17035 | 0.1745 | 0.16287 | 0.14966 | 0.16982 | 0.14623
155 | 0.058358 | 0.039037 | 0.026823 | 0.027389 | 0.02546 | 0.039001 | 0.084415 | 0.10435 | 0.10181 | 0.085161 | 0.090312 | 0.085212 | 0.11673 | 0.11378 | 0.081834 | 0.075804 | 0.076904 | 0.087187 | 0.075404 | 0.077242 | 0.072092 | 0.066246 | 0.073866 | 0.063605
156 | 0.027975 | 0.018714 | 0.012859 | 0.01313 | 0.012205 | 0.018697 | 0.040467 | 0.050021 | 0.056772 | 0.047486 | 0.050357 | 0.047513 | 0.065086 | 0.063442 | 0.04563 | 0.042268 | 0.042881 | 0.048616 | 0.042044 | 0.043069 | 0.040197 | 0.036939 | 0.03541 | 0.030491
157 | 0.13296 | 0.08894 | 0.061113 | 0.0624 | 0.058006 | 0.088858 | 0.19233 | 0.23774 | 0.26014 | 0.21758 | 0.23075 | 0.21771 | 0.29823 | 0.2907 | 0.20909 | 0.19368 | 0.19649 | 0.22276 | 0.19266 | 0.19735 | 0.18419 | 0.16926 | 0.1683 | 0.14492
158 | 0.11431 | 0.076465 | 0.05254 | 0.053648 | 0.04987 | 0.076394 | 0.16535 | 0.20439 | 0.21589 | 0.18058 | 0.1915 | 0.18068 | 0.24751 | 0.24126 | 0.17352 | 0.16073 | 0.16307 | 0.18487 | 0.15989 | 0.16379 | 0.15287 | 0.14047 | 0.14469 | 0.12459
159 | 0.13657 | 0.091356 | 0.062773 | 0.064095 | 0.059581 | 0.091271 | 0.19755 | 0.24419 | 0.25081 | 0.20978 | 0.22247 | 0.20991 | 0.28754 | 0.28028 | 0.20159 | 0.18673 | 0.18944 | 0.21477 | 0.18575 | 0.19027 | 0.17759 | 0.16319 | 0.17286 | 0.14885
160 | 0.1107 | 0.07405 | 0.050881 | 0.051954 | 0.048295 | 0.073982 | 0.16013 | 0.19794 | 0.23375 | 0.19551 | 0.20734 | 0.19563 | 0.26798 | 0.26122 | 0.18788 | 0.17403 | 0.17656 | 0.20017 | 0.17311 | 0.17733 | 0.16551 | 0.15209 | 0.14012 | 0.12065
161 | 0.020155 | 0.013482 | 0.0092639 | 0.0094591 | 0.0087932 | 0.013469 | 0.029153 | 0.036037 | 0.041048 | 0.034331 | 0.036409 | 0.034352 | 0.047059 | 0.045868 | 0.03299 | 0.03056 | 0.031003 | 0.035148 | 0.030398 | 0.031138 | 0.029064 | 0.026706 | 0.025511 | 0.021967
162 | 0.089944 | 0.060166 | 0.041341 | 0.042212 | 0.03924 | 0.06011 | 0.1301 | 0.16082 | 0.16365 | 0.13688 | 0.14516 | 0.13696 | 0.18762 | 0.18288 | 0.13154 | 0.12184 | 0.12361 | 0.14014 | 0.1212 | 0.12415 | 0.11588 | 0.10648 | 0.11385 | 0.098031
163 | 0.019553 | 0.013079 | 0.0089871 | 0.0091765 | 0.0085304 | 0.013068 | 0.028284 | 0.034963 | 0.055174 | 0.046148 | 0.048938 | 0.046174 | 0.063252 | 0.061657 | 0.044346 | 0.041076 | 0.041674 | 0.047246 | 0.04086 | 0.041857 | 0.039065 | 0.035898 | 0.02475 | 0.021312
164 | 0.10859 | 0.072642 | 0.049914 | 0.050965 | 0.047376 | 0.072574 | 0.15708 | 0.19417 | 0.14739 | 0.12328 | 0.13074 | 0.12336 | 0.16898 | 0.16471 | 0.11847 | 0.10974 | 0.11133 | 0.12622 | 0.10916 | 0.11182 | 0.10436 | 0.0959 | 0.13745 | 0.11836
165 | 0.042716 | 0.028574 | 0.019633 | 0.020048 | 0.018635 | 0.028548 | 0.061789 | 0.076379 | 0.080492 | 0.067325 | 0.071399 | 0.067367 | 0.09228 | 0.089952 | 0.064697 | 0.059928 | 0.060799 | 0.068929 | 0.059613 | 0.061064 | 0.056995 | 0.052373 | 0.054067 | 0.046556
166 | 0.1122 | 0.075056 | 0.051573 | 0.05266 | 0.048951 | 0.074987 | 0.1623 | 0.20062 | 0.21323 | 0.17835 | 0.18914 | 0.17845 | 0.24445 | 0.23828 | 0.17138 | 0.15875 | 0.16106 | 0.18259 | 0.15791 | 0.16176 | 0.15098 | 0.13874 | 0.14202 | 0.12229
167 | 0.037602 | 0.025153 | 0.017283 | 0.017647 | 0.016405 | 0.02513 | 0.054391 | 0.067235 | 0.057839 | 0.048377 | 0.051303 | 0.048405 | 0.066307 | 0.064634 | 0.046486 | 0.043061 | 0.043687 | 0.049529 | 0.042835 | 0.043879 | 0.040952 | 0.037632 | 0.047594 | 0.040984
168 | 0.15372 | 0.10282 | 0.070653 | 0.072142 | 0.067061 | 0.10273 | 0.22235 | 0.27485 | 0.31051 | 0.25972 | 0.27543 | 0.25987 | 0.35599 | 0.347 | 0.24957 | 0.23118 | 0.23454 | 0.2659 | 0.22996 | 0.23557 | 0.21986 | 0.20203 | 0.19457 | 0.16754
169 | 0.030081 | 0.020122 | 0.013826 | 0.014118 | 0.013124 | 0.020104 | 0.043512 | 0.053786 | 0.090623 | 0.075797 | 0.080382 | 0.075843 | 0.10389 | 0.10127 | 0.072837 | 0.06747 | 0.068449 | 0.077601 | 0.067113 | 0.06875 | 0.064165 | 0.058963 | 0.038075 | 0.032786
170 | 0.031585 | 0.021128 | 0.014518 | 0.014823 | 0.01378 | 0.021109 | 0.045689 | 0.056477 | 0.064235 | 0.053726 | 0.056976 | 0.053758 | 0.073643 | 0.071783 | 0.051628 | 0.047823 | 0.048518 | 0.055006 | 0.047571 | 0.048732 | 0.045482 | 0.041795 | 0.039979 | 0.034426
171 | 0.070993 | 0.047489 | 0.03263 | 0.033318 | 0.030972 | 0.047445 | 0.10269 | 0.12694 | 0.1402 | 0.11726 | 0.12436 | 0.11733 | 0.16073 | 0.15667 | 0.11268 | 0.10438 | 0.1059 | 0.12005 | 0.10383 | 0.10636 | 0.099269 | 0.091218 | 0.089858 | 0.077376
172 | 0.034593 | 0.023141 | 0.0159 | 0.016235 | 0.015092 | 0.023119 | 0.050038 | 0.061856 | 0.064235 | 0.053726 | 0.056976 | 0.053758 | 0.073643 | 0.071783 | 0.051628 | 0.047823 | 0.048518 | 0.055006 | 0.047571 | 0.048732 | 0.045482 | 0.041795 | 0.043786 | 0.037704
245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Upward flexibility
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.048574 | 0.046807 | 0.038054 | 0.038542 | 0.038006 | 0.041423 | 0.052549 | 0.046873 | 0.033938 | 0.056201 | 0.063088 | 0.069076 | 0.034538 | 0.033767 | 0.065828 | 0.06602 | 0.054297 | 0.019825 | 0.0093054 | 0.0097867 | 0.016334 | 0.045655 | 0.068558 | 0.063013
109 | 0.29376 | 0.28307 | 0.23014 | 0.23309 | 0.22985 | 0.25051 | 0.3178 | 0.28347 | 0.1874 | 0.31033 | 0.34836 | 0.38143 | 0.19072 | 0.18645 | 0.36349 | 0.36455 | 0.29982 | 0.10947 | 0.051383 | 0.05404 | 0.090195 | 0.2521 | 0.41461 | 0.38108
110 | 0.21367 | 0.2059 | 0.16739 | 0.16954 | 0.16718 | 0.18221 | 0.23116 | 0.20618 | 0.14808 | 0.24523 | 0.27528 | 0.30141 | 0.1507 | 0.14734 | 0.28723 | 0.28807 | 0.23692 | 0.086504 | 0.040603 | 0.042703 | 0.071272 | 0.19921 | 0.30157 | 0.27718
111 | 0.15295 | 0.14739 | 0.11982 | 0.12136 | 0.11967 | 0.13043 | 0.16547 | 0.14759 | 0.10858 | 0.17981 | 0.20185 | 0.22101 | 0.1105 | 0.10804 | 0.21061 | 0.21123 | 0.17372 | 0.063429 | 0.029772 | 0.031312 | 0.05226 | 0.14607 | 0.21588 | 0.19842
112 | 0.40884 | 0.39396 | 0.32029 | 0.32439 | 0.31989 | 0.34864 | 0.44229 | 0.39451 | 0.22402 | 0.37098 | 0.41645 | 0.45598 | 0.22799 | 0.2229 | 0.43453 | 0.4358 | 0.35842 | 0.13087 | 0.061425 | 0.064602 | 0.10782 | 0.30137 | 0.57703 | 0.53036
113 | 0.18187 | 0.17525 | 0.14248 | 0.1443 | 0.1423 | 0.15509 | 0.19675 | 0.17549 | 0.085307 | 0.14127 | 0.15858 | 0.17364 | 0.086818 | 0.084878 | 0.16547 | 0.16595 | 0.13648 | 0.049833 | 0.023391 | 0.0246 | 0.041058 | 0.11476 | 0.25668 | 0.23593
114 | 0.2261 | 0.21788 | 0.17713 | 0.1794 | 0.17691 | 0.19281 | 0.2446 | 0.21818 | 0.14576 | 0.24139 | 0.27097 | 0.29669 | 0.14835 | 0.14503 | 0.28273 | 0.28356 | 0.23321 | 0.08515 | 0.039967 | 0.042034 | 0.070156 | 0.19609 | 0.31912 | 0.29331
115 | 0.03325 | 0.032041 | 0.026049 | 0.026382 | 0.026016 | 0.028355 | 0.035971 | 0.032086 | 0.021049 | 0.034857 | 0.039128 | 0.042843 | 0.021422 | 0.020943 | 0.040827 | 0.040948 | 0.033677 | 0.012296 | 0.0057713 | 0.0060697 | 0.010131 | 0.028316 | 0.046928 | 0.043133
116 | 0.37877 | 0.36499 | 0.29673 | 0.30053 | 0.29636 | 0.323 | 0.40976 | 0.36549 | 0.24322 | 0.40277 | 0.45213 | 0.49505 | 0.24753 | 0.24199 | 0.47176 | 0.47314 | 0.38913 | 0.14208 | 0.066688 | 0.070137 | 0.11706 | 0.32719 | 0.53459 | 0.49135
117 | 0.077489 | 0.07467 | 0.060705 | 0.061483 | 0.060629 | 0.06608 | 0.083828 | 0.074773 | 0.050165 | 0.083073 | 0.093253 | 0.1021 | 0.051053 | 0.049912 | 0.097301 | 0.097587 | 0.080259 | 0.029304 | 0.013755 | 0.014466 | 0.024144 | 0.067485 | 0.10936 | 0.10052
118 | 0.1304 | 0.12566 | 0.10216 | 0.10347 | 0.10203 | 0.1112 | 0.14107 | 0.12583 | 0.081876 | 0.13559 | 0.1522 | 0.16665 | 0.083327 | 0.081464 | 0.15881 | 0.15928 | 0.131 | 0.047829 | 0.02245 | 0.023611 | 0.039407 | 0.11015 | 0.18404 | 0.16916
119 | 0.24576 | 0.23682 | 0.19253 | 0.195 | 0.19229 | 0.20958 | 0.26587 | 0.23715 | 0.1657 | 0.2744 | 0.30803 | 0.33727 | 0.16863 | 0.16487 | 0.3214 | 0.32234 | 0.26511 | 0.096796 | 0.045434 | 0.047783 | 0.079751 | 0.22291 | 0.34687 | 0.31882
120 | 0.33655 | 0.32431 | 0.26366 | 0.26704 | 0.26333 | 0.287 | 0.36409 | 0.32476 | 0.21679 | 0.35901 | 0.403 | 0.44126 | 0.22063 | 0.2157 | 0.4205 | 0.42173 | 0.34685 | 0.12664 | 0.059442 | 0.062517 | 0.10434 | 0.29164 | 0.47501 | 0.43659
121 | 0.23073 | 0.22234 | 0.18076 | 0.18307 | 0.18053 | 0.19676 | 0.24961 | 0.22264 | 0.14753 | 0.2443 | 0.27424 | 0.30028 | 0.15014 | 0.14678 | 0.28615 | 0.28699 | 0.23603 | 0.08618 | 0.04045 | 0.042542 | 0.071004 | 0.19846 | 0.32565 | 0.29931
122 | 0.30041 | 0.28948 | 0.23535 | 0.23836 | 0.23505 | 0.25618 | 0.32499 | 0.28988 | 0.18777 | 0.31095 | 0.34905 | 0.38219 | 0.19109 | 0.18682 | 0.36421 | 0.36527 | 0.30042 | 0.10969 | 0.051484 | 0.054147 | 0.090373 | 0.2526 | 0.424 | 0.38971
123 | 0.18042 | 0.17386 | 0.14134 | 0.14316 | 0.14117 | 0.15386 | 0.19518 | 0.1741 | 0.1211 | 0.20054 | 0.22512 | 0.24649 | 0.12324 | 0.12049 | 0.23489 | 0.23558 | 0.19375 | 0.070742 | 0.033204 | 0.034922 | 0.058285 | 0.16291 | 0.25464 | 0.23405
124 | 0.15469 | 0.14906 | 0.12118 | 0.12274 | 0.12103 | 0.13191 | 0.16735 | 0.14927 | 0.10153 | 0.16814 | 0.18875 | 0.20666 | 0.10333 | 0.10102 | 0.19694 | 0.19752 | 0.16245 | 0.059313 | 0.02784 | 0.02928 | 0.048869 | 0.13659 | 0.21832 | 0.20067
125 | 0.16278 | 0.15686 | 0.12753 | 0.12916 | 0.12737 | 0.13882 | 0.1761 | 0.15708 | 0.11479 | 0.1901 | 0.2134 | 0.23365 | 0.11683 | 0.11422 | 0.22266 | 0.22331 | 0.18366 | 0.067059 | 0.031476 | 0.033103 | 0.05525 | 0.15443 | 0.22975 | 0.21117
126 | 0.1677 | 0.1616 | 0.13138 | 0.13306 | 0.13121 | 0.14301 | 0.18142 | 0.16182 | 0.0854 | 0.14142 | 0.15875 | 0.17382 | 0.086912 | 0.08497 | 0.16565 | 0.16613 | 0.13663 | 0.049888 | 0.023416 | 0.024627 | 0.041103 | 0.11489 | 0.23669 | 0.21755
127 | 0.12028 | 0.1159 | 0.094229 | 0.095436 | 0.09411 | 0.10257 | 0.13012 | 0.11606 | 0.08438 | 0.13973 | 0.15686 | 0.17175 | 0.085874 | 0.083956 | 0.16367 | 0.16415 | 0.135 | 0.049292 | 0.023136 | 0.024333 | 0.040612 | 0.11351 | 0.16976 | 0.15603
128 | 0.29 | 0.27945 | 0.22719 | 0.2301 | 0.22691 | 0.2473 | 0.31373 | 0.27984 | 0.24303 | 0.40246 | 0.45179 | 0.49467 | 0.24734 | 0.24181 | 0.4714 | 0.47278 | 0.38883 | 0.14197 | 0.066638 | 0.070084 | 0.11697 | 0.32694 | 0.40931 | 0.3762
129 | 0.25878 | 0.24936 | 0.20273 | 0.20533 | 0.20247 | 0.22068 | 0.27995 | 0.24971 | 0.19009 | 0.31479 | 0.35336 | 0.38691 | 0.19345 | 0.18913 | 0.3687 | 0.36978 | 0.30412 | 0.11104 | 0.05212 | 0.054816 | 0.091489 | 0.25572 | 0.36523 | 0.3357
130 | 0.28653 | 0.27611 | 0.22447 | 0.22735 | 0.22419 | 0.24435 | 0.30998 | 0.27649 | 0.21076 | 0.34903 | 0.3918 | 0.42899 | 0.2145 | 0.2097 | 0.40881 | 0.41001 | 0.33721 | 0.12312 | 0.05779 | 0.060778 | 0.10144 | 0.28353 | 0.40441 | 0.3717
131 | 0.22871 | 0.22038 | 0.17917 | 0.18147 | 0.17895 | 0.19503 | 0.24742 | 0.22069 | 0.12991 | 0.21513 | 0.24149 | 0.26442 | 0.13221 | 0.12925 | 0.25198 | 0.25271 | 0.20784 | 0.075888 | 0.03562 | 0.037462 | 0.062525 | 0.17476 | 0.32279 | 0.29669
132 | 0.037299 | 0.035941 | 0.02922 | 0.029595 | 0.029183 | 0.031807 | 0.040351 | 0.03599 | 0.061662 | 0.10211 | 0.11463 | 0.12551 | 0.062754 | 0.061352 | 0.1196 | 0.11995 | 0.098655 | 0.036021 | 0.016907 | 0.017782 | 0.029678 | 0.082952 | 0.052643 | 0.048386
133 | 0.22263 | 0.21453 | 0.17441 | 0.17665 | 0.17419 | 0.18986 | 0.24085 | 0.21483 | 0.14938 | 0.24738 | 0.27769 | 0.30405 | 0.15203 | 0.14863 | 0.28975 | 0.29059 | 0.239 | 0.087263 | 0.040959 | 0.043077 | 0.071897 | 0.20096 | 0.31422 | 0.28881
134 | 0.19372 | 0.18667 | 0.15176 | 0.15371 | 0.15157 | 0.1652 | 0.20957 | 0.18693 | 0.13325 | 0.22066 | 0.2477 | 0.27121 | 0.13561 | 0.13258 | 0.25845 | 0.25921 | 0.21318 | 0.077838 | 0.036535 | 0.038425 | 0.064131 | 0.17925 | 0.27342 | 0.2513
135 | 0.20962 | 0.202 | 0.16422 | 0.16633 | 0.16401 | 0.17876 | 0.22678 | 0.20228 | 0.14855 | 0.24599 | 0.27614 | 0.30235 | 0.15118 | 0.1478 | 0.28813 | 0.28897 | 0.23766 | 0.086775 | 0.04073 | 0.042836 | 0.071495 | 0.19983 | 0.29586 | 0.27193
136 | 0.23767 | 0.22902 | 0.18619 | 0.18858 | 0.18596 | 0.20268 | 0.25712 | 0.22934 | 0.17006 | 0.28162 | 0.31613 | 0.34614 | 0.17307 | 0.1692 | 0.32985 | 0.33082 | 0.27208 | 0.099342 | 0.046628 | 0.04904 | 0.081849 | 0.22877 | 0.33544 | 0.30831
137 | 0.15035 | 0.14488 | 0.11779 | 0.1193 | 0.11764 | 0.12821 | 0.16265 | 0.14508 | 0.11841 | 0.19609 | 0.22012 | 0.24101 | 0.12051 | 0.11781 | 0.22967 | 0.23035 | 0.18945 | 0.069171 | 0.032467 | 0.034146 | 0.056991 | 0.15929 | 0.2122 | 0.19504
138 | 0.13069 | 0.12594 | 0.10238 | 0.10369 | 0.10225 | 0.11145 | 0.14138 | 0.12611 | 0.1109 | 0.18365 | 0.20616 | 0.22573 | 0.11286 | 0.11034 | 0.21511 | 0.21574 | 0.17743 | 0.064783 | 0.030408 | 0.03198 | 0.053376 | 0.14919 | 0.18445 | 0.16954
139 | 0.22668 | 0.21843 | 0.17759 | 0.17986 | 0.17736 | 0.19331 | 0.24523 | 0.21874 | 0.18693 | 0.30956 | 0.3475 | 0.38049 | 0.19024 | 0.18599 | 0.36259 | 0.36365 | 0.29908 | 0.1092 | 0.051256 | 0.053907 | 0.089971 | 0.25148 | 0.31993 | 0.29406
140 | 0.10004 | 0.096401 | 0.078373 | 0.079377 | 0.078274 | 0.085311 | 0.10823 | 0.096534 | 0.064815 | 0.10733 | 0.12049 | 0.13193 | 0.065963 | 0.064489 | 0.12572 | 0.12609 | 0.1037 | 0.037863 | 0.017772 | 0.018691 | 0.031195 | 0.087193 | 0.1412 | 0.12978
141 | 0.11276 | 0.10866 | 0.08834 | 0.089471 | 0.088229 | 0.096161 | 0.12199 | 0.10881 | 0.075942 | 0.12576 | 0.14117 | 0.15457 | 0.077287 | 0.07556 | 0.1473 | 0.14773 | 0.1215 | 0.044363 | 0.020823 | 0.021899 | 0.036551 | 0.10216 | 0.15915 | 0.14628
142 | 0.13532 | 0.13039 | 0.10601 | 0.10737 | 0.10587 | 0.11539 | 0.14639 | 0.13057 | 0.10311 | 0.17075 | 0.19168 | 0.20987 | 0.10494 | 0.10259 | 0.2 | 0.20058 | 0.16497 | 0.060234 | 0.028272 | 0.029734 | 0.049627 | 0.13871 | 0.19098 | 0.17554
143 | 0.094547 | 0.091108 | 0.074069 | 0.075018 | 0.073976 | 0.080628 | 0.10228 | 0.091233 | 0.070935 | 0.11747 | 0.13186 | 0.14438 | 0.072191 | 0.070578 | 0.13759 | 0.13799 | 0.11349 | 0.041437 | 0.01945 | 0.020456 | 0.034141 | 0.095426 | 0.13344 | 0.12265
144 | 0.074019 | 0.071325 | 0.057987 | 0.058731 | 0.057915 | 0.063121 | 0.080075 | 0.071424 | 0.056655 | 0.093821 | 0.10532 | 0.11532 | 0.057658 | 0.05637 | 0.10989 | 0.11021 | 0.090644 | 0.033096 | 0.015534 | 0.016338 | 0.027268 | 0.076216 | 0.10447 | 0.09602
145 | 0.28711 | 0.27667 | 0.22493 | 0.22781 | 0.22464 | 0.24484 | 0.3106 | 0.27705 | 0.1504 | 0.24906 | 0.27959 | 0.30613 | 0.15306 | 0.14964 | 0.29172 | 0.29258 | 0.24063 | 0.087859 | 0.041239 | 0.043371 | 0.072388 | 0.20233 | 0.40523 | 0.37245
146 | 0.011854 | 0.011423 | 0.009287 | 0.0094063 | 0.0092757 | 0.010109 | 0.012825 | 0.01144 | 0.008809 | 0.014588 | 0.016374 | 0.017929 | 0.0089646 | 0.0087643 | 0.017086 | 0.017137 | 0.014093 | 0.0051459 | 0.0024154 | 0.0025403 | 0.0042396 | 0.01185 | 0.016731 | 0.015378
147 | 0.068815 | 0.066311 | 0.05391 | 0.054601 | 0.053842 | 0.058682 | 0.074446 | 0.066403 | 0.051556 | 0.085376 | 0.095839 | 0.10494 | 0.052468 | 0.051296 | 0.099999 | 0.10029 | 0.082484 | 0.030117 | 0.014136 | 0.014867 | 0.024813 | 0.069356 | 0.097124 | 0.089269
149 | 0.23709 | 0.22846 | 0.18574 | 0.18812 | 0.18551 | 0.20218 | 0.25649 | 0.22878 | 0.15884 | 0.26304 | 0.29527 | 0.3233 | 0.16165 | 0.15804 | 0.30809 | 0.30899 | 0.25413 | 0.092788 | 0.043552 | 0.045805 | 0.076449 | 0.21368 | 0.33463 | 0.30757
150 | 0.055514 | 0.053494 | 0.04349 | 0.044048 | 0.043435 | 0.04734 | 0.060056 | 0.053569 | 0.030322 | 0.050211 | 0.056365 | 0.061717 | 0.030858 | 0.030169 | 0.058812 | 0.058985 | 0.048512 | 0.017713 | 0.0083139 | 0.0087439 | 0.014594 | 0.04079 | 0.078351 | 0.072015
151 | 0.21627 | 0.2084 | 0.16943 | 0.1716 | 0.16922 | 0.18443 | 0.23397 | 0.20869 | 0.1683 | 0.2787 | 0.31285 | 0.34255 | 0.17128 | 0.16745 | 0.32644 | 0.32739 | 0.26926 | 0.098313 | 0.046146 | 0.048532 | 0.081001 | 0.2264 | 0.30524 | 0.28056
152 | 0.078356 | 0.075505 | 0.061384 | 0.062172 | 0.061308 | 0.066819 | 0.084766 | 0.07561 | 0.056192 | 0.093053 | 0.10446 | 0.11437 | 0.057187 | 0.055909 | 0.10899 | 0.10931 | 0.089902 | 0.032825 | 0.015407 | 0.016204 | 0.027045 | 0.075593 | 0.11059 | 0.10165
153 | 0.011565 | 0.011144 | 0.0090611 | 0.0091759 | 0.0090491 | 0.0098626 | 0.012512 | 0.01116 | 0.007418 | 0.012284 | 0.013789 | 0.015099 | 0.0075492 | 0.0073807 | 0.014389 | 0.01443 | 0.011868 | 0.0043331 | 0.0020339 | 0.002139 | 0.0035701 | 0.0099798 | 0.016324 | 0.015002
154 | 0.12895 | 0.12426 | 0.10102 | 0.10232 | 0.1009 | 0.10997 | 0.13951 | 0.12444 | 0.080022 | 0.13252 | 0.14876 | 0.16288 | 0.081439 | 0.079619 | 0.15521 | 0.15567 | 0.12803 | 0.046746 | 0.021941 | 0.023076 | 0.038514 | 0.10765 | 0.182 | 0.16728
155 | 0.056093 | 0.054051 | 0.043943 | 0.044507 | 0.043888 | 0.047834 | 0.060683 | 0.054126 | 0.035421 | 0.058658 | 0.065846 | 0.072097 | 0.036048 | 0.035243 | 0.068704 | 0.068907 | 0.056671 | 0.020692 | 0.0097122 | 0.010214 | 0.017048 | 0.047651 | 0.079167 | 0.072765
156 | 0.026889 | 0.025911 | 0.021066 | 0.021336 | 0.021039 | 0.022931 | 0.02909 | 0.025947 | 0.01975 | 0.032708 | 0.036715 | 0.0402 | 0.0201 | 0.019651 | 0.038309 | 0.038422 | 0.031599 | 0.011538 | 0.0054153 | 0.0056954 | 0.0095057 | 0.02657 | 0.037951 | 0.034882
157 | 0.1278 | 0.12315 | 0.10012 | 0.1014 | 0.099992 | 0.10898 | 0.13826 | 0.12332 | 0.0905 | 0.14987 | 0.16824 | 0.1842 | 0.092103 | 0.090044 | 0.17554 | 0.17605 | 0.14479 | 0.052867 | 0.024814 | 0.026098 | 0.043558 | 0.12175 | 0.18037 | 0.16578
158 | 0.10987 | 0.10587 | 0.086074 | 0.087178 | 0.085967 | 0.093695 | 0.11886 | 0.10602 | 0.075108 | 0.12438 | 0.13962 | 0.15287 | 0.076437 | 0.07473 | 0.14568 | 0.14611 | 0.12017 | 0.043875 | 0.020594 | 0.021659 | 0.036149 | 0.10104 | 0.15507 | 0.14253
159 | 0.13127 | 0.12649 | 0.10284 | 0.10415 | 0.10271 | 0.11194 | 0.14201 | 0.12667 | 0.087255 | 0.14449 | 0.1622 | 0.1776 | 0.0888 | 0.086815 | 0.16924 | 0.16974 | 0.1396 | 0.050971 | 0.023925 | 0.025162 | 0.041996 | 0.11738 | 0.18527 | 0.17029
160 | 0.1064 | 0.10253 | 0.083356 | 0.084425 | 0.083252 | 0.090736 | 0.11511 | 0.10267 | 0.081321 | 0.13467 | 0.15117 | 0.16552 | 0.08276 | 0.080911 | 0.15773 | 0.15819 | 0.13011 | 0.047504 | 0.022297 | 0.02345 | 0.03914 | 0.1094 | 0.15017 | 0.13803
161 | 0.019372 | 0.018667 | 0.015177 | 0.015371 | 0.015158 | 0.016519 | 0.020957 | 0.018693 | 0.01428 | 0.023647 | 0.026545 | 0.029065 | 0.014533 | 0.014208 | 0.027697 | 0.027779 | 0.022846 | 0.0083416 | 0.0039154 | 0.0041177 | 0.0068729 | 0.01921 | 0.027342 | 0.02513
162 | 0.086451 | 0.083307 | 0.067727 | 0.068594 | 0.067642 | 0.073724 | 0.093524 | 0.083422 | 0.056933 | 0.094282 | 0.10584 | 0.11588 | 0.057942 | 0.056646 | 0.11043 | 0.11075 | 0.091089 | 0.033258 | 0.015611 | 0.016418 | 0.027402 | 0.07659 | 0.12202 | 0.11215
163 | 0.018794 | 0.01811 | 0.014723 | 0.014912 | 0.014705 | 0.016027 | 0.020332 | 0.018136 | 0.019195 | 0.031786 | 0.03568 | 0.039067 | 0.019534 | 0.019098 | 0.03723 | 0.037338 | 0.030709 | 0.011213 | 0.0052629 | 0.0055351 | 0.009238 | 0.025822 | 0.026526 | 0.024381
164 | 0.10438 | 0.10058 | 0.081771 | 0.082818 | 0.081667 | 0.089009 | 0.11292 | 0.10072 | 0.051277 | 0.084916 | 0.095322 | 0.10437 | 0.052185 | 0.051019 | 0.09946 | 0.099751 | 0.082039 | 0.029955 | 0.01406 | 0.014787 | 0.02468 | 0.068981 | 0.14732 | 0.1354
165 | 0.041057 | 0.039564 | 0.032164 | 0.032577 | 0.032124 | 0.035013 | 0.044418 | 0.039619 | 0.028003 | 0.046373 | 0.052056 | 0.056998 | 0.028499 | 0.027862 | 0.054317 | 0.054475 | 0.044803 | 0.016358 | 0.0076783 | 0.0080751 | 0.013478 | 0.037672 | 0.057947 | 0.053261
166 | 0.10785 | 0.10392 | 0.084489 | 0.085572 | 0.084383 | 0.09197 | 0.11667 | 0.10407 | 0.07418 | 0.12284 | 0.1379 | 0.15099 | 0.075494 | 0.073807 | 0.14388 | 0.14431 | 0.11868 | 0.043333 | 0.02034 | 0.021392 | 0.035703 | 0.099792 | 0.15221 | 0.1399
167 | 0.036142 | 0.034827 | 0.028315 | 0.028677 | 0.028279 | 0.030821 | 0.0391 | 0.034876 | 0.020122 | 0.033321 | 0.037405 | 0.040955 | 0.020477 | 0.02002 | 0.039028 | 0.039143 | 0.032193 | 0.011754 | 0.0055172 | 0.0058026 | 0.0096842 | 0.027069 | 0.051009 | 0.046885
168 | 0.14775 | 0.14237 | 0.11575 | 0.11723 | 0.1156 | 0.12599 | 0.15984 | 0.14257 | 0.10802 | 0.17889 | 0.20081 | 0.21988 | 0.10994 | 0.10748 | 0.20953 | 0.21014 | 0.17283 | 0.063105 | 0.029619 | 0.031151 | 0.051992 | 0.14532 | 0.20853 | 0.19167
169 | 0.028913 | 0.027861 | 0.022651 | 0.022942 | 0.022623 | 0.024656 | 0.031279 | 0.0279 | 0.031527 | 0.052208 | 0.058606 | 0.06417 | 0.032085 | 0.031368 | 0.061151 | 0.061331 | 0.05044 | 0.018417 | 0.0086443 | 0.0090915 | 0.015174 | 0.042412 | 0.040807 | 0.037507
170 | 0.030359 | 0.029254 | 0.023784 | 0.024088 | 0.023754 | 0.02589 | 0.032844 | 0.029296 | 0.022347 | 0.037006 | 0.041541 | 0.045484 | 0.022743 | 0.022234 | 0.043344 | 0.043471 | 0.035753 | 0.013054 | 0.0061272 | 0.0064443 | 0.010756 | 0.030063 | 0.042848 | 0.039383
171 | 0.068236 | 0.065754 | 0.053456 | 0.054142 | 0.05339 | 0.05819 | 0.073819 | 0.065844 | 0.048774 | 0.08077 | 0.090668 | 0.099274 | 0.049638 | 0.048528 | 0.094603 | 0.094882 | 0.078035 | 0.028492 | 0.013373 | 0.014065 | 0.023475 | 0.065613 | 0.096306 | 0.088518
172 | 0.03325 | 0.032041 | 0.026049 | 0.026382 | 0.026016 | 0.028355 | 0.035971 | 0.032086 | 0.022347 | 0.037006 | 0.041541 | 0.045484 | 0.022743 | 0.022234 | 0.043344 | 0.043471 | 0.035753 | 0.013054 | 0.0061272 | 0.0064443 | 0.010756 | 0.030063 | 0.046928 | 0.043133
245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0