## OF Values
Agent | 2020, Summer, [m.u.] | Total, [NPV Mm.u.]
ESSO | -2.3463e-05 | -8.5641e-08
TSO | 0 | 0

## Shared ESS Specifications
Year | Node ID | Sinst, [MVA] | Einst, [MVAh]
2020 | 2 | 0 | 0

## Primal Evolution
Iteration | OF value
0 | -0.085086
1 | -0.085086
2 | -0.085641

## Interface PF
Node ID | Operator | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
2 | TSO | 2020 | Summer | P, [MW] | 0 | 0 | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
2 | TSO | 2020 | Summer | Q, [MVAr] | 0 | 0 | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8578 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6312 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
2 | TSO | 2020 | Summer | P, [MW] | Expected | - | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
2 | TSO | 2020 | Summer | Q, [MVAr] | Expected | - | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8578 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6312 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
2 | DSO | 2020 | Summer | P, [MW] | 0 | 0 | 7.7545 | 7.3126 | 6.6642 | 6.8059 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.5241 | 9.4179 | 9.3925 | 9.7543 | 10.4722 | 10.5048 | 9.5242 | 8.3132
2 | DSO | 2020 | Summer | Q, [MVAr] | 0 | 0 | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8577 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6311 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
2 | DSO | 2020 | Summer | P, [MW] | Expected | - | 7.7545 | 7.3126 | 6.6642 | 6.8059 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.5241 | 9.4179 | 9.3925 | 9.7543 | 10.4722 | 10.5048 | 9.5242 | 8.3132
2 | DSO | 2020 | Summer | Q, [MVAr] | Expected | - | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8577 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6311 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621

## Shared ESS
Node ID | Operator | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
2 | ESSO | 2020 | Summer | P, [MW] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | SoC, [MVAh] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | SoC, [%] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | Pup, [MW] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | Pdown, [MW] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | P, [MW] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | SoC, [MVAh] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | SoC, [%] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | Pup, [MW] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | ESSO | 2020 | Summer | Pdown, [MW] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | P, [MW] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [MVAh] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [%] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | P, [MW] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [MVAh] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [%] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | DSO | 2020 | Summer | P, [MW] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | DSO | 2020 | Summer | SoC, [MVAh] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | DSO | 2020 | Summer | SoC, [%] | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | DSO | 2020 | Summer | P, [MW] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [MVAh] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | TSO | 2020 | Summer | SoC, [%] | Expected | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Voltage
Operator | Connection Node ID | Network Node ID | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
TSO | - | 1 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
TSO | - | 1 | 2020 | Summer | Vang, [º] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 2 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0467 | 1.054 | 1.0537 | 1.0509 | 1.0514 | 1.0549 | 1.0475 | 1.0357 | 1.025 | 1.0338 | 1.0288 | 1.0221 | 1.023 | 1.026 | 1.0385 | 1.0319 | 1.0349 | 1.0281 | 1.0289 | 1.0385 | 1.0373 | 1.0409 | 1.0435 | 1.0402
TSO | - | 2 | 2020 | Summer | Vang, [º] | 0 | 0 | -0.62891 | -0.57885 | -0.81849 | -0.84266 | -0.76901 | -0.91939 | -0.60916 | 1.061 | 0.99644 | 0.89043 | 1.0739 | 0.60374 | 0.5526 | 0.79543 | -0.43404 | -0.30503 | 0.74686 | 0.73684 | 0.29224 | 0.64834 | 0.63808 | -0.5178 | -0.31286 | -0.38192
TSO | - | 3 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0308 | 1.0369 | 1.0391 | 1.0374 | 1.0386 | 1.0399 | 1.0246 | 1.0244 | 1.0188 | 1.0274 | 1.0291 | 1.0162 | 1.0189 | 1.0246 | 1.0317 | 1.0197 | 1.0278 | 1.0259 | 1.0314 | 1.0318 | 1.0262 | 1.0316 | 1.0309 | 1.0287
TSO | - | 3 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.636 | -2.3603 | -2.9466 | -3.0526 | -2.9236 | -3.1054 | -2.4164 | 1.6347 | 0.1617 | -0.15162 | 0.30428 | -0.94702 | -1.076 | -0.52833 | -2.3257 | -2.2194 | -0.65579 | -0.73842 | -1.522 | -0.88343 | -0.85937 | -2.4909 | -1.6902 | -1.9653
TSO | - | 4 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0271 | 1.0337 | 1.0363 | 1.0342 | 1.0351 | 1.036 | 1.0192 | 1.0193 | 1.0126 | 1.0211 | 1.0237 | 1.0108 | 1.0132 | 1.019 | 1.0252 | 1.0138 | 1.0221 | 1.0205 | 1.027 | 1.0274 | 1.0219 | 1.0271 | 1.0269 | 1.0249
TSO | - | 4 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.9822 | -2.6782 | -3.2709 | -3.3801 | -3.2583 | -3.4646 | -2.8352 | 1.3975 | -0.11682 | -0.38835 | 0.10703 | -1.1602 | -1.2704 | -0.72219 | -2.5555 | -2.4678 | -0.92549 | -1.0033 | -1.7234 | -1.0946 | -1.0768 | -2.7621 | -1.9079 | -2.2118
TSO | - | 5 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0204 | 1.0273 | 1.0294 | 1.0271 | 1.0282 | 1.0291 | 1.0127 | 1.0174 | 1.0088 | 1.0172 | 1.0196 | 1.0088 | 1.011 | 1.0168 | 1.02 | 1.0086 | 1.0163 | 1.0149 | 1.0232 | 1.0248 | 1.0193 | 1.0232 | 1.022 | 1.0189
TSO | - | 5 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.8642 | -2.5224 | -3.1844 | -3.3208 | -3.1697 | -3.3736 | -2.7003 | 1.7478 | 0.1732 | -0.11137 | 0.38169 | -0.84167 | -0.95731 | -0.40757 | -2.3282 | -2.2414 | -0.73742 | -0.8079 | -1.4554 | -0.77027 | -0.75049 | -2.5026 | -1.6696 | -2.0239
TSO | - | 6 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0179 | 1.0241 | 1.0261 | 1.0234 | 1.0241 | 1.0245 | 1.0099 | 1.0196 | 1.0107 | 1.0193 | 1.0216 | 1.0129 | 1.0146 | 1.0204 | 1.022 | 1.0096 | 1.0168 | 1.0155 | 1.0244 | 1.0267 | 1.0212 | 1.0255 | 1.0242 | 1.0189
TSO | - | 6 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.6791 | -2.384 | -3.0656 | -3.2162 | -3.0912 | -3.268 | -2.4892 | 2.1848 | 0.65594 | 0.38086 | 0.87132 | -0.27267 | -0.40554 | 0.15933 | -1.8199 | -1.7663 | -0.29441 | -0.3721 | -0.99413 | -0.29104 | -0.23852 | -1.9581 | -1.1152 | -1.6195
TSO | - | 7 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99712 | 1.0043 | 1.0051 | 1.0034 | 1.0043 | 1.0061 | 0.99027 | 1.0059 | 0.99393 | 1.0005 | 1.0021 | 1.0004 | 1.0009 | 1.0037 | 1.0027 | 0.99129 | 0.99642 | 0.99529 | 1.0093 | 1.0136 | 1.0088 | 1.0099 | 1.0067 | 0.99908
TSO | - | 7 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.046 | -2.5391 | -3.5989 | -3.5988 | -3.4756 | -3.6063 | -2.7734 | 2.0851 | 0.036654 | -0.72109 | -0.077145 | -0.81479 | -0.99108 | -1.2979 | -2.5446 | -2.4262 | -1.4495 | -1.5245 | -1.2546 | -0.36675 | -0.31512 | -2.3838 | -1.5634 | -1.9097
TSO | - | 8 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98596 | 0.99338 | 0.99233 | 0.98928 | 0.98996 | 0.99028 | 0.97822 | 1.0073 | 0.99221 | 0.9995 | 1.001 | 1.0061 | 1.0052 | 1.006 | 1.0018 | 0.98798 | 0.99119 | 0.99054 | 1.0104 | 1.0163 | 1.0111 | 1.0126 | 1.0076 | 0.99333
TSO | - | 8 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.3284 | -1.7862 | -3.1249 | -3.1443 | -3.0649 | -3.147 | -1.9987 | 3.538 | 1.3019 | 0.27029 | 1.0377 | 0.65018 | 0.4213 | -0.36892 | -1.1978 | -1.1446 | -0.50787 | -0.60042 | 0.15338 | 1.2253 | 1.3525 | -0.82468 | 0.076771 | -0.5794
TSO | - | 9 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99184 | 1.0005 | 0.99748 | 1.0001 | 0.99711 | 1.0018 | 0.98947 | 0.99818 | 1.0015 | 1.0134 | 1.0041 | 1.0171 | 1.0155 | 1.0154 | 1.0126 | 1.0033 | 1.0085 | 1.0085 | 1.0013 | 1.0052 | 1.0022 | 1.0012 | 0.99888 | 0.99425
TSO | - | 9 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.7191 | -2.868 | -4.8716 | -4.0573 | -4.7282 | -4.8778 | -3.1373 | 1.0297 | -1.3914 | -2.3148 | -1.6965 | -2.0192 | -2.2381 | -2.9413 | -3.6674 | -3.5008 | -2.968 | -3.0354 | -1.5645 | -1.0514 | -0.88315 | -2.9058 | -2.2981 | -2.3272
TSO | - | 10 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98231 | 0.98643 | 0.98973 | 0.99127 | 0.99074 | 0.99551 | 0.98036 | 0.97307 | 1.0008 | 1.0218 | 1.0005 | 1.0249 | 1.0265 | 1.0261 | 1.0281 | 1.0161 | 1.023 | 1.0226 | 0.98299 | 0.98419 | 0.98381 | 0.98408 | 0.97968 | 0.98049
TSO | - | 10 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.878 | -4.8094 | -5.6484 | -5.2619 | -5.4912 | -5.5643 | -4.1681 | -1.5158 | -3.8222 | -4.625 | -4.1112 | -4.1061 | -4.1483 | -4.6961 | -5.1044 | -4.7138 | -4.7898 | -4.8224 | -2.4635 | -2.8709 | -2.6629 | -4.0245 | -4.1365 | -4.2214
TSO | - | 11 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99449 | 1.0005 | 1.0018 | 1.004 | 1.0024 | 1.0079 | 0.99264 | 0.99126 | 1.0026 | 1.0163 | 1.0044 | 1.0186 | 1.0178 | 1.017 | 1.0163 | 1.0078 | 1.0135 | 1.0134 | 0.99639 | 0.99843 | 0.99623 | 0.99611 | 0.99477 | 0.99409
TSO | - | 11 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.3442 | -3.8684 | -5.1081 | -4.5952 | -4.9687 | -4.9931 | -3.7245 | -0.3187 | -2.5319 | -3.1822 | -2.7382 | -2.9505 | -3.1034 | -3.7871 | -4.308 | -4.26 | -3.796 | -3.836 | -2.2076 | -2.1585 | -1.9979 | -3.6687 | -3.4175 | -3.3676
TSO | - | 12 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.963 | 0.96415 | 0.96903 | 0.96943 | 0.9696 | 0.97435 | 0.96385 | 0.95972 | 1.013 | 1.0407 | 1.009 | 1.0469 | 1.0498 | 1.0498 | 1.0421 | 1.0314 | 1.0413 | 1.0419 | 0.97031 | 0.96927 | 0.96909 | 0.96918 | 0.96405 | 0.96073
TSO | - | 12 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.2006 | -4.5981 | -4.8152 | -4.7775 | -4.7955 | -4.8751 | -3.3114 | -1.5781 | -3.8077 | -4.4249 | -4.0065 | -3.7768 | -3.6699 | -3.8189 | -3.9943 | -3.4866 | -4.1738 | -4.167 | -1.0597 | -2.1512 | -1.8976 | -2.6162 | -3.4342 | -3.8133
TSO | - | 13 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99552 | 0.99892 | 1.0026 | 1.0045 | 1.0041 | 1.01 | 0.99587 | 0.99023 | 1.0093 | 1.0246 | 1.0094 | 1.0266 | 1.0273 | 1.0257 | 1.0259 | 1.0164 | 1.0226 | 1.0225 | 0.99638 | 0.99674 | 0.99529 | 0.99576 | 0.99324 | 0.99407
TSO | - | 13 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.1627 | -4.0211 | -4.6673 | -4.4618 | -4.5743 | -4.4388 | -3.4604 | -0.71215 | -2.7624 | -3.2731 | -2.9735 | -3.0544 | -3.1644 | -3.8008 | -4.1057 | -4.1493 | -3.7916 | -3.8061 | -1.9926 | -2.3078 | -2.1367 | -3.4809 | -3.6264 | -3.5787
TSO | - | 14 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0065 | 1.0102 | 1.0141 | 1.0163 | 1.0159 | 1.0217 | 1.0073 | 0.9985 | 1.011 | 1.0223 | 1.0113 | 1.0224 | 1.0224 | 1.0212 | 1.023 | 1.0149 | 1.0191 | 1.0188 | 1.003 | 1.0036 | 1.0015 | 1.0028 | 1.0015 | 1.0046
TSO | - | 14 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.0663 | -3.9173 | -4.4392 | -4.2801 | -4.3592 | -4.2592 | -3.5341 | -0.78408 | -2.5568 | -3.0717 | -2.7826 | -3.0619 | -3.2735 | -3.7962 | -4.3011 | -4.3002 | -3.7234 | -3.7658 | -2.4069 | -2.5227 | -2.4861 | -3.8236 | -3.7747 | -3.6449
TSO | - | 15 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0197 | 1.0235 | 1.0264 | 1.0272 | 1.0274 | 1.0311 | 1.0182 | 1.012 | 1.0177 | 1.0267 | 1.0208 | 1.0239 | 1.0249 | 1.0254 | 1.0287 | 1.0211 | 1.0259 | 1.0253 | 1.017 | 1.0175 | 1.0149 | 1.0173 | 1.0165 | 1.018
TSO | - | 15 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.192 | -3.0301 | -3.4784 | -3.4056 | -3.4172 | -3.4119 | -2.8503 | -0.24206 | -1.6572 | -2.0289 | -1.7312 | -2.2377 | -2.3783 | -2.522 | -3.2759 | -3.2422 | -2.5025 | -2.5488 | -2.0042 | -1.889 | -1.866 | -3.0748 | -2.8062 | -2.791
TSO | - | 16 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98266 | 0.98375 | 0.98745 | 0.9879 | 0.98821 | 0.99162 | 0.98282 | 0.9787 | 1.016 | 1.0355 | 1.013 | 1.0397 | 1.0419 | 1.0416 | 1.0367 | 1.0292 | 1.0364 | 1.0368 | 0.98596 | 0.98495 | 0.98516 | 0.98465 | 0.98159 | 0.9801
TSO | - | 16 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.9687 | -4.1649 | -4.3008 | -4.2374 | -4.2426 | -4.2926 | -3.4295 | -2.3705 | -3.9998 | -4.4358 | -4.1657 | -3.9878 | -3.9123 | -4.0794 | -4.0965 | -3.7861 | -4.2428 | -4.2373 | -2.0593 | -2.826 | -2.638 | -3.2461 | -3.7644 | -3.8505
TSO | - | 17 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0133 | 1.014 | 1.0165 | 1.0167 | 1.0169 | 1.0186 | 1.0106 | 1.007 | 1.026 | 1.0376 | 1.0262 | 1.0391 | 1.039 | 1.0397 | 1.0372 | 1.0348 | 1.0376 | 1.0368 | 1.0103 | 1.0123 | 1.0109 | 1.0112 | 1.012 | 1.0114
TSO | - | 17 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.5929 | -2.6461 | -2.7186 | -2.7078 | -2.7379 | -2.7821 | -2.4997 | -2.1257 | -2.8552 | -2.9699 | -2.869 | -2.9475 | -2.9116 | -2.921 | -2.9249 | -2.6808 | -2.9471 | -2.942 | -1.8778 | -2.2241 | -2.2542 | -2.4457 | -2.5169 | -2.5486
TSO | - | 18 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0329 | 1.0424 | 1.0469 | 1.0431 | 1.0429 | 1.0438 | 1.0182 | 0.9993 | 0.993 | 0.99848 | 1.0052 | 0.9861 | 0.98668 | 0.99412 | 1.0044 | 0.99799 | 1.0098 | 1.0096 | 1.0147 | 1.0132 | 1.0091 | 1.0168 | 1.0198 | 1.0244
TSO | - | 18 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.5914 | -5.0959 | -5.425 | -5.473 | -5.4789 | -5.9035 | -6.1801 | -2.2939 | -3.9295 | -3.9407 | -3.0665 | -4.9043 | -4.8706 | -4.3114 | -5.8547 | -5.7332 | -4.0661 | -4.097 | -4.7271 | -4.4487 | -4.5086 | -6.3144 | -4.9562 | -4.8829
TSO | - | 19 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0136 | 1.0205 | 1.0259 | 1.0314 | 1.029 | 1.0314 | 1.0066 | 0.9864 | 0.98486 | 0.99696 | 0.99907 | 0.98755 | 0.98871 | 0.98683 | 0.98981 | 0.98614 | 0.99419 | 0.9949 | 0.99781 | 0.99694 | 0.99334 | 0.99946 | 1.0077 | 1.0139
TSO | - | 19 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.3535 | -5.9853 | -6.4697 | -5.8274 | -6.0162 | -6.7155 | -6.6678 | -2.8086 | -4.2446 | -3.6666 | -2.9521 | -4.5453 | -4.5458 | -4.8961 | -6.8326 | -6.7477 | -5.0294 | -5.0692 | -4.9948 | -4.8426 | -4.9809 | -6.7217 | -5.1209 | -5.2437
TSO | - | 20 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0097 | 1.0147 | 1.0215 | 1.0271 | 1.025 | 1.0322 | 1.0081 | 0.98341 | 0.98176 | 0.98884 | 0.98807 | 0.98302 | 0.98472 | 0.98031 | 0.98621 | 0.98449 | 0.98722 | 0.98851 | 0.99111 | 0.99059 | 0.98757 | 0.99266 | 0.9978 | 1.0083
TSO | - | 20 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.3862 | -6.1032 | -6.5273 | -5.9794 | -6.1597 | -6.6113 | -6.5123 | -2.9304 | -4.5225 | -4.4267 | -3.8046 | -5.1278 | -5.1461 | -5.7929 | -7.2654 | -7.2057 | -5.7512 | -5.7949 | -5.1243 | -5.0485 | -5.2435 | -6.9451 | -5.7279 | -5.7046
TSO | - | 21 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.003 | 1.0055 | 1.0132 | 1.0199 | 1.0189 | 1.0261 | 1.0042 | 0.98327 | 0.98786 | 0.99518 | 0.9894 | 0.99352 | 0.9943 | 0.99288 | 0.99526 | 0.9917 | 0.99394 | 0.99416 | 0.98686 | 0.98833 | 0.98686 | 0.98871 | 0.99288 | 1.0026
TSO | - | 21 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.9691 | -5.9288 | -6.2437 | -5.8226 | -5.9614 | -5.9057 | -5.5836 | -2.4085 | -4.1624 | -4.9226 | -4.4908 | -5.0267 | -5.3951 | -6.2761 | -7.0799 | -6.9775 | -6.0814 | -6.1528 | -4.8129 | -4.7827 | -5.0095 | -6.6776 | -6.2772 | -5.9326
TSO | - | 22 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0027 | 1.0045 | 1.0124 | 1.019 | 1.0183 | 1.0264 | 1.0052 | 0.98411 | 0.98936 | 0.99533 | 0.9885 | 0.99527 | 0.99534 | 0.994 | 0.99693 | 0.99316 | 0.99442 | 0.99443 | 0.98673 | 0.98842 | 0.98714 | 0.98856 | 0.99125 | 1.0014
TSO | - | 22 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.8699 | -5.8529 | -6.156 | -5.7603 | -5.8988 | -5.7669 | -5.4232 | -2.3294 | -4.1422 | -5.0315 | -4.6019 | -5.0689 | -5.4846 | -6.4168 | -7.1016 | -6.9828 | -6.1676 | -6.2373 | -4.7425 | -4.7302 | -4.9704 | -6.6155 | -6.3338 | -5.9364
TSO | - | 23 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0022 | 1.0037 | 1.0119 | 1.0187 | 1.018 | 1.0262 | 1.0047 | 0.98399 | 0.98885 | 0.99416 | 0.98779 | 0.9943 | 0.99426 | 0.99288 | 0.99562 | 0.99201 | 0.99337 | 0.9934 | 0.98623 | 0.98796 | 0.98655 | 0.98789 | 0.99051 | 1.0004
TSO | - | 23 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.8646 | -5.8422 | -6.1527 | -5.7551 | -5.8933 | -5.7581 | -5.4184 | -2.2868 | -4.1031 | -5.0078 | -4.5687 | -5.0495 | -5.4804 | -6.4258 | -7.1208 | -6.9979 | -6.178 | -6.2476 | -4.7569 | -4.7294 | -4.9822 | -6.6448 | -6.3563 | -5.968
TSO | - | 24 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99048 | 0.98482 | 0.99575 | 1.0048 | 1.0051 | 1.0125 | 0.99072 | 0.97922 | 0.97833 | 0.97811 | 0.97988 | 0.98186 | 0.98296 | 0.98283 | 0.98229 | 0.97959 | 0.98199 | 0.98154 | 0.98078 | 0.98356 | 0.98177 | 0.9827 | 0.98427 | 0.99001
TSO | - | 24 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.7023 | -5.7794 | -6.2341 | -5.7757 | -5.7726 | -5.7052 | -5.2681 | -1.681 | -3.6455 | -4.618 | -3.9589 | -4.5361 | -4.8386 | -5.5759 | -6.5035 | -6.3203 | -5.4741 | -5.5509 | -4.591 | -4.2104 | -4.3558 | -6.164 | -5.7585 | -5.4174
TSO | - | 25 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97876 | 0.95903 | 0.97908 | 0.99584 | 0.99597 | 1.0043 | 0.9799 | 0.96388 | 0.96304 | 0.95237 | 0.96334 | 0.96266 | 0.96508 | 0.96326 | 0.95697 | 0.96211 | 0.96391 | 0.96399 | 0.96509 | 0.96657 | 0.96528 | 0.9654 | 0.97011 | 0.97671
TSO | - | 25 | 2020 | Summer | Vang, [º] | 0 | 0 | -7.1498 | -9.0733 | -8.7186 | -7.3088 | -7.2606 | -7.0008 | -6.3805 | -2.672 | -4.6649 | -6.3985 | -4.8386 | -5.3856 | -5.5614 | -6.2583 | -7.6459 | -7.2236 | -6.5001 | -6.5983 | -6.0308 | -5.4672 | -5.5357 | -7.1428 | -6.878 | -6.293
TSO | - | 26 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98946 | 0.98423 | 0.99496 | 1.0035 | 1.0038 | 1.011 | 0.98934 | 0.97875 | 0.97731 | 0.97732 | 0.97908 | 0.98082 | 0.98177 | 0.98165 | 0.98146 | 0.97818 | 0.98073 | 0.98018 | 0.98089 | 0.9834 | 0.98136 | 0.9825 | 0.98352 | 0.98871
TSO | - | 26 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.6259 | -5.6122 | -6.1313 | -5.7265 | -5.7028 | -5.663 | -5.2303 | -1.5485 | -3.5583 | -4.5096 | -3.8498 | -4.4641 | -4.7537 | -5.4605 | -6.4 | -6.2223 | -5.3579 | -5.4364 | -4.485 | -4.0671 | -4.2061 | -6.0511 | -5.6239 | -5.3277
TSO | - | 27 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98865 | 0.99123 | 0.99703 | 0.9998 | 1.0011 | 1.0061 | 0.98426 | 0.98424 | 0.97715 | 0.97962 | 0.98142 | 0.97957 | 0.98056 | 0.9823 | 0.98331 | 0.97657 | 0.98103 | 0.97988 | 0.98788 | 0.99123 | 0.98826 | 0.98829 | 0.98772 | 0.98723
TSO | - | 27 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.009 | -4.6007 | -5.422 | -5.2087 | -5.0648 | -5.1546 | -4.7459 | -0.74605 | -2.8829 | -3.767 | -3.103 | -3.8637 | -4.0547 | -4.5992 | -5.6777 | -5.406 | -4.4768 | -4.5441 | -3.9431 | -3.2714 | -3.3259 | -5.4089 | -4.7539 | -4.5814
TSO | - | 28 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99205 | 0.99759 | 1.001 | 1.0018 | 1.003 | 1.0077 | 0.98718 | 0.99243 | 0.98312 | 0.98671 | 0.9881 | 0.98538 | 0.98624 | 0.98883 | 0.98949 | 0.98129 | 0.98654 | 0.98506 | 0.99563 | 0.99958 | 0.99611 | 0.99564 | 0.99388 | 0.99101
TSO | - | 28 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.4119 | -3.8662 | -4.8254 | -4.664 | -4.5079 | -4.6195 | -4.1307 | 0.047106 | -2.1371 | -2.9796 | -2.3482 | -3.1396 | -3.3014 | -3.7771 | -4.8962 | -4.6449 | -3.6876 | -3.7518 | -3.2867 | -2.5092 | -2.5393 | -4.7072 | -4.0044 | -3.8836
TSO | - | 29 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.9958 | 1.0031 | 1.0047 | 1.0042 | 1.0055 | 1.0094 | 0.99035 | 0.99986 | 0.98935 | 0.9944 | 0.99557 | 0.99269 | 0.99356 | 0.99664 | 0.99654 | 0.98732 | 0.99291 | 0.99139 | 1.0031 | 1.0075 | 1.0036 | 1.0031 | 1.0004 | 0.99557
TSO | - | 29 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.9305 | -3.3168 | -4.3599 | -4.2287 | -4.064 | -4.1824 | -3.6379 | 0.63449 | -1.5598 | -2.4026 | -1.7771 | -2.5935 | -2.7429 | -3.1675 | -4.3069 | -4.0551 | -3.084 | -3.1469 | -2.7715 | -1.9328 | -1.9393 | -4.1585 | -3.4175 | -3.3328
TSO | - | 30 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97107 | 0.95391 | 0.97213 | 0.98852 | 0.9883 | 0.99823 | 0.97348 | 0.9568 | 0.95615 | 0.94744 | 0.95595 | 0.95639 | 0.9578 | 0.95632 | 0.95081 | 0.9549 | 0.95558 | 0.95562 | 0.95607 | 0.95701 | 0.95646 | 0.95738 | 0.96167 | 0.96918
TSO | - | 30 | 2020 | Summer | Vang, [º] | 0 | 0 | -7.4575 | -9.3585 | -9.1203 | -7.6961 | -7.6128 | -7.3051 | -6.6072 | -2.8444 | -4.8229 | -6.4027 | -4.926 | -5.4143 | -5.5586 | -6.2309 | -7.6445 | -7.294 | -6.6061 | -6.7126 | -6.1708 | -5.675 | -5.6981 | -7.2735 | -7.0267 | -6.3941
TSO | - | 31 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.96153 | 0.95083 | 0.96469 | 0.9801 | 0.97899 | 0.99264 | 0.96699 | 0.94845 | 0.94812 | 0.94387 | 0.94643 | 0.94946 | 0.94847 | 0.94779 | 0.94435 | 0.94607 | 0.94406 | 0.94393 | 0.9429 | 0.9425 | 0.94387 | 0.94661 | 0.94988 | 0.95953
TSO | - | 31 | 2020 | Summer | Vang, [º] | 0 | 0 | -8.5829 | -10.4308 | -10.4808 | -9.0136 | -8.8456 | -8.4052 | -7.5267 | -3.6313 | -5.568 | -6.7573 | -5.4894 | -5.8248 | -5.8962 | -6.5067 | -7.9916 | -7.8253 | -7.2294 | -7.3551 | -6.882 | -6.5545 | -6.4674 | -7.956 | -7.7537 | -6.9955
TSO | - | 32 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98077 | 0.9814 | 0.99329 | 1.0032 | 1.0013 | 1.0147 | 0.98312 | 0.95312 | 0.95042 | 0.951 | 0.94698 | 0.94959 | 0.94556 | 0.94499 | 0.94842 | 0.95276 | 0.95165 | 0.95323 | 0.95286 | 0.95095 | 0.95222 | 0.95149 | 0.95833 | 0.97348
TSO | - | 32 | 2020 | Summer | Vang, [º] | 0 | 0 | -9.2488 | -10.2701 | -10.2641 | -9.1673 | -9.1331 | -8.9528 | -8.5115 | -4.9692 | -7.0137 | -8.1373 | -7.1704 | -7.5811 | -7.7357 | -8.441 | -9.5981 | -9.5106 | -8.7852 | -8.9342 | -8.0141 | -7.9458 | -7.9297 | -9.4797 | -9.2157 | -8.2758
TSO | - | 33 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98034 | 0.98118 | 0.99319 | 1.0032 | 1.0013 | 1.0147 | 0.98273 | 0.95235 | 0.94925 | 0.94972 | 0.94561 | 0.94811 | 0.94384 | 0.94333 | 0.94679 | 0.95142 | 0.95035 | 0.95199 | 0.95182 | 0.94985 | 0.9511 | 0.95027 | 0.95728 | 0.97283
TSO | - | 33 | 2020 | Summer | Vang, [º] | 0 | 0 | -9.3163 | -10.3347 | -10.3233 | -9.2255 | -9.1902 | -9.0268 | -8.5942 | -5.0452 | -7.0887 | -8.2122 | -7.2448 | -7.6613 | -7.8097 | -8.5137 | -9.6691 | -9.5926 | -8.8588 | -9.011 | -8.0953 | -8.0293 | -8.0124 | -9.5627 | -9.2973 | -8.3455
TSO | - | 34 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98786 | 0.98887 | 0.99804 | 1.0059 | 1.0052 | 1.0146 | 0.98701 | 0.96084 | 0.96306 | 0.96918 | 0.96335 | 0.96813 | 0.9675 | 0.96755 | 0.97219 | 0.97144 | 0.97218 | 0.97319 | 0.9646 | 0.96528 | 0.96603 | 0.96536 | 0.97134 | 0.98633
TSO | - | 34 | 2020 | Summer | Vang, [º] | 0 | 0 | -7.2366 | -7.3834 | -7.6423 | -7.1088 | -7.218 | -7.147 | -6.7712 | -3.5901 | -5.4639 | -6.2983 | -5.7747 | -6.1495 | -6.4219 | -7.2488 | -7.9924 | -7.967 | -7.2002 | -7.3038 | -5.9948 | -6.0169 | -6.1687 | -7.7676 | -7.5206 | -6.9051
TSO | - | 35 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99025 | 0.99216 | 1.0009 | 1.0081 | 1.0073 | 1.0163 | 0.98888 | 0.96262 | 0.9654 | 0.97225 | 0.96586 | 0.97085 | 0.97038 | 0.97036 | 0.97549 | 0.97428 | 0.9752 | 0.97621 | 0.96733 | 0.96812 | 0.96867 | 0.96796 | 0.97387 | 0.98855
TSO | - | 35 | 2020 | Summer | Vang, [º] | 0 | 0 | -7.0931 | -7.1725 | -7.4427 | -6.9468 | -7.0713 | -6.996 | -6.6386 | -3.4995 | -5.3764 | -6.2063 | -5.7119 | -6.0909 | -6.3839 | -7.2224 | -7.9372 | -7.8998 | -7.1358 | -7.2339 | -5.8671 | -5.9051 | -6.0683 | -7.6713 | -7.4224 | -6.8314
TSO | - | 36 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99356 | 0.99607 | 1.0043 | 1.0111 | 1.0102 | 1.0188 | 0.99297 | 0.96762 | 0.97113 | 0.97817 | 0.97131 | 0.97703 | 0.97653 | 0.97625 | 0.98119 | 0.97936 | 0.98038 | 0.98108 | 0.97212 | 0.97303 | 0.97327 | 0.97303 | 0.97825 | 0.99201
TSO | - | 36 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.8574 | -6.8948 | -7.1794 | -6.7075 | -6.8424 | -6.7608 | -6.4057 | -3.3029 | -5.1828 | -6.0187 | -5.5483 | -5.9402 | -6.2477 | -7.1051 | -7.7845 | -7.7318 | -6.9695 | -7.0607 | -5.6448 | -5.6842 | -5.8518 | -7.4648 | -7.2055 | -6.6415
TSO | - | 37 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99624 | 0.99884 | 1.0069 | 1.0134 | 1.0126 | 1.0211 | 0.99645 | 0.97189 | 0.97602 | 0.98306 | 0.97586 | 0.98214 | 0.98169 | 0.98117 | 0.98581 | 0.98345 | 0.98448 | 0.98498 | 0.97606 | 0.97713 | 0.97705 | 0.97723 | 0.9818 | 0.99482
TSO | - | 37 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.6337 | -6.6533 | -6.9409 | -6.4902 | -6.6284 | -6.5355 | -6.1844 | -3.1104 | -4.9815 | -5.8284 | -5.3738 | -5.7762 | -6.1035 | -6.976 | -7.6377 | -7.5697 | -6.8024 | -6.888 | -5.4386 | -5.4758 | -5.6529 | -7.2679 | -7.008 | -6.4722
TSO | - | 38 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0036 | 1.0056 | 1.0132 | 1.0194 | 1.0187 | 1.0269 | 1.0064 | 0.98455 | 0.99075 | 0.99762 | 0.98963 | 0.99759 | 0.99769 | 0.99644 | 0.99989 | 0.99576 | 0.99658 | 0.99651 | 0.98768 | 0.98935 | 0.98834 | 0.98982 | 0.99225 | 1.0029
TSO | - | 38 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.8548 | -5.8539 | -6.1399 | -5.7543 | -5.8936 | -5.7489 | -5.392 | -2.3921 | -4.2131 | -5.1051 | -4.6942 | -5.1175 | -5.5155 | -6.4352 | -7.0704 | -6.9554 | -6.1695 | -6.2388 | -4.6968 | -4.7185 | -4.9375 | -6.543 | -6.3042 | -5.8757
TSO | - | 39 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99574 | 0.99858 | 1.0066 | 1.0131 | 1.0122 | 1.0206 | 0.99572 | 0.97095 | 0.9749 | 0.982 | 0.97481 | 0.98099 | 0.98041 | 0.97996 | 0.98472 | 0.98251 | 0.98362 | 0.98413 | 0.97518 | 0.97617 | 0.97615 | 0.97624 | 0.98098 | 0.9942
TSO | - | 39 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.6981 | -6.7075 | -6.9997 | -6.5457 | -6.6868 | -6.6033 | -6.2529 | -3.1748 | -5.0539 | -5.8942 | -5.4396 | -5.8415 | -6.1609 | -7.0309 | -7.6871 | -7.6246 | -6.8595 | -6.9468 | -5.5003 | -5.5406 | -5.7122 | -7.3311 | -7.0653 | -6.5193
TSO | - | 40 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99313 | 0.996 | 1.0042 | 1.0108 | 1.0098 | 1.0184 | 0.99224 | 0.96667 | 0.97004 | 0.97724 | 0.97039 | 0.97604 | 0.97542 | 0.97522 | 0.98035 | 0.97865 | 0.97976 | 0.98046 | 0.97139 | 0.9722 | 0.97254 | 0.9722 | 0.97763 | 0.99151
TSO | - | 40 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.9347 | -6.9577 | -7.2507 | -6.7735 | -6.9132 | -6.8406 | -6.4844 | -3.378 | -5.2719 | -6.0983 | -5.628 | -6.0185 | -6.3144 | -7.1686 | -7.8396 | -7.792 | -7.0364 | -7.129 | -5.7142 | -5.7579 | -5.917 | -7.5364 | -7.268 | -6.6912
TSO | - | 41 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0114 | 1.0184 | 1.0221 | 1.0246 | 1.0227 | 1.0298 | 1.0042 | 0.98588 | 0.99306 | 1.0049 | 0.9967 | 1.0046 | 1.0003 | 1.001 | 1.0046 | 1.0027 | 1.0072 | 1.0069 | 0.99353 | 0.9972 | 0.99543 | 0.99585 | 1.0008 | 1.0058
TSO | - | 41 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.9272 | -6.3926 | -7.2366 | -6.695 | -7.0542 | -7.1407 | -6.6443 | -3.7169 | -5.9875 | -6.5113 | -6.0307 | -6.4881 | -6.6514 | -7.3572 | -7.7375 | -7.5946 | -7.031 | -7.0845 | -5.5788 | -5.6741 | -5.5816 | -7.3321 | -6.7339 | -6.147
TSO | - | 42 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0049 | 1.013 | 1.0199 | 1.0218 | 1.0197 | 1.0271 | 0.99431 | 0.96254 | 0.96781 | 0.97689 | 0.97162 | 0.97465 | 0.96936 | 0.97038 | 0.97823 | 0.97978 | 0.98564 | 0.98635 | 0.97457 | 0.97514 | 0.97473 | 0.97518 | 0.98267 | 0.99464
TSO | - | 42 | 2020 | Summer | Vang, [º] | 0 | 0 | -8.3139 | -7.7927 | -8.4215 | -7.9157 | -8.2389 | -8.363 | -8.1292 | -5.0783 | -7.3616 | -7.8367 | -7.3422 | -7.7825 | -7.9107 | -8.6348 | -8.9556 | -8.8898 | -8.2957 | -8.3893 | -6.9932 | -7.1626 | -7.1029 | -8.9611 | -8.3312 | -7.5616
TSO | - | 43 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99805 | 1.0044 | 1.0068 | 1.0089 | 1.0071 | 1.0133 | 0.99452 | 0.98868 | 0.99883 | 1.0119 | 1.001 | 1.0134 | 1.0116 | 1.0112 | 1.0119 | 1.0051 | 1.0104 | 1.0103 | 0.99428 | 0.99678 | 0.9946 | 0.9946 | 0.99508 | 0.99595
TSO | - | 43 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.1378 | -4.6451 | -5.798 | -5.1932 | -5.5837 | -5.6875 | -4.6079 | -1.2786 | -3.461 | -3.9514 | -3.4971 | -3.7949 | -3.9479 | -4.68 | -5.2702 | -5.2017 | -4.6679 | -4.7114 | -3.14 | -3.1308 | -2.9891 | -4.6819 | -4.2549 | -4.1051
TSO | - | 44 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0072 | 1.01 | 1.0166 | 1.0216 | 1.021 | 1.0285 | 1.0092 | 0.98961 | 0.99536 | 1.0029 | 0.99544 | 1.0015 | 1.0029 | 1.0016 | 1.0052 | 1.0008 | 1.0021 | 1.0022 | 0.99337 | 0.99473 | 0.99346 | 0.99533 | 0.99777 | 1.0069
TSO | - | 44 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.5169 | -5.4731 | -5.778 | -5.4496 | -5.5652 | -5.4412 | -5.0851 | -2.2194 | -3.9485 | -4.7345 | -4.385 | -4.837 | -5.0798 | -5.9001 | -6.5468 | -6.4529 | -5.6876 | -5.7427 | -4.4029 | -4.3995 | -4.5647 | -6.1032 | -5.8093 | -5.449
TSO | - | 45 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0191 | 1.0227 | 1.0269 | 1.029 | 1.0291 | 1.0342 | 1.0189 | 1.0065 | 1.0128 | 1.022 | 1.0153 | 1.0196 | 1.0209 | 1.0219 | 1.0252 | 1.0188 | 1.0221 | 1.0218 | 1.0118 | 1.0128 | 1.0111 | 1.0139 | 1.0144 | 1.0186
TSO | - | 45 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.2555 | -4.1494 | -4.5152 | -4.3091 | -4.3693 | -4.2907 | -3.8552 | -1.2204 | -2.7663 | -3.3193 | -3.01 | -3.4756 | -3.6561 | -4.0948 | -4.8019 | -4.7252 | -3.9944 | -4.04 | -3.1665 | -3.0928 | -3.1409 | -4.4911 | -4.1927 | -3.987
TSO | - | 46 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0098 | 1.0137 | 1.0188 | 1.0227 | 1.0222 | 1.0294 | 1.0123 | 0.99705 | 1.0073 | 1.0164 | 1.0058 | 1.0169 | 1.017 | 1.0166 | 1.0191 | 1.0127 | 1.0159 | 1.0159 | 1.0011 | 1.0021 | 1.0008 | 1.0025 | 1.002 | 1.0073
TSO | - | 46 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.6554 | -4.5193 | -4.9184 | -4.6479 | -4.8068 | -4.6221 | -4.1116 | -1.3198 | -3.1245 | -3.8981 | -3.5565 | -3.9347 | -4.3524 | -5.1696 | -5.6766 | -5.5995 | -4.9676 | -5.0104 | -3.3639 | -3.4872 | -3.6429 | -5.1184 | -5.0036 | -4.7862
TSO | - | 47 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0096 | 1.0135 | 1.0205 | 1.0266 | 1.0255 | 1.0344 | 1.0137 | 0.99276 | 1.0008 | 1.0063 | 0.99655 | 1.007 | 1.0062 | 1.005 | 1.0082 | 1.0038 | 1.0062 | 1.0065 | 0.99424 | 0.9955 | 0.99413 | 0.99549 | 0.9961 | 1.0037
TSO | - | 47 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.2561 | -5.1342 | -5.4406 | -5.0952 | -5.3256 | -5.0854 | -4.7294 | -1.7909 | -3.5891 | -4.568 | -4.1847 | -4.6572 | -5.2719 | -6.3815 | -6.9012 | -6.7775 | -6.0772 | -6.1251 | -4.2232 | -4.3599 | -4.7104 | -6.3223 | -6.1583 | -5.8918
TSO | - | 48 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0067 | 1.0092 | 1.0167 | 1.023 | 1.0222 | 1.0307 | 1.0103 | 0.98905 | 0.99675 | 1.003 | 0.99396 | 1.0039 | 1.0038 | 1.0027 | 1.0061 | 1.0016 | 1.0036 | 1.0036 | 0.99159 | 0.99315 | 0.99207 | 0.99353 | 0.99471 | 1.0032
TSO | - | 48 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.4601 | -5.4212 | -5.7102 | -5.3315 | -5.528 | -5.3272 | -4.944 | -2.0047 | -3.8308 | -4.7986 | -4.3776 | -4.8192 | -5.3348 | -6.3574 | -6.9167 | -6.787 | -6.078 | -6.1291 | -4.3505 | -4.4515 | -4.7353 | -6.3327 | -6.1556 | -5.8366
TSO | - | 49 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0018 | 0.99885 | 1.0084 | 1.0156 | 1.0154 | 1.023 | 1.0044 | 0.98337 | 0.9934 | 1.0024 | 0.99341 | 1.0056 | 1.0079 | 1.0069 | 1.0113 | 1.0058 | 1.0085 | 1.0074 | 0.98911 | 0.99164 | 0.99135 | 0.99316 | 0.99379 | 1.0003
TSO | - | 49 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.5294 | -5.8641 | -6.0549 | -5.5144 | -5.6802 | -5.5446 | -4.943 | -2.1721 | -4.1679 | -5.2543 | -4.5925 | -4.9378 | -5.2324 | -6.0764 | -6.6342 | -6.4356 | -5.8968 | -5.9236 | -4.1469 | -4.2652 | -4.3686 | -5.866 | -5.7704 | -5.4482
TSO | - | 50 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.99265 | 0.99575 | 1.0036 | 1.0075 | 1.0074 | 1.0157 | 0.99432 | 0.96458 | 0.97424 | 0.99233 | 0.97523 | 0.99029 | 0.993 | 0.99246 | 1.0067 | 0.99636 | 0.99925 | 0.99511 | 0.96973 | 0.97539 | 0.9757 | 0.97848 | 0.97955 | 0.98645
TSO | - | 50 | 2020 | Summer | Vang, [º] | 0 | 0 | -6.3576 | -6.6187 | -6.9616 | -6.4369 | -6.6049 | -6.5849 | -5.7856 | -3.059 | -5.0533 | -6.1491 | -5.4516 | -5.6815 | -5.8497 | -6.6375 | -7.291 | -6.9927 | -6.5938 | -6.5448 | -4.5877 | -4.9545 | -4.9685 | -6.5042 | -6.3832 | -6.1207
TSO | - | 51 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98802 | 0.99239 | 0.99665 | 0.99841 | 0.99817 | 1.0029 | 0.985 | 0.97058 | 0.99425 | 1.0154 | 0.9948 | 1.0168 | 1.0191 | 1.0189 | 1.0277 | 1.0141 | 1.0195 | 1.0186 | 0.98293 | 0.98454 | 0.98497 | 0.98631 | 0.98361 | 0.9857
TSO | - | 51 | 2020 | Summer | Vang, [º] | 0 | 0 | -5.5436 | -5.5398 | -6.2251 | -5.8162 | -5.9963 | -6.0632 | -4.914 | -2.4599 | -4.7661 | -5.6399 | -5.0566 | -5.1396 | -5.1889 | -5.7956 | -6.2002 | -5.7606 | -5.7661 | -5.7995 | -3.4916 | -3.8831 | -3.7044 | -5.0916 | -5.0844 | -5.0534
TSO | - | 52 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97984 | 0.99269 | 0.99238 | 0.99496 | 0.99651 | 1.0043 | 0.97733 | 0.97137 | 0.96024 | 0.9635 | 0.962 | 0.95661 | 0.95831 | 0.96037 | 0.96274 | 0.95851 | 0.96529 | 0.96297 | 0.97324 | 0.97739 | 0.97387 | 0.96724 | 0.96284 | 0.96752
TSO | - | 52 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.3982 | -3.5395 | -4.8412 | -4.5795 | -4.4628 | -4.7391 | -4.117 | -0.067463 | -2.5837 | -3.4316 | -2.8383 | -3.5929 | -3.7213 | -4.3122 | -5.3639 | -5.1121 | -4.2258 | -4.2344 | -3.6132 | -2.791 | -2.8854 | -5.2383 | -4.5917 | -4.1517
TSO | - | 53 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97393 | 0.98926 | 0.98759 | 0.99177 | 0.99353 | 1.0027 | 0.97245 | 0.95979 | 0.9488 | 0.95238 | 0.94961 | 0.94361 | 0.94584 | 0.94724 | 0.95001 | 0.94825 | 0.95536 | 0.9529 | 0.96167 | 0.9657 | 0.96216 | 0.95293 | 0.94739 | 0.95617
TSO | - | 53 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.4429 | -3.4757 | -4.9216 | -4.593 | -4.501 | -4.8517 | -4.1702 | -0.24785 | -2.9142 | -3.808 | -3.2079 | -3.9441 | -4.0721 | -4.736 | -5.7306 | -5.4594 | -4.6231 | -4.6041 | -3.8478 | -3.0411 | -3.1704 | -5.5967 | -4.9928 | -4.3728
TSO | - | 54 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97892 | 0.99156 | 0.98874 | 0.9927 | 0.9915 | 0.99903 | 0.97744 | 0.97459 | 0.97011 | 0.97722 | 0.97149 | 0.97421 | 0.97454 | 0.97524 | 0.97577 | 0.97035 | 0.97627 | 0.97469 | 0.97713 | 0.9809 | 0.97782 | 0.97276 | 0.96834 | 0.97064
TSO | - | 54 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.2248 | -3.33 | -5.0565 | -4.4796 | -4.6921 | -4.9056 | -3.7635 | 0.25059 | -2.3331 | -3.2322 | -2.6108 | -3.1885 | -3.337 | -4.0024 | -4.8909 | -4.6668 | -3.985 | -4.0152 | -2.9338 | -2.2584 | -2.2371 | -4.4838 | -3.9019 | -3.5393
TSO | - | 55 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.98674 | 0.99682 | 0.99308 | 0.99672 | 0.99287 | 0.99876 | 0.98522 | 0.99163 | 0.99331 | 1.0037 | 0.99515 | 1.0061 | 1.0047 | 1.0047 | 1.0031 | 0.9943 | 0.99907 | 0.99833 | 0.99473 | 0.99821 | 0.99563 | 0.99455 | 0.99121 | 0.98732
TSO | - | 55 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.1512 | -3.3258 | -5.3227 | -4.5103 | -5.0186 | -5.102 | -3.5135 | 0.59835 | -1.9042 | -2.8002 | -2.1635 | -2.5926 | -2.7613 | -3.4278 | -4.2224 | -4.0455 | -3.5036 | -3.578 | -2.2001 | -1.644 | -1.4866 | -3.5692 | -3.0097 | -2.8826
TSO | - | 56 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0014 | 1.0077 | 1.016 | 1.0194 | 1.018 | 1.0269 | 0.9954 | 0.96484 | 0.96879 | 0.97677 | 0.97019 | 0.97439 | 0.96926 | 0.96966 | 0.97645 | 0.97822 | 0.98225 | 0.98315 | 0.97229 | 0.97236 | 0.97272 | 0.97197 | 0.97923 | 0.99272
TSO | - | 56 | 2020 | Summer | Vang, [º] | 0 | 0 | -8.6132 | -8.1318 | -8.6412 | -8.1521 | -8.4338 | -8.582 | -8.4022 | -5.4029 | -7.6401 | -8.1838 | -7.709 | -8.1182 | -8.2948 | -9.0392 | -9.4188 | -9.3677 | -8.6712 | -8.7891 | -7.4762 | -7.6643 | -7.5996 | -9.4031 | -8.8237 | -7.9298
TSO | - | 57 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0015 | 1.0077 | 1.0169 | 1.0211 | 1.0199 | 1.03 | 0.99726 | 0.96538 | 0.96738 | 0.97425 | 0.96693 | 0.97095 | 0.96477 | 0.96512 | 0.97143 | 0.97445 | 0.9782 | 0.9795 | 0.97031 | 0.97042 | 0.97029 | 0.96931 | 0.97669 | 0.99201
TSO | - | 57 | 2020 | Summer | Vang, [º] | 0 | 0 | -8.8014 | -8.3184 | -8.7295 | -8.2492 | -8.5051 | -8.7007 | -8.6763 | -5.7347 | -7.9942 | -8.5981 | -8.1489 | -8.6235 | -8.8767 | -9.619 | -10.0051 | -9.9356 | -9.1452 | -9.2622 | -7.9327 | -8.1248 | -8.0981 | -9.9018 | -9.3133 | -8.3053
TSO | - | 1 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
TSO | - | 1 | 2020 | Summer | Vang, [º] | Expected | - | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
TSO | - | 2 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0467 | 1.054 | 1.0537 | 1.0509 | 1.0514 | 1.0549 | 1.0475 | 1.0357 | 1.025 | 1.0338 | 1.0288 | 1.0221 | 1.023 | 1.026 | 1.0385 | 1.0319 | 1.0349 | 1.0281 | 1.0289 | 1.0385 | 1.0373 | 1.0409 | 1.0435 | 1.0402
TSO | - | 2 | 2020 | Summer | Vang, [º] | Expected | - | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402
TSO | - | 3 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0308 | 1.0369 | 1.0391 | 1.0374 | 1.0386 | 1.0399 | 1.0246 | 1.0244 | 1.0188 | 1.0274 | 1.0291 | 1.0162 | 1.0189 | 1.0246 | 1.0317 | 1.0197 | 1.0278 | 1.0259 | 1.0314 | 1.0318 | 1.0262 | 1.0316 | 1.0309 | 1.0287
TSO | - | 3 | 2020 | Summer | Vang, [º] | Expected | - | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287 | 1.0287
TSO | - | 4 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0271 | 1.0337 | 1.0363 | 1.0342 | 1.0351 | 1.036 | 1.0192 | 1.0193 | 1.0126 | 1.0211 | 1.0237 | 1.0108 | 1.0132 | 1.019 | 1.0252 | 1.0138 | 1.0221 | 1.0205 | 1.027 | 1.0274 | 1.0219 | 1.0271 | 1.0269 | 1.0249
TSO | - | 4 | 2020 | Summer | Vang, [º] | Expected | - | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249 | 1.0249
TSO | - | 5 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0204 | 1.0273 | 1.0294 | 1.0271 | 1.0282 | 1.0291 | 1.0127 | 1.0174 | 1.0088 | 1.0172 | 1.0196 | 1.0088 | 1.011 | 1.0168 | 1.02 | 1.0086 | 1.0163 | 1.0149 | 1.0232 | 1.0248 | 1.0193 | 1.0232 | 1.022 | 1.0189
TSO | - | 5 | 2020 | Summer | Vang, [º] | Expected | - | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189
TSO | - | 6 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0179 | 1.0241 | 1.0261 | 1.0234 | 1.0241 | 1.0245 | 1.0099 | 1.0196 | 1.0107 | 1.0193 | 1.0216 | 1.0129 | 1.0146 | 1.0204 | 1.022 | 1.0096 | 1.0168 | 1.0155 | 1.0244 | 1.0267 | 1.0212 | 1.0255 | 1.0242 | 1.0189
TSO | - | 6 | 2020 | Summer | Vang, [º] | Expected | - | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189 | 1.0189
TSO | - | 7 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99712 | 1.0043 | 1.0051 | 1.0034 | 1.0043 | 1.0061 | 0.99027 | 1.0059 | 0.99393 | 1.0005 | 1.0021 | 1.0004 | 1.0009 | 1.0037 | 1.0027 | 0.99129 | 0.99642 | 0.99529 | 1.0093 | 1.0136 | 1.0088 | 1.0099 | 1.0067 | 0.99908
TSO | - | 7 | 2020 | Summer | Vang, [º] | Expected | - | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908 | 0.99908
TSO | - | 8 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98596 | 0.99338 | 0.99233 | 0.98928 | 0.98996 | 0.99028 | 0.97822 | 1.0073 | 0.99221 | 0.9995 | 1.001 | 1.0061 | 1.0052 | 1.006 | 1.0018 | 0.98798 | 0.99119 | 0.99054 | 1.0104 | 1.0163 | 1.0111 | 1.0126 | 1.0076 | 0.99333
TSO | - | 8 | 2020 | Summer | Vang, [º] | Expected | - | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333 | 0.99333
TSO | - | 9 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99184 | 1.0005 | 0.99748 | 1.0001 | 0.99711 | 1.0018 | 0.98947 | 0.99818 | 1.0015 | 1.0134 | 1.0041 | 1.0171 | 1.0155 | 1.0154 | 1.0126 | 1.0033 | 1.0085 | 1.0085 | 1.0013 | 1.0052 | 1.0022 | 1.0012 | 0.99888 | 0.99425
TSO | - | 9 | 2020 | Summer | Vang, [º] | Expected | - | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425 | 0.99425
TSO | - | 10 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98231 | 0.98643 | 0.98973 | 0.99127 | 0.99074 | 0.99551 | 0.98036 | 0.97307 | 1.0008 | 1.0218 | 1.0005 | 1.0249 | 1.0265 | 1.0261 | 1.0281 | 1.0161 | 1.023 | 1.0226 | 0.98299 | 0.98419 | 0.98381 | 0.98408 | 0.97968 | 0.98049
TSO | - | 10 | 2020 | Summer | Vang, [º] | Expected | - | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049 | 0.98049
TSO | - | 11 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99449 | 1.0005 | 1.0018 | 1.004 | 1.0024 | 1.0079 | 0.99264 | 0.99126 | 1.0026 | 1.0163 | 1.0044 | 1.0186 | 1.0178 | 1.017 | 1.0163 | 1.0078 | 1.0135 | 1.0134 | 0.99639 | 0.99843 | 0.99623 | 0.99611 | 0.99477 | 0.99409
TSO | - | 11 | 2020 | Summer | Vang, [º] | Expected | - | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409 | 0.99409
TSO | - | 12 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.963 | 0.96415 | 0.96903 | 0.96943 | 0.9696 | 0.97435 | 0.96385 | 0.95972 | 1.013 | 1.0407 | 1.009 | 1.0469 | 1.0498 | 1.0498 | 1.0421 | 1.0314 | 1.0413 | 1.0419 | 0.97031 | 0.96927 | 0.96909 | 0.96918 | 0.96405 | 0.96073
TSO | - | 12 | 2020 | Summer | Vang, [º] | Expected | - | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073 | 0.96073
TSO | - | 13 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99552 | 0.99892 | 1.0026 | 1.0045 | 1.0041 | 1.01 | 0.99587 | 0.99023 | 1.0093 | 1.0246 | 1.0094 | 1.0266 | 1.0273 | 1.0257 | 1.0259 | 1.0164 | 1.0226 | 1.0225 | 0.99638 | 0.99674 | 0.99529 | 0.99576 | 0.99324 | 0.99407
TSO | - | 13 | 2020 | Summer | Vang, [º] | Expected | - | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407 | 0.99407
TSO | - | 14 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0065 | 1.0102 | 1.0141 | 1.0163 | 1.0159 | 1.0217 | 1.0073 | 0.9985 | 1.011 | 1.0223 | 1.0113 | 1.0224 | 1.0224 | 1.0212 | 1.023 | 1.0149 | 1.0191 | 1.0188 | 1.003 | 1.0036 | 1.0015 | 1.0028 | 1.0015 | 1.0046
TSO | - | 14 | 2020 | Summer | Vang, [º] | Expected | - | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046 | 1.0046
TSO | - | 15 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0197 | 1.0235 | 1.0264 | 1.0272 | 1.0274 | 1.0311 | 1.0182 | 1.012 | 1.0177 | 1.0267 | 1.0208 | 1.0239 | 1.0249 | 1.0254 | 1.0287 | 1.0211 | 1.0259 | 1.0253 | 1.017 | 1.0175 | 1.0149 | 1.0173 | 1.0165 | 1.018
TSO | - | 15 | 2020 | Summer | Vang, [º] | Expected | - | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018 | 1.018
TSO | - | 16 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98266 | 0.98375 | 0.98745 | 0.9879 | 0.98821 | 0.99162 | 0.98282 | 0.9787 | 1.016 | 1.0355 | 1.013 | 1.0397 | 1.0419 | 1.0416 | 1.0367 | 1.0292 | 1.0364 | 1.0368 | 0.98596 | 0.98495 | 0.98516 | 0.98465 | 0.98159 | 0.9801
TSO | - | 16 | 2020 | Summer | Vang, [º] | Expected | - | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801 | 0.9801
TSO | - | 17 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0133 | 1.014 | 1.0165 | 1.0167 | 1.0169 | 1.0186 | 1.0106 | 1.007 | 1.026 | 1.0376 | 1.0262 | 1.0391 | 1.039 | 1.0397 | 1.0372 | 1.0348 | 1.0376 | 1.0368 | 1.0103 | 1.0123 | 1.0109 | 1.0112 | 1.012 | 1.0114
TSO | - | 17 | 2020 | Summer | Vang, [º] | Expected | - | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114 | 1.0114
TSO | - | 18 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0329 | 1.0424 | 1.0469 | 1.0431 | 1.0429 | 1.0438 | 1.0182 | 0.9993 | 0.993 | 0.99848 | 1.0052 | 0.9861 | 0.98668 | 0.99412 | 1.0044 | 0.99799 | 1.0098 | 1.0096 | 1.0147 | 1.0132 | 1.0091 | 1.0168 | 1.0198 | 1.0244
TSO | - | 18 | 2020 | Summer | Vang, [º] | Expected | - | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244 | 1.0244
TSO | - | 19 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0136 | 1.0205 | 1.0259 | 1.0314 | 1.029 | 1.0314 | 1.0066 | 0.9864 | 0.98486 | 0.99696 | 0.99907 | 0.98755 | 0.98871 | 0.98683 | 0.98981 | 0.98614 | 0.99419 | 0.9949 | 0.99781 | 0.99694 | 0.99334 | 0.99946 | 1.0077 | 1.0139
TSO | - | 19 | 2020 | Summer | Vang, [º] | Expected | - | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139 | 1.0139
TSO | - | 20 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0097 | 1.0147 | 1.0215 | 1.0271 | 1.025 | 1.0322 | 1.0081 | 0.98341 | 0.98176 | 0.98884 | 0.98807 | 0.98302 | 0.98472 | 0.98031 | 0.98621 | 0.98449 | 0.98722 | 0.98851 | 0.99111 | 0.99059 | 0.98757 | 0.99266 | 0.9978 | 1.0083
TSO | - | 20 | 2020 | Summer | Vang, [º] | Expected | - | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
TSO | - | 21 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.003 | 1.0055 | 1.0132 | 1.0199 | 1.0189 | 1.0261 | 1.0042 | 0.98327 | 0.98786 | 0.99518 | 0.9894 | 0.99352 | 0.9943 | 0.99288 | 0.99526 | 0.9917 | 0.99394 | 0.99416 | 0.98686 | 0.98833 | 0.98686 | 0.98871 | 0.99288 | 1.0026
TSO | - | 21 | 2020 | Summer | Vang, [º] | Expected | - | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 1.0026
TSO | - | 22 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0027 | 1.0045 | 1.0124 | 1.019 | 1.0183 | 1.0264 | 1.0052 | 0.98411 | 0.98936 | 0.99533 | 0.9885 | 0.99527 | 0.99534 | 0.994 | 0.99693 | 0.99316 | 0.99442 | 0.99443 | 0.98673 | 0.98842 | 0.98714 | 0.98856 | 0.99125 | 1.0014
TSO | - | 22 | 2020 | Summer | Vang, [º] | Expected | - | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014 | 1.0014
TSO | - | 23 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0022 | 1.0037 | 1.0119 | 1.0187 | 1.018 | 1.0262 | 1.0047 | 0.98399 | 0.98885 | 0.99416 | 0.98779 | 0.9943 | 0.99426 | 0.99288 | 0.99562 | 0.99201 | 0.99337 | 0.9934 | 0.98623 | 0.98796 | 0.98655 | 0.98789 | 0.99051 | 1.0004
TSO | - | 23 | 2020 | Summer | Vang, [º] | Expected | - | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 1.0004
TSO | - | 24 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99048 | 0.98482 | 0.99575 | 1.0048 | 1.0051 | 1.0125 | 0.99072 | 0.97922 | 0.97833 | 0.97811 | 0.97988 | 0.98186 | 0.98296 | 0.98283 | 0.98229 | 0.97959 | 0.98199 | 0.98154 | 0.98078 | 0.98356 | 0.98177 | 0.9827 | 0.98427 | 0.99001
TSO | - | 24 | 2020 | Summer | Vang, [º] | Expected | - | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001 | 0.99001
TSO | - | 25 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97876 | 0.95903 | 0.97908 | 0.99584 | 0.99597 | 1.0043 | 0.9799 | 0.96388 | 0.96304 | 0.95237 | 0.96334 | 0.96266 | 0.96508 | 0.96326 | 0.95697 | 0.96211 | 0.96391 | 0.96399 | 0.96509 | 0.96657 | 0.96528 | 0.9654 | 0.97011 | 0.97671
TSO | - | 25 | 2020 | Summer | Vang, [º] | Expected | - | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671 | 0.97671
TSO | - | 26 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98946 | 0.98423 | 0.99496 | 1.0035 | 1.0038 | 1.011 | 0.98934 | 0.97875 | 0.97731 | 0.97732 | 0.97908 | 0.98082 | 0.98177 | 0.98165 | 0.98146 | 0.97818 | 0.98073 | 0.98018 | 0.98089 | 0.9834 | 0.98136 | 0.9825 | 0.98352 | 0.98871
TSO | - | 26 | 2020 | Summer | Vang, [º] | Expected | - | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871 | 0.98871
TSO | - | 27 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98865 | 0.99123 | 0.99703 | 0.9998 | 1.0011 | 1.0061 | 0.98426 | 0.98424 | 0.97715 | 0.97962 | 0.98142 | 0.97957 | 0.98056 | 0.9823 | 0.98331 | 0.97657 | 0.98103 | 0.97988 | 0.98788 | 0.99123 | 0.98826 | 0.98829 | 0.98772 | 0.98723
TSO | - | 27 | 2020 | Summer | Vang, [º] | Expected | - | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723 | 0.98723
TSO | - | 28 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99205 | 0.99759 | 1.001 | 1.0018 | 1.003 | 1.0077 | 0.98718 | 0.99243 | 0.98312 | 0.98671 | 0.9881 | 0.98538 | 0.98624 | 0.98883 | 0.98949 | 0.98129 | 0.98654 | 0.98506 | 0.99563 | 0.99958 | 0.99611 | 0.99564 | 0.99388 | 0.99101
TSO | - | 28 | 2020 | Summer | Vang, [º] | Expected | - | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101 | 0.99101
TSO | - | 29 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.9958 | 1.0031 | 1.0047 | 1.0042 | 1.0055 | 1.0094 | 0.99035 | 0.99986 | 0.98935 | 0.9944 | 0.99557 | 0.99269 | 0.99356 | 0.99664 | 0.99654 | 0.98732 | 0.99291 | 0.99139 | 1.0031 | 1.0075 | 1.0036 | 1.0031 | 1.0004 | 0.99557
TSO | - | 29 | 2020 | Summer | Vang, [º] | Expected | - | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557 | 0.99557
TSO | - | 30 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97107 | 0.95391 | 0.97213 | 0.98852 | 0.9883 | 0.99823 | 0.97348 | 0.9568 | 0.95615 | 0.94744 | 0.95595 | 0.95639 | 0.9578 | 0.95632 | 0.95081 | 0.9549 | 0.95558 | 0.95562 | 0.95607 | 0.95701 | 0.95646 | 0.95738 | 0.96167 | 0.96918
TSO | - | 30 | 2020 | Summer | Vang, [º] | Expected | - | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918 | 0.96918
TSO | - | 31 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.96153 | 0.95083 | 0.96469 | 0.9801 | 0.97899 | 0.99264 | 0.96699 | 0.94845 | 0.94812 | 0.94387 | 0.94643 | 0.94946 | 0.94847 | 0.94779 | 0.94435 | 0.94607 | 0.94406 | 0.94393 | 0.9429 | 0.9425 | 0.94387 | 0.94661 | 0.94988 | 0.95953
TSO | - | 31 | 2020 | Summer | Vang, [º] | Expected | - | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953 | 0.95953
TSO | - | 32 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98077 | 0.9814 | 0.99329 | 1.0032 | 1.0013 | 1.0147 | 0.98312 | 0.95312 | 0.95042 | 0.951 | 0.94698 | 0.94959 | 0.94556 | 0.94499 | 0.94842 | 0.95276 | 0.95165 | 0.95323 | 0.95286 | 0.95095 | 0.95222 | 0.95149 | 0.95833 | 0.97348
TSO | - | 32 | 2020 | Summer | Vang, [º] | Expected | - | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348 | 0.97348
TSO | - | 33 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98034 | 0.98118 | 0.99319 | 1.0032 | 1.0013 | 1.0147 | 0.98273 | 0.95235 | 0.94925 | 0.94972 | 0.94561 | 0.94811 | 0.94384 | 0.94333 | 0.94679 | 0.95142 | 0.95035 | 0.95199 | 0.95182 | 0.94985 | 0.9511 | 0.95027 | 0.95728 | 0.97283
TSO | - | 33 | 2020 | Summer | Vang, [º] | Expected | - | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283 | 0.97283
TSO | - | 34 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98786 | 0.98887 | 0.99804 | 1.0059 | 1.0052 | 1.0146 | 0.98701 | 0.96084 | 0.96306 | 0.96918 | 0.96335 | 0.96813 | 0.9675 | 0.96755 | 0.97219 | 0.97144 | 0.97218 | 0.97319 | 0.9646 | 0.96528 | 0.96603 | 0.96536 | 0.97134 | 0.98633
TSO | - | 34 | 2020 | Summer | Vang, [º] | Expected | - | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633 | 0.98633
TSO | - | 35 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99025 | 0.99216 | 1.0009 | 1.0081 | 1.0073 | 1.0163 | 0.98888 | 0.96262 | 0.9654 | 0.97225 | 0.96586 | 0.97085 | 0.97038 | 0.97036 | 0.97549 | 0.97428 | 0.9752 | 0.97621 | 0.96733 | 0.96812 | 0.96867 | 0.96796 | 0.97387 | 0.98855
TSO | - | 35 | 2020 | Summer | Vang, [º] | Expected | - | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855 | 0.98855
TSO | - | 36 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99356 | 0.99607 | 1.0043 | 1.0111 | 1.0102 | 1.0188 | 0.99297 | 0.96762 | 0.97113 | 0.97817 | 0.97131 | 0.97703 | 0.97653 | 0.97625 | 0.98119 | 0.97936 | 0.98038 | 0.98108 | 0.97212 | 0.97303 | 0.97327 | 0.97303 | 0.97825 | 0.99201
TSO | - | 36 | 2020 | Summer | Vang, [º] | Expected | - | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201
TSO | - | 37 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99624 | 0.99884 | 1.0069 | 1.0134 | 1.0126 | 1.0211 | 0.99645 | 0.97189 | 0.97602 | 0.98306 | 0.97586 | 0.98214 | 0.98169 | 0.98117 | 0.98581 | 0.98345 | 0.98448 | 0.98498 | 0.97606 | 0.97713 | 0.97705 | 0.97723 | 0.9818 | 0.99482
TSO | - | 37 | 2020 | Summer | Vang, [º] | Expected | - | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482 | 0.99482
TSO | - | 38 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0036 | 1.0056 | 1.0132 | 1.0194 | 1.0187 | 1.0269 | 1.0064 | 0.98455 | 0.99075 | 0.99762 | 0.98963 | 0.99759 | 0.99769 | 0.99644 | 0.99989 | 0.99576 | 0.99658 | 0.99651 | 0.98768 | 0.98935 | 0.98834 | 0.98982 | 0.99225 | 1.0029
TSO | - | 38 | 2020 | Summer | Vang, [º] | Expected | - | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029 | 1.0029
TSO | - | 39 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99574 | 0.99858 | 1.0066 | 1.0131 | 1.0122 | 1.0206 | 0.99572 | 0.97095 | 0.9749 | 0.982 | 0.97481 | 0.98099 | 0.98041 | 0.97996 | 0.98472 | 0.98251 | 0.98362 | 0.98413 | 0.97518 | 0.97617 | 0.97615 | 0.97624 | 0.98098 | 0.9942
TSO | - | 39 | 2020 | Summer | Vang, [º] | Expected | - | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942 | 0.9942
TSO | - | 40 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99313 | 0.996 | 1.0042 | 1.0108 | 1.0098 | 1.0184 | 0.99224 | 0.96667 | 0.97004 | 0.97724 | 0.97039 | 0.97604 | 0.97542 | 0.97522 | 0.98035 | 0.97865 | 0.97976 | 0.98046 | 0.97139 | 0.9722 | 0.97254 | 0.9722 | 0.97763 | 0.99151
TSO | - | 40 | 2020 | Summer | Vang, [º] | Expected | - | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151 | 0.99151
TSO | - | 41 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0114 | 1.0184 | 1.0221 | 1.0246 | 1.0227 | 1.0298 | 1.0042 | 0.98588 | 0.99306 | 1.0049 | 0.9967 | 1.0046 | 1.0003 | 1.001 | 1.0046 | 1.0027 | 1.0072 | 1.0069 | 0.99353 | 0.9972 | 0.99543 | 0.99585 | 1.0008 | 1.0058
TSO | - | 41 | 2020 | Summer | Vang, [º] | Expected | - | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058 | 1.0058
TSO | - | 42 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0049 | 1.013 | 1.0199 | 1.0218 | 1.0197 | 1.0271 | 0.99431 | 0.96254 | 0.96781 | 0.97689 | 0.97162 | 0.97465 | 0.96936 | 0.97038 | 0.97823 | 0.97978 | 0.98564 | 0.98635 | 0.97457 | 0.97514 | 0.97473 | 0.97518 | 0.98267 | 0.99464
TSO | - | 42 | 2020 | Summer | Vang, [º] | Expected | - | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464 | 0.99464
TSO | - | 43 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99805 | 1.0044 | 1.0068 | 1.0089 | 1.0071 | 1.0133 | 0.99452 | 0.98868 | 0.99883 | 1.0119 | 1.001 | 1.0134 | 1.0116 | 1.0112 | 1.0119 | 1.0051 | 1.0104 | 1.0103 | 0.99428 | 0.99678 | 0.9946 | 0.9946 | 0.99508 | 0.99595
TSO | - | 43 | 2020 | Summer | Vang, [º] | Expected | - | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595 | 0.99595
TSO | - | 44 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0072 | 1.01 | 1.0166 | 1.0216 | 1.021 | 1.0285 | 1.0092 | 0.98961 | 0.99536 | 1.0029 | 0.99544 | 1.0015 | 1.0029 | 1.0016 | 1.0052 | 1.0008 | 1.0021 | 1.0022 | 0.99337 | 0.99473 | 0.99346 | 0.99533 | 0.99777 | 1.0069
TSO | - | 44 | 2020 | Summer | Vang, [º] | Expected | - | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 1.0069
TSO | - | 45 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0191 | 1.0227 | 1.0269 | 1.029 | 1.0291 | 1.0342 | 1.0189 | 1.0065 | 1.0128 | 1.022 | 1.0153 | 1.0196 | 1.0209 | 1.0219 | 1.0252 | 1.0188 | 1.0221 | 1.0218 | 1.0118 | 1.0128 | 1.0111 | 1.0139 | 1.0144 | 1.0186
TSO | - | 45 | 2020 | Summer | Vang, [º] | Expected | - | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186 | 1.0186
TSO | - | 46 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0098 | 1.0137 | 1.0188 | 1.0227 | 1.0222 | 1.0294 | 1.0123 | 0.99705 | 1.0073 | 1.0164 | 1.0058 | 1.0169 | 1.017 | 1.0166 | 1.0191 | 1.0127 | 1.0159 | 1.0159 | 1.0011 | 1.0021 | 1.0008 | 1.0025 | 1.002 | 1.0073
TSO | - | 46 | 2020 | Summer | Vang, [º] | Expected | - | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073 | 1.0073
TSO | - | 47 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0096 | 1.0135 | 1.0205 | 1.0266 | 1.0255 | 1.0344 | 1.0137 | 0.99276 | 1.0008 | 1.0063 | 0.99655 | 1.007 | 1.0062 | 1.005 | 1.0082 | 1.0038 | 1.0062 | 1.0065 | 0.99424 | 0.9955 | 0.99413 | 0.99549 | 0.9961 | 1.0037
TSO | - | 47 | 2020 | Summer | Vang, [º] | Expected | - | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 1.0037
TSO | - | 48 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0067 | 1.0092 | 1.0167 | 1.023 | 1.0222 | 1.0307 | 1.0103 | 0.98905 | 0.99675 | 1.003 | 0.99396 | 1.0039 | 1.0038 | 1.0027 | 1.0061 | 1.0016 | 1.0036 | 1.0036 | 0.99159 | 0.99315 | 0.99207 | 0.99353 | 0.99471 | 1.0032
TSO | - | 48 | 2020 | Summer | Vang, [º] | Expected | - | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 1.0032
TSO | - | 49 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0018 | 0.99885 | 1.0084 | 1.0156 | 1.0154 | 1.023 | 1.0044 | 0.98337 | 0.9934 | 1.0024 | 0.99341 | 1.0056 | 1.0079 | 1.0069 | 1.0113 | 1.0058 | 1.0085 | 1.0074 | 0.98911 | 0.99164 | 0.99135 | 0.99316 | 0.99379 | 1.0003
TSO | - | 49 | 2020 | Summer | Vang, [º] | Expected | - | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 1.0003
TSO | - | 50 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.99265 | 0.99575 | 1.0036 | 1.0075 | 1.0074 | 1.0157 | 0.99432 | 0.96458 | 0.97424 | 0.99233 | 0.97523 | 0.99029 | 0.993 | 0.99246 | 1.0067 | 0.99636 | 0.99925 | 0.99511 | 0.96973 | 0.97539 | 0.9757 | 0.97848 | 0.97955 | 0.98645
TSO | - | 50 | 2020 | Summer | Vang, [º] | Expected | - | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645 | 0.98645
TSO | - | 51 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98802 | 0.99239 | 0.99665 | 0.99841 | 0.99817 | 1.0029 | 0.985 | 0.97058 | 0.99425 | 1.0154 | 0.9948 | 1.0168 | 1.0191 | 1.0189 | 1.0277 | 1.0141 | 1.0195 | 1.0186 | 0.98293 | 0.98454 | 0.98497 | 0.98631 | 0.98361 | 0.9857
TSO | - | 51 | 2020 | Summer | Vang, [º] | Expected | - | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857 | 0.9857
TSO | - | 52 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97984 | 0.99269 | 0.99238 | 0.99496 | 0.99651 | 1.0043 | 0.97733 | 0.97137 | 0.96024 | 0.9635 | 0.962 | 0.95661 | 0.95831 | 0.96037 | 0.96274 | 0.95851 | 0.96529 | 0.96297 | 0.97324 | 0.97739 | 0.97387 | 0.96724 | 0.96284 | 0.96752
TSO | - | 52 | 2020 | Summer | Vang, [º] | Expected | - | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752 | 0.96752
TSO | - | 53 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97393 | 0.98926 | 0.98759 | 0.99177 | 0.99353 | 1.0027 | 0.97245 | 0.95979 | 0.9488 | 0.95238 | 0.94961 | 0.94361 | 0.94584 | 0.94724 | 0.95001 | 0.94825 | 0.95536 | 0.9529 | 0.96167 | 0.9657 | 0.96216 | 0.95293 | 0.94739 | 0.95617
TSO | - | 53 | 2020 | Summer | Vang, [º] | Expected | - | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617 | 0.95617
TSO | - | 54 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97892 | 0.99156 | 0.98874 | 0.9927 | 0.9915 | 0.99903 | 0.97744 | 0.97459 | 0.97011 | 0.97722 | 0.97149 | 0.97421 | 0.97454 | 0.97524 | 0.97577 | 0.97035 | 0.97627 | 0.97469 | 0.97713 | 0.9809 | 0.97782 | 0.97276 | 0.96834 | 0.97064
TSO | - | 54 | 2020 | Summer | Vang, [º] | Expected | - | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064 | 0.97064
TSO | - | 55 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.98674 | 0.99682 | 0.99308 | 0.99672 | 0.99287 | 0.99876 | 0.98522 | 0.99163 | 0.99331 | 1.0037 | 0.99515 | 1.0061 | 1.0047 | 1.0047 | 1.0031 | 0.9943 | 0.99907 | 0.99833 | 0.99473 | 0.99821 | 0.99563 | 0.99455 | 0.99121 | 0.98732
TSO | - | 55 | 2020 | Summer | Vang, [º] | Expected | - | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732 | 0.98732
TSO | - | 56 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0014 | 1.0077 | 1.016 | 1.0194 | 1.018 | 1.0269 | 0.9954 | 0.96484 | 0.96879 | 0.97677 | 0.97019 | 0.97439 | 0.96926 | 0.96966 | 0.97645 | 0.97822 | 0.98225 | 0.98315 | 0.97229 | 0.97236 | 0.97272 | 0.97197 | 0.97923 | 0.99272
TSO | - | 56 | 2020 | Summer | Vang, [º] | Expected | - | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272 | 0.99272
TSO | - | 57 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0015 | 1.0077 | 1.0169 | 1.0211 | 1.0199 | 1.03 | 0.99726 | 0.96538 | 0.96738 | 0.97425 | 0.96693 | 0.97095 | 0.96477 | 0.96512 | 0.97143 | 0.97445 | 0.9782 | 0.9795 | 0.97031 | 0.97042 | 0.97029 | 0.96931 | 0.97669 | 0.99201
TSO | - | 57 | 2020 | Summer | Vang, [º] | Expected | - | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201 | 0.99201
DSO | 2 | 1 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97489 | 0.981 | 0.97842 | 0.97707 | 0.9764 | 0.97884 | 0.97509 | 0.96797 | 0.95503 | 0.95349 | 0.94084 | 0.9328 | 0.9351 | 0.93663 | 0.95333 | 0.9499 | 0.95964 | 0.96069 | 0.96149 | 0.97518 | 0.97676 | 0.97899 | 0.97692 | 0.96963
DSO | 2 | 1 | 2020 | Summer | Vang, [º] | 0 | 0 | -2.8786 | -2.6517 | -2.3811 | -2.4572 | -2.4288 | -2.4597 | -3.08 | -3.711 | -3.4167 | -1.2157 | 0.33638 | 0.91711 | 0.56832 | 0.97003 | -0.26025 | -1.1499 | -2.4291 | -3.6998 | -3.6836 | -3.7503 | -4.0444 | -4.0321 | -3.6256 | -3.153
DSO | 2 | 2 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.96972 | 0.97638 | 0.97461 | 0.97331 | 0.97256 | 0.97497 | 0.96987 | 0.96068 | 0.94693 | 0.94593 | 0.93449 | 0.92594 | 0.92815 | 0.93 | 0.94667 | 0.94298 | 0.95238 | 0.95304 | 0.95408 | 0.96746 | 0.96832 | 0.97059 | 0.96965 | 0.96355
DSO | 2 | 2 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.1201 | -2.8622 | -2.5837 | -2.6631 | -2.6355 | -2.6682 | -3.36 | -4.0458 | -3.7377 | -1.3988 | 0.26621 | 0.87339 | 0.51733 | 0.94133 | -0.38501 | -1.3225 | -2.6668 | -4.013 | -3.9903 | -4.0632 | -4.3907 | -4.3849 | -3.9382 | -3.4076
DSO | 2 | 3 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.96242 | 0.96981 | 0.96911 | 0.96792 | 0.96706 | 0.96944 | 0.96236 | 0.95044 | 0.93549 | 0.93529 | 0.92548 | 0.91631 | 0.91837 | 0.92067 | 0.93716 | 0.93312 | 0.94197 | 0.94206 | 0.94348 | 0.95633 | 0.9563 | 0.95888 | 0.95956 | 0.95504
DSO | 2 | 3 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.433 | -3.1374 | -2.8538 | -2.936 | -2.9127 | -2.9462 | -3.7325 | -4.4963 | -4.1943 | -1.6723 | 0.15786 | 0.8145 | 0.44366 | 0.89798 | -0.55944 | -1.5708 | -3.0176 | -4.4768 | -4.4441 | -4.5326 | -4.8946 | -4.8746 | -4.353 | -3.7448
DSO | 2 | 4 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.95889 | 0.96664 | 0.96645 | 0.96535 | 0.96444 | 0.9668 | 0.95873 | 0.9454 | 0.92983 | 0.93002 | 0.92106 | 0.9116 | 0.91357 | 0.91611 | 0.9325 | 0.92829 | 0.93685 | 0.9366 | 0.93828 | 0.95087 | 0.95034 | 0.9531 | 0.9546 | 0.95087
DSO | 2 | 4 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.5851 | -3.2703 | -2.9863 | -3.0683 | -3.0471 | -3.0814 | -3.9166 | -4.7216 | -4.4226 | -1.8032 | 0.11547 | 0.80049 | 0.42105 | 0.89167 | -0.63643 | -1.6868 | -3.1891 | -4.7109 | -4.6693 | -4.7664 | -5.1489 | -5.1205 | -4.5589 | -3.9106
DSO | 2 | 5 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.951 | 0.95969 | 0.95987 | 0.95888 | 0.95782 | 0.96012 | 0.94956 | 0.93402 | 0.91731 | 0.9185 | 0.91165 | 0.90127 | 0.90303 | 0.90616 | 0.92252 | 0.91792 | 0.92584 | 0.92492 | 0.92737 | 0.93916 | 0.93722 | 0.94046 | 0.94413 | 0.94245
DSO | 2 | 5 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.9283 | -3.5709 | -3.2696 | -3.3479 | -3.3328 | -3.3697 | -4.3219 | -5.2352 | -4.9306 | -2.0801 | 0.040381 | 0.78755 | 0.39017 | 0.89462 | -0.78427 | -1.9334 | -3.5643 | -5.2214 | -5.1516 | -5.2784 | -5.7218 | -5.6702 | -5.0191 | -4.2826
DSO | 2 | 6 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.94998 | 0.95878 | 0.95896 | 0.95798 | 0.95691 | 0.95921 | 0.94861 | 0.93278 | 0.91597 | 0.91752 | 0.91089 | 0.90075 | 0.90248 | 0.90572 | 0.92188 | 0.91706 | 0.92477 | 0.9236 | 0.92605 | 0.93773 | 0.93554 | 0.93873 | 0.94263 | 0.94131
DSO | 2 | 6 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.9785 | -3.6152 | -3.313 | -3.3913 | -3.3767 | -3.4133 | -4.3699 | -5.2986 | -4.9819 | -2.0595 | 0.10803 | 0.89236 | 0.48593 | 0.99996 | -0.7279 | -1.9115 | -3.5848 | -5.2858 | -5.2176 | -5.3489 | -5.8045 | -5.755 | -5.0927 | -4.339
DSO | 2 | 7 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.94718 | 0.95631 | 0.9566 | 0.95559 | 0.95453 | 0.9568 | 0.94596 | 0.9297 | 0.913 | 0.91596 | 0.91018 | 0.9008 | 0.90227 | 0.90588 | 0.92121 | 0.9158 | 0.92263 | 0.92048 | 0.92285 | 0.93436 | 0.93169 | 0.9348 | 0.93909 | 0.93835
DSO | 2 | 7 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.0399 | -3.6689 | -3.364 | -3.443 | -3.4281 | -3.4657 | -4.4308 | -5.3705 | -5.0223 | -1.9743 | 0.27276 | 1.1178 | 0.69469 | 1.222 | -0.59196 | -1.8286 | -3.5765 | -5.3526 | -5.2896 | -5.4237 | -5.8894 | -5.8409 | -5.1709 | -4.405
DSO | 2 | 8 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.94236 | 0.95202 | 0.9525 | 0.95143 | 0.95041 | 0.95259 | 0.94143 | 0.92475 | 0.90864 | 0.91507 | 0.91129 | 0.90372 | 0.90462 | 0.909 | 0.92214 | 0.91508 | 0.91976 | 0.9153 | 0.91747 | 0.92887 | 0.92539 | 0.92833 | 0.93315 | 0.93344
DSO | 2 | 8 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.0703 | -3.6958 | -3.3886 | -3.4682 | -3.4531 | -3.4916 | -4.464 | -5.4076 | -5.0019 | -1.7675 | 0.59821 | 1.53 | 1.0841 | 1.6246 | -0.3203 | -1.6366 | -3.4948 | -5.3797 | -5.3239 | -5.4585 | -5.9282 | -5.8797 | -5.2082 | -4.4368
DSO | 2 | 9 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.97021 | 0.97692 | 0.97521 | 0.97391 | 0.97317 | 0.97555 | 0.97062 | 0.96124 | 0.94778 | 0.94675 | 0.93534 | 0.92663 | 0.9289 | 0.93074 | 0.94758 | 0.94396 | 0.95353 | 0.95425 | 0.95534 | 0.9689 | 0.96944 | 0.97118 | 0.96999 | 0.96398
DSO | 2 | 9 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.1522 | -2.8866 | -2.602 | -2.6823 | -2.6492 | -2.6846 | -3.3893 | -4.0724 | -3.7289 | -1.369 | 0.28828 | 0.88199 | 0.53094 | 0.95753 | -0.38136 | -1.3099 | -2.6419 | -3.9838 | -3.9578 | -4.0235 | -4.3698 | -4.3903 | -3.967 | -3.4309
DSO | 2 | 20 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.96582 | 0.97269 | 0.97141 | 0.9684 | 0.96885 | 0.97271 | 0.96779 | 0.95826 | 0.94668 | 0.95459 | 0.94824 | 0.94271 | 0.94308 | 0.94628 | 0.95962 | 0.95178 | 0.95534 | 0.94998 | 0.95028 | 0.96223 | 0.96267 | 0.96564 | 0.9657 | 0.95959
DSO | 2 | 20 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.506 | -3.2935 | -2.9379 | -3.0013 | -2.9828 | -3.0847 | -3.7704 | -4.46 | -3.9725 | -0.93001 | 1.0935 | 1.9913 | 1.4668 | 2.0168 | 0.2952 | -0.9343 | -2.7352 | -4.4673 | -4.4623 | -4.4854 | -4.7969 | -4.7791 | -4.3518 | -3.8519
DSO | 2 | 21 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.95917 | 0.96652 | 0.9662 | 0.96191 | 0.9633 | 0.96829 | 0.96199 | 0.95113 | 0.94109 | 0.95684 | 0.95544 | 0.95204 | 0.9509 | 0.95522 | 0.96509 | 0.95383 | 0.9526 | 0.94239 | 0.9423 | 0.95283 | 0.95281 | 0.95672 | 0.95811 | 0.95253
DSO | 2 | 21 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.7922 | -3.6089 | -3.1923 | -3.2442 | -3.2379 | -3.3925 | -4.1004 | -4.8425 | -4.1919 | -0.51742 | 1.8857 | 3.0271 | 2.3761 | 3.0109 | 0.92908 | -0.56032 | -2.7606 | -4.8537 | -4.8552 | -4.8394 | -5.1491 | -5.1357 | -4.7016 | -4.2049
DSO | 2 | 22 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.95821 | 0.96562 | 0.96533 | 0.96104 | 0.96242 | 0.96748 | 0.96108 | 0.94986 | 0.94115 | 0.96086 | 0.96195 | 0.96012 | 0.95825 | 0.96305 | 0.97038 | 0.95737 | 0.95398 | 0.94123 | 0.94099 | 0.95155 | 0.95155 | 0.95545 | 0.95691 | 0.95143
DSO | 2 | 22 | 2020 | Summer | Vang, [º] | 0 | 0 | -3.8181 | -3.6298 | -3.2108 | -3.2627 | -3.2572 | -3.4159 | -4.1331 | -4.878 | -4.1133 | -0.12304 | 2.4785 | 3.7555 | 3.0476 | 3.7197 | 1.4279 | -0.19215 | -2.5819 | -4.8809 | -4.8948 | -4.8787 | -5.1882 | -5.1747 | -4.7378 | -4.2335
DSO | 2 | 23 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.94958 | 0.95753 | 0.95884 | 0.95218 | 0.95532 | 0.96224 | 0.95375 | 0.94126 | 0.93313 | 0.95972 | 0.96542 | 0.96491 | 0.96153 | 0.96758 | 0.9728 | 0.95662 | 0.9485 | 0.9318 | 0.9312 | 0.93912 | 0.93832 | 0.94398 | 0.94749 | 0.94259
DSO | 2 | 23 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.2614 | -4.1382 | -3.614 | -3.6476 | -3.6646 | -3.9067 | -4.6396 | -5.4713 | -4.6115 | -0.066275 | 2.8329 | 4.291 | 3.4717 | 4.2189 | 1.684 | -0.15291 | -2.9065 | -5.487 | -5.4888 | -5.401 | -5.7062 | -5.7014 | -5.2583 | -4.7839
DSO | 2 | 24 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.94732 | 0.95535 | 0.95689 | 0.95012 | 0.95326 | 0.9602 | 0.9516 | 0.93877 | 0.93136 | 0.96072 | 0.96797 | 0.96835 | 0.9645 | 0.97089 | 0.97469 | 0.95735 | 0.94768 | 0.92951 | 0.92862 | 0.93656 | 0.93588 | 0.94151 | 0.94517 | 0.94042
DSO | 2 | 24 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.3089 | -4.1867 | -3.6677 | -3.6948 | -3.7102 | -3.954 | -4.6818 | -5.5304 | -4.6105 | 0.14007 | 3.1551 | 4.6952 | 3.8378 | 4.6103 | 1.961 | 0.042976 | -2.8317 | -5.5434 | -5.5376 | -5.4463 | -5.7571 | -5.7479 | -5.2994 | -4.8287
DSO | 2 | 25 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.9473 | 0.95658 | 0.95696 | 0.94986 | 0.95402 | 0.96247 | 0.95327 | 0.93967 | 0.93315 | 0.96625 | 0.97613 | 0.97764 | 0.97299 | 0.98011 | 0.9826 | 0.96362 | 0.9514 | 0.93032 | 0.929 | 0.93505 | 0.93344 | 0.94042 | 0.9455 | 0.94147
DSO | 2 | 25 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.548 | -4.4606 | -3.8762 | -3.8664 | -3.9199 | -4.2456 | -4.9843 | -5.8794 | -4.8801 | 0.18056 | 3.3613 | 5.0029 | 4.0965 | 4.9032 | 2.1078 | 0.072009 | -3.0042 | -5.8788 | -5.9021 | -5.7423 | -6.0341 | -6.0498 | -5.6096 | -5.1413
DSO | 2 | 26 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 0.9472 | 0.95648 | 0.95702 | 0.94974 | 0.9539 | 0.96234 | 0.95315 | 0.93956 | 0.93375 | 0.96874 | 0.9798 | 0.98211 | 0.97709 | 0.98447 | 0.98582 | 0.96593 | 0.95259 | 0.93027 | 0.92886 | 0.93486 | 0.93326 | 0.94025 | 0.94532 | 0.94128
DSO | 2 | 26 | 2020 | Summer | Vang, [º] | 0 | 0 | -4.5594 | -4.4709 | -3.8929 | -3.8755 | -3.9287 | -4.2538 | -4.9995 | -5.9013 | -4.8502 | 0.35399 | 3.6181 | 5.316 | 4.3874 | 5.2095 | 2.3234 | 0.23627 | -2.9217 | -5.889 | -5.9183 | -5.7584 | -6.0515 | -6.0652 | -5.6217 | -5.1496
DSO | 2 | 50 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.041 | 1.048 | 1.0473 | 1.0447 | 1.0452 | 1.0484 | 1.0415 | 1.0306 | 1.0199 | 1.0281 | 1.0223 | 1.0157 | 1.0167 | 1.0196 | 1.0321 | 1.0259 | 1.0293 | 1.0232 | 1.0239 | 1.0341 | 1.0332 | 1.0367 | 1.0386 | 1.0348
DSO | 2 | 50 | 2020 | Summer | Vang, [º] | 0 | 0 | -0.097362 | -0.085896 | -0.071271 | -0.075967 | -0.073634 | -0.073621 | -0.10452 | -0.13935 | -0.12634 | -0.023391 | 0.048451 | 0.07307 | 0.057528 | 0.075381 | 0.021611 | -0.018168 | -0.078095 | -0.14011 | -0.13921 | -0.14718 | -0.16416 | -0.16212 | -0.13766 | -0.1116
DSO | 2 | 51 | 2020 | Summer | Vmag, [p.u.] | 0 | 0 | 1.0467 | 1.054 | 1.0537 | 1.0509 | 1.0514 | 1.0549 | 1.0475 | 1.0357 | 1.025 | 1.0338 | 1.0288 | 1.0221 | 1.023 | 1.026 | 1.0385 | 1.0319 | 1.0349 | 1.0281 | 1.0289 | 1.0385 | 1.0373 | 1.0409 | 1.0435 | 1.0402
DSO | 2 | 51 | 2020 | Summer | Vang, [º] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97489 | 0.981 | 0.97842 | 0.97707 | 0.9764 | 0.97884 | 0.97509 | 0.96797 | 0.95503 | 0.95349 | 0.94084 | 0.9328 | 0.9351 | 0.93663 | 0.95333 | 0.9499 | 0.95964 | 0.96069 | 0.96149 | 0.97518 | 0.97676 | 0.97899 | 0.97692 | 0.96963
DSO | 2 | 1 | 2020 | Summer | Vang, [º] | Expected | - | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963 | 0.96963
DSO | 2 | 2 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.96972 | 0.97638 | 0.97461 | 0.97331 | 0.97256 | 0.97497 | 0.96987 | 0.96068 | 0.94693 | 0.94593 | 0.93449 | 0.92594 | 0.92815 | 0.93 | 0.94667 | 0.94298 | 0.95238 | 0.95304 | 0.95408 | 0.96746 | 0.96832 | 0.97059 | 0.96965 | 0.96355
DSO | 2 | 2 | 2020 | Summer | Vang, [º] | Expected | - | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355 | 0.96355
DSO | 2 | 3 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.96242 | 0.96981 | 0.96911 | 0.96792 | 0.96706 | 0.96944 | 0.96236 | 0.95044 | 0.93549 | 0.93529 | 0.92548 | 0.91631 | 0.91837 | 0.92067 | 0.93716 | 0.93312 | 0.94197 | 0.94206 | 0.94348 | 0.95633 | 0.9563 | 0.95888 | 0.95956 | 0.95504
DSO | 2 | 3 | 2020 | Summer | Vang, [º] | Expected | - | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504 | 0.95504
DSO | 2 | 4 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.95889 | 0.96664 | 0.96645 | 0.96535 | 0.96444 | 0.9668 | 0.95873 | 0.9454 | 0.92983 | 0.93002 | 0.92106 | 0.9116 | 0.91357 | 0.91611 | 0.9325 | 0.92829 | 0.93685 | 0.9366 | 0.93828 | 0.95087 | 0.95034 | 0.9531 | 0.9546 | 0.95087
DSO | 2 | 4 | 2020 | Summer | Vang, [º] | Expected | - | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087 | 0.95087
DSO | 2 | 5 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.951 | 0.95969 | 0.95987 | 0.95888 | 0.95782 | 0.96012 | 0.94956 | 0.93402 | 0.91731 | 0.9185 | 0.91165 | 0.90127 | 0.90303 | 0.90616 | 0.92252 | 0.91792 | 0.92584 | 0.92492 | 0.92737 | 0.93916 | 0.93722 | 0.94046 | 0.94413 | 0.94245
DSO | 2 | 5 | 2020 | Summer | Vang, [º] | Expected | - | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245 | 0.94245
DSO | 2 | 6 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.94998 | 0.95878 | 0.95896 | 0.95798 | 0.95691 | 0.95921 | 0.94861 | 0.93278 | 0.91597 | 0.91752 | 0.91089 | 0.90075 | 0.90248 | 0.90572 | 0.92188 | 0.91706 | 0.92477 | 0.9236 | 0.92605 | 0.93773 | 0.93554 | 0.93873 | 0.94263 | 0.94131
DSO | 2 | 6 | 2020 | Summer | Vang, [º] | Expected | - | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131 | 0.94131
DSO | 2 | 7 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.94718 | 0.95631 | 0.9566 | 0.95559 | 0.95453 | 0.9568 | 0.94596 | 0.9297 | 0.913 | 0.91596 | 0.91018 | 0.9008 | 0.90227 | 0.90588 | 0.92121 | 0.9158 | 0.92263 | 0.92048 | 0.92285 | 0.93436 | 0.93169 | 0.9348 | 0.93909 | 0.93835
DSO | 2 | 7 | 2020 | Summer | Vang, [º] | Expected | - | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835 | 0.93835
DSO | 2 | 8 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.94236 | 0.95202 | 0.9525 | 0.95143 | 0.95041 | 0.95259 | 0.94143 | 0.92475 | 0.90864 | 0.91507 | 0.91129 | 0.90372 | 0.90462 | 0.909 | 0.92214 | 0.91508 | 0.91976 | 0.9153 | 0.91747 | 0.92887 | 0.92539 | 0.92833 | 0.93315 | 0.93344
DSO | 2 | 8 | 2020 | Summer | Vang, [º] | Expected | - | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344 | 0.93344
DSO | 2 | 9 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.97021 | 0.97692 | 0.97521 | 0.97391 | 0.97317 | 0.97555 | 0.97062 | 0.96124 | 0.94778 | 0.94675 | 0.93534 | 0.92663 | 0.9289 | 0.93074 | 0.94758 | 0.94396 | 0.95353 | 0.95425 | 0.95534 | 0.9689 | 0.96944 | 0.97118 | 0.96999 | 0.96398
DSO | 2 | 9 | 2020 | Summer | Vang, [º] | Expected | - | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398 | 0.96398
DSO | 2 | 20 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.96582 | 0.97269 | 0.97141 | 0.9684 | 0.96885 | 0.97271 | 0.96779 | 0.95826 | 0.94668 | 0.95459 | 0.94824 | 0.94271 | 0.94308 | 0.94628 | 0.95962 | 0.95178 | 0.95534 | 0.94998 | 0.95028 | 0.96223 | 0.96267 | 0.96564 | 0.9657 | 0.95959
DSO | 2 | 20 | 2020 | Summer | Vang, [º] | Expected | - | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959 | 0.95959
DSO | 2 | 21 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.95917 | 0.96652 | 0.9662 | 0.96191 | 0.9633 | 0.96829 | 0.96199 | 0.95113 | 0.94109 | 0.95684 | 0.95544 | 0.95204 | 0.9509 | 0.95522 | 0.96509 | 0.95383 | 0.9526 | 0.94239 | 0.9423 | 0.95283 | 0.95281 | 0.95672 | 0.95811 | 0.95253
DSO | 2 | 21 | 2020 | Summer | Vang, [º] | Expected | - | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253 | 0.95253
DSO | 2 | 22 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.95821 | 0.96562 | 0.96533 | 0.96104 | 0.96242 | 0.96748 | 0.96108 | 0.94986 | 0.94115 | 0.96086 | 0.96195 | 0.96012 | 0.95825 | 0.96305 | 0.97038 | 0.95737 | 0.95398 | 0.94123 | 0.94099 | 0.95155 | 0.95155 | 0.95545 | 0.95691 | 0.95143
DSO | 2 | 22 | 2020 | Summer | Vang, [º] | Expected | - | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143 | 0.95143
DSO | 2 | 23 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.94958 | 0.95753 | 0.95884 | 0.95218 | 0.95532 | 0.96224 | 0.95375 | 0.94126 | 0.93313 | 0.95972 | 0.96542 | 0.96491 | 0.96153 | 0.96758 | 0.9728 | 0.95662 | 0.9485 | 0.9318 | 0.9312 | 0.93912 | 0.93832 | 0.94398 | 0.94749 | 0.94259
DSO | 2 | 23 | 2020 | Summer | Vang, [º] | Expected | - | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259 | 0.94259
DSO | 2 | 24 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.94732 | 0.95535 | 0.95689 | 0.95012 | 0.95326 | 0.9602 | 0.9516 | 0.93877 | 0.93136 | 0.96072 | 0.96797 | 0.96835 | 0.9645 | 0.97089 | 0.97469 | 0.95735 | 0.94768 | 0.92951 | 0.92862 | 0.93656 | 0.93588 | 0.94151 | 0.94517 | 0.94042
DSO | 2 | 24 | 2020 | Summer | Vang, [º] | Expected | - | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042 | 0.94042
DSO | 2 | 25 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.9473 | 0.95658 | 0.95696 | 0.94986 | 0.95402 | 0.96247 | 0.95327 | 0.93967 | 0.93315 | 0.96625 | 0.97613 | 0.97764 | 0.97299 | 0.98011 | 0.9826 | 0.96362 | 0.9514 | 0.93032 | 0.929 | 0.93505 | 0.93344 | 0.94042 | 0.9455 | 0.94147
DSO | 2 | 25 | 2020 | Summer | Vang, [º] | Expected | - | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147 | 0.94147
DSO | 2 | 26 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 0.9472 | 0.95648 | 0.95702 | 0.94974 | 0.9539 | 0.96234 | 0.95315 | 0.93956 | 0.93375 | 0.96874 | 0.9798 | 0.98211 | 0.97709 | 0.98447 | 0.98582 | 0.96593 | 0.95259 | 0.93027 | 0.92886 | 0.93486 | 0.93326 | 0.94025 | 0.94532 | 0.94128
DSO | 2 | 26 | 2020 | Summer | Vang, [º] | Expected | - | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128 | 0.94128
DSO | 2 | 50 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.041 | 1.048 | 1.0473 | 1.0447 | 1.0452 | 1.0484 | 1.0415 | 1.0306 | 1.0199 | 1.0281 | 1.0223 | 1.0157 | 1.0167 | 1.0196 | 1.0321 | 1.0259 | 1.0293 | 1.0232 | 1.0239 | 1.0341 | 1.0332 | 1.0367 | 1.0386 | 1.0348
DSO | 2 | 50 | 2020 | Summer | Vang, [º] | Expected | - | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348 | 1.0348
DSO | 2 | 51 | 2020 | Summer | Vmag, [p.u.] | Expected | - | 1.0467 | 1.054 | 1.0537 | 1.0509 | 1.0514 | 1.0549 | 1.0475 | 1.0357 | 1.025 | 1.0338 | 1.0288 | 1.0221 | 1.023 | 1.026 | 1.0385 | 1.0319 | 1.0349 | 1.0281 | 1.0289 | 1.0385 | 1.0373 | 1.0409 | 1.0435 | 1.0402
DSO | 2 | 51 | 2020 | Summer | Vang, [º] | Expected | - | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402 | 1.0402

## Consumption
Operator | Connection Node ID | Network Node ID | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
TSO | - | 1 | 2020 | Summer | Pc, [MW] | 0 | 0 | 5.1562 | 55 | 27.5 | 4.2969 | 4.2969 | 5.1562 | 3.4375 | 1.7188 | 3.4375 | 32.6562 | 2.5781 | 6.875 | 3.4375 | 4.2969 | 15.4688 | 4.2969 | 3.4375 | 3.4375 | 10.3125 | 1.7188 | 3.4375 | 1.7188 | 3.4375 | 1.7188
TSO | - | 1 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.24327 | 2.5198 | 1.0569 | 0.17068 | 0.17018 | 0.22172 | 0.25656 | 0.14293 | 0.26351 | 1.9825 | 0.16186 | 0.39623 | 0.27601 | 0.33698 | 0.84646 | 0.21455 | 0.17407 | 0.20062 | 0.53252 | 0.090428 | 0.17159 | 0.077767 | 0.17838 | 0.089173
TSO | - | 1 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.24327 | 2.5198 | 1.0569 | 0.17068 | 0.17018 | 0.22172 | 0.25656 | 0.14293 | 0.26351 | 1.9825 | 0.16186 | 0.39623 | 0.27601 | 0.33698 | 0.84646 | 0.21455 | 0.17407 | 0.20062 | 0.53252 | 0.090428 | 0.17159 | 0.077767 | 0.17838 | 0.089173
TSO | - | 1 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 5.1562 | 55 | 27.5 | 4.2969 | 4.2969 | 5.1562 | 3.4375 | 1.7188 | 3.4375 | 32.6562 | 2.5781 | 6.875 | 3.4375 | 4.2969 | 15.4688 | 4.2969 | 3.4375 | 3.4375 | 10.3125 | 1.7188 | 3.4375 | 1.7188 | 3.4375 | 1.7188
TSO | - | 1 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 2.3182 | 17 | 9.2727 | 2.3182 | 1.1591 | 2.3182 | 2.3182 | 3.8636 | 3.8636 | 12.75 | 2.7045 | 5.7955 | 2.3182 | 3.8636 | 10.4318 | 3.4773 | 2.7045 | 2.3182 | 0 | 1.5455 | 1.5455 | 3.0909 | 0 | 0
TSO | - | 2 | 2020 | Summer | Pc, [MW] | 0 | 0 | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
TSO | - | 2 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 2 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 2 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
TSO | - | 2 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8578 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6312 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
TSO | - | 3 | 2020 | Summer | Pc, [MW] | 0 | 0 | 27.7948 | 27.5818 | 25.3455 | 26.7299 | 24.174 | 26.8364 | 33.226 | 40.4675 | 39.4026 | 41 | 38.2312 | 40.361 | 39.7221 | 40.574 | 39.7221 | 35.5688 | 36.2078 | 35.7818 | 35.8883 | 37.3792 | 36.4208 | 36.5273 | 32.9065 | 31.8416
TSO | - | 3 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 1.341 | 1.2839 | 0.99658 | 1.1035 | 0.9819 | 1.2044 | 2.5641 | 2.9952 | 2.9787 | 2.4638 | 2.3519 | 2.3472 | 3.2303 | 3.1512 | 2.2046 | 1.803 | 1.8296 | 2.0855 | 1.8874 | 1.9828 | 1.8345 | 1.6809 | 1.72 | 1.6742
TSO | - | 3 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 1.2817 | 1.2434 | 0.95164 | 1.0201 | 0.93297 | 1.1035 | 2.3955 | 3.7351 | 3.0622 | 2.5142 | 2.4486 | 2.3051 | 3.1486 | 3.2127 | 2.1426 | 1.7491 | 1.8374 | 2.0911 | 1.819 | 1.9505 | 1.8016 | 1.6245 | 1.6953 | 1.6299
TSO | - | 3 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 27.8541 | 27.6223 | 25.3904 | 26.8132 | 24.223 | 26.9373 | 33.3946 | 39.7276 | 39.319 | 40.9496 | 38.1345 | 40.4031 | 39.8039 | 40.5126 | 39.7841 | 35.6227 | 36.2 | 35.7762 | 35.9568 | 37.4115 | 36.4537 | 36.5837 | 32.9311 | 31.8859
TSO | - | 3 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -14.7 | -14.175 | -19.425 | -19.425 | -21 | -17.325 | -2.1 | 13.125 | 13.65 | 12.075 | 11.025 | 18.375 | 16.275 | 16.8 | -11.025 | 4.725 | 4.2 | 1.575 | -2.625 | 0 | -2.1 | -4.2 | -9.975 | -13.65
TSO | - | 4 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 5 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.3955 | 1.3582 | 1.8433 | 1.5522 | 0.38806 | 0.6791 | 3.5896 | 7.9552 | 9.9925 | 10.6716 | 10.6716 | 12.5149 | 12.0299 | 12.5149 | 11.9328 | 10.3806 | 10.0896 | 9.8955 | 9.6045 | 9.4104 | 10.0896 | 12.3209 | 13 | 9.0224
TSO | - | 5 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.15718 | 0.062034 | 0.069528 | 0.06029 | 0.0153 | 0.028953 | 0.26196 | 0.70574 | 0.77359 | 0.64419 | 0.66697 | 0.71893 | 0.95696 | 0.95959 | 0.64662 | 0.51567 | 0.5001 | 0.56574 | 0.49915 | 0.5133 | 0.52331 | 0.55444 | 0.67038 | 0.46614
TSO | - | 5 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.16321 | 0.062419 | 0.07216 | 0.063028 | 0.015439 | 0.029451 | 0.27385 | 0.61734 | 0.75839 | 0.65152 | 0.67301 | 0.72363 | 0.97489 | 1.0033 | 0.65932 | 0.52097 | 0.52174 | 0.58931 | 0.49276 | 0.47692 | 0.48397 | 0.5605 | 0.67885 | 0.47007
TSO | - | 5 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.3895 | 1.3578 | 1.8407 | 1.5495 | 0.38792 | 0.67861 | 3.5777 | 8.0436 | 10.0077 | 10.6643 | 10.6656 | 12.5102 | 12.0119 | 12.4712 | 11.9201 | 10.3753 | 10.0679 | 9.872 | 9.6109 | 9.4468 | 10.1289 | 12.3148 | 12.9915 | 9.0185
TSO | - | 5 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.5172 | 1.1034 | 1.2414 | 0.68966 | 0.68966 | -0.27586 | 0.96552 | 3.0345 | 3.0345 | 3.1724 | 3.1724 | 4 | 3.7241 | 3.5862 | 3.3103 | 2.4828 | 2.3448 | 2.6207 | 2.3448 | 2.4828 | 2.2069 | 2.7586 | 3.0345 | 2.3448
TSO | - | 6 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.942 | 1.9536 | 1.9768 | 1.9923 | 1.9961 | 2 | 1.9556 | 1.886 | 1.8531 | 1.7971 | 1.8106 | 1.7894 | 1.8106 | 1.8068 | 1.83 | 1.8647 | 1.8686 | 1.8589 | 1.8725 | 1.857 | 1.8879 | 1.8667 | 1.8744 | 1.8821
TSO | - | 7 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 8 | 2020 | Summer | Pc, [MW] | 0 | 0 | 130.7812 | 128.4375 | 117.6562 | 116.7188 | 115.3125 | 120 | 120.9375 | 131.25 | 137.3438 | 136.875 | 132.1875 | 127.5 | 119.0625 | 120.4688 | 111.0938 | 113.4375 | 117.1875 | 120.4688 | 133.125 | 150 | 133.125 | 139.2188 | 133.5938 | 105.9375
TSO | - | 8 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 6.1955 | 5.9131 | 4.5397 | 4.6697 | 4.5882 | 5.1831 | 9.1091 | 10.8551 | 10.4872 | 8.3003 | 8.2812 | 7.3263 | 9.5371 | 9.4595 | 6.0809 | 5.6695 | 5.9454 | 7.0451 | 6.8683 | 7.8449 | 6.6222 | 6.2813 | 6.9085 | 5.5099
TSO | - | 8 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 6.1447 | 5.8557 | 4.5042 | 4.6031 | 4.5459 | 5.137 | 8.9433 | 10.9738 | 10.5693 | 8.3185 | 8.3169 | 7.3703 | 9.5829 | 9.4358 | 6.0774 | 5.6587 | 5.9231 | 7.0166 | 6.8804 | 7.9389 | 6.6682 | 6.3169 | 6.9568 | 5.4827
TSO | - | 8 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 130.8321 | 128.4948 | 117.6918 | 116.7853 | 115.3547 | 120.0461 | 121.1033 | 131.1313 | 137.2616 | 136.8569 | 132.1518 | 127.456 | 119.0167 | 120.4925 | 111.0972 | 113.4483 | 117.2098 | 120.4973 | 133.1129 | 149.906 | 133.079 | 139.1832 | 133.5455 | 105.9647
TSO | - | 8 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -19.0385 | -19.6731 | -19.25 | -19.6731 | -19.4615 | -22 | -18.4038 | -6.7692 | -5.0769 | -3.1731 | -3.5962 | 1.0577 | 3.5962 | 3.3846 | -0.84615 | -6.3462 | -4.0192 | -6.1346 | -9.3077 | -6.3462 | -10.1538 | -6.7692 | -11.2115 | -12.6923
TSO | - | 9 | 2020 | Summer | Pc, [MW] | 0 | 0 | 63.525 | 53.24 | 45.375 | 43.56 | 43.56 | 51.425 | 71.995 | 79.86 | 96.195 | 101.035 | 104.06 | 112.53 | 121 | 117.975 | 113.74 | 108.295 | 101.64 | 101.035 | 95.59 | 99.825 | 99.825 | 104.06 | 96.8 | 73.205
TSO | - | 9 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 3.2298 | 2.3417 | 2.0182 | 1.8122 | 2.0013 | 2.6735 | 5.9159 | 6.1645 | 6.8716 | 6.2714 | 6.02 | 5.9272 | 8.7155 | 9.4566 | 6.9767 | 5.9578 | 5.5161 | 6.4138 | 5.3542 | 4.4612 | 4.1235 | 5.0337 | 4.7052 | 3.7693
TSO | - | 9 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 2.7642 | 2.5367 | 1.4696 | 1.6484 | 1.4492 | 1.7491 | 4.8308 | 7.1175 | 7.8763 | 5.9958 | 7.0463 | 7.0438 | 10.7157 | 9.0475 | 5.4711 | 4.857 | 4.7778 | 5.3795 | 4.5181 | 6.0429 | 5.8425 | 4.3829 | 5.3414 | 3.8269
TSO | - | 9 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 63.9906 | 53.045 | 45.9236 | 43.7238 | 44.1121 | 52.3495 | 73.0801 | 78.907 | 95.1903 | 101.3106 | 103.0338 | 111.4134 | 118.9998 | 118.3842 | 115.2455 | 109.3958 | 102.3783 | 102.0693 | 96.4261 | 98.2433 | 98.106 | 104.7108 | 96.1637 | 73.1474
TSO | - | 9 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -14.2581 | -16.7742 | -17.6129 | -18.4516 | -17.6129 | -26 | -19.7097 | -10.0645 | -2.9355 | -1.2581 | 0.41935 | 0.41935 | 6.2903 | 5.871 | 5.871 | -2.5161 | -0.41935 | -2.5161 | -7.129 | -6.7097 | -6.2903 | -4.6129 | -7.129 | -10.9032
TSO | - | 10 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.8 | 2.1333 | 1.7333 | 2 | 1.3333 | 0.66667 | 1.3333 | 2.6667 | 3.3333 | 2.7333 | 4.1333 | 2.4667 | 2.3333 | 5 | 2.4667 | 3.6667 | 3.5333 | 3.9333 | 2.2 | 2.9333 | 2.0667 | 2.8667 | 3.9333 | 2.0667
TSO | - | 10 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.08506 | 0.097682 | 0.066918 | 0.079609 | 0.053002 | 0.02873 | 0.099752 | 0.21875 | 0.25559 | 0.16642 | 0.26128 | 0.14241 | 0.18724 | 0.39243 | 0.13545 | 0.18369 | 0.17936 | 0.23017 | 0.11349 | 0.15333 | 0.10276 | 0.12942 | 0.20331 | 0.1069
TSO | - | 10 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.084784 | 0.097797 | 0.066318 | 0.079282 | 0.052614 | 0.028604 | 0.099275 | 0.22475 | 0.25545 | 0.16545 | 0.25772 | 0.14192 | 0.18747 | 0.39181 | 0.1345 | 0.18248 | 0.17849 | 0.22895 | 0.11372 | 0.15533 | 0.10357 | 0.12999 | 0.20492 | 0.10755
TSO | - | 10 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.8003 | 2.1332 | 1.7339 | 2.0003 | 1.3337 | 0.66679 | 1.3338 | 2.6607 | 3.3335 | 2.7343 | 4.1369 | 2.4672 | 2.3331 | 5.0006 | 2.4676 | 3.6679 | 3.5342 | 3.9345 | 2.1998 | 2.9313 | 2.0659 | 2.8661 | 3.9317 | 2.066
TSO | - | 10 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -2 | -1.9467 | -1.9467 | -1.8667 | -1.8933 | -1.8133 | -1.8933 | -1.6533 | -1.7067 | -1.9467 | -1.92 | -1.7333 | -1.4667 | -1.52 | -2 | -1.6 | -1.7333 | -1.6 | -1.92 | -1.6267 | -1.8667 | -1.5467 | 1.84 | -1.7333
TSO | - | 11 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 12 | 2020 | Summer | Pc, [MW] | 0 | 0 | 277.5714 | 252.7143 | 236.1429 | 265.1429 | 281.7143 | 240.2857 | 339.7143 | 306.5714 | 319 | 343.8571 | 294.1429 | 323.1429 | 314.8571 | 298.2857 | 310.7143 | 298.2857 | 331.4286 | 314.8571 | 306.5714 | 360.4286 | 352.1429 | 377 | 327.2857 | 343.8571
TSO | - | 12 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 13.6976 | 12.2454 | 9.4649 | 11.0166 | 11.6249 | 10.8563 | 25.5275 | 27.2344 | 25.8211 | 21.4079 | 19.5497 | 18.8737 | 25.5151 | 23.3602 | 16.7607 | 14.459 | 16.6909 | 18.5765 | 15.0646 | 17.8573 | 16.6277 | 11.1391 | 17.2949 | 18.3564
TSO | - | 12 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 12.4934 | 10.9109 | 8.6866 | 10.0477 | 10.6901 | 9.8085 | 25.1818 | 23.7532 | 23.0856 | 20.3418 | 17.3844 | 18.3741 | 25.0472 | 23.4252 | 17.2442 | 15.3289 | 16.8753 | 18.1753 | 16.5971 | 20.0689 | 18.5282 | 22.9764 | 16.6732 | 17.3241
TSO | - | 12 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 278.7756 | 254.0488 | 236.9211 | 266.1117 | 282.6491 | 241.3335 | 340.06 | 310.0526 | 321.7355 | 344.9233 | 296.3082 | 323.6424 | 315.325 | 298.2206 | 310.2308 | 297.4157 | 331.2442 | 315.2584 | 305.039 | 358.2169 | 350.2423 | 365.1626 | 327.9075 | 344.8894
TSO | - | 12 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -17.6 | -19.2 | -20.8 | -20.8 | -20.8 | -24 | -17.6 | -6.4 | -3.2 | 1.6 | 0 | 3.2 | 0 | 0 | 1.6 | -9.6 | -9.6 | -11.2 | -12.8 | -12.8 | -16 | -14.4 | -16 | -16
TSO | - | 13 | 2020 | Summer | Pc, [MW] | 0 | 0 | 6.75 | 4.5 | 0 | 6.75 | 0 | -18 | -6.75 | -4.5 | 6.75 | -6.75 | 6.75 | -9 | -11.25 | 15.75 | -11.25 | 15.75 | 6.75 | 4.5 | -11.25 | 2.25 | -6.75 | -2.25 | 13.5 | 4.5
TSO | - | 13 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.31891 | 0.20807 | 0 | 0.2685 | 0 | 0.63586 | 0.36248 | 0.19392 | 0.51752 | 0.28264 | 0.42465 | 0.43717 | 0.27778 | 1.2202 | 0.51784 | 0.7819 | 0.34215 | 0.26283 | 0.074726 | 0.11831 | 0.079672 | 0.073056 | 0.71072 | 0.23549
TSO | - | 13 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.31801 | 0.20427 | 0 | 0.26775 | 0 | 0.62632 | 0.36182 | 0.1943 | 0.51734 | 0.28186 | 0.42292 | 0.44057 | 0.28015 | 1.2501 | 0.51583 | 0.79095 | 0.34147 | 0.26244 | 0.074923 | 0.11845 | 0.079685 | 0.073399 | 0.69041 | 0.23146
TSO | - | 13 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 6.7509 | 4.5038 | 0 | 6.7507 | 0 | -17.9905 | -6.7493 | -4.5004 | 6.7502 | -6.7492 | 6.7517 | -9.0034 | -11.2524 | 15.7201 | -11.248 | 15.741 | 6.7507 | 4.5004 | -11.2502 | 2.2499 | -6.75 | -2.2503 | 13.5203 | 4.504
TSO | - | 13 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -2.0579 | -2.0579 | -2.1789 | -2.1789 | -2.1789 | -2.3 | -1.9368 | -1.3316 | -1.9368 | -1.8158 | -1.9368 | -1.4526 | -1.2105 | -1.4526 | -1.0895 | -1.6947 | -1.5737 | -1.3316 | -2.1789 | -1.6947 | -1.8158 | -1.3316 | -1.8158 | -1.6947
TSO | - | 14 | 2020 | Summer | Pc, [MW] | 0 | 0 | 8.0902 | 7.7459 | 7.7459 | 8.6066 | 7.7459 | 7.4016 | 7.4016 | 7.5738 | 7.918 | 7.4016 | 9.4672 | 7.4016 | 9.2951 | 9.8115 | 9.6393 | 9.9836 | 9.6393 | 10.5 | 7.4016 | 6.541 | 6.541 | 6.8852 | 7.2295 | 0.51639
TSO | - | 14 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.38103 | 0.35736 | 0.29724 | 0.34293 | 0.30725 | 0.31892 | 0.55255 | 0.6218 | 0.58285 | 0.43994 | 0.56778 | 0.42797 | 0.75949 | 0.77467 | 0.54493 | 0.51917 | 0.48949 | 0.62006 | 0.38152 | 0.34325 | 0.32605 | 0.30984 | 0.37683 | 0.02681
TSO | - | 14 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.38234 | 0.35241 | 0.29817 | 0.34081 | 0.30631 | 0.31763 | 0.5523 | 0.63784 | 0.63108 | 0.45873 | 0.62098 | 0.42519 | 0.73319 | 0.76424 | 0.51001 | 0.47783 | 0.48675 | 0.60555 | 0.3829 | 0.34502 | 0.32696 | 0.31322 | 0.3735 | 0.026774
TSO | - | 14 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 8.0889 | 7.7509 | 7.745 | 8.6087 | 7.7468 | 7.4029 | 7.4019 | 7.5577 | 7.8698 | 7.3828 | 9.414 | 7.4044 | 9.3214 | 9.8219 | 9.6743 | 10.025 | 9.6421 | 10.5145 | 7.4003 | 6.5392 | 6.5401 | 6.8819 | 7.2328 | 0.51643
TSO | - | 14 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -2.65 | -3.18 | -2.65 | -3.18 | -2.65 | -3.18 | -5.3 | -1.59 | -2.12 | -2.65 | -2.12 | -2.65 | -1.59 | -1.06 | -1.06 | -0.53 | 4.24 | 4.24 | -0.53 | -0.53 | -0.53 | -1.06 | -1.59 | -4.24
TSO | - | 15 | 2020 | Summer | Pc, [MW] | 0 | 0 | 12.1748 | 11.1068 | 10.466 | 10.2524 | 10.2524 | 10.2524 | 14.7379 | 20.0777 | 20.932 | 20.7184 | 20.2913 | 20.932 | 22 | 21.3592 | 20.0777 | 18.3689 | 18.3689 | 18.5825 | 20.7184 | 19.2233 | 20.2913 | 21.5728 | 18.7961 | 14.7379
TSO | - | 15 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.5792 | 0.51458 | 0.40423 | 0.4105 | 0.40903 | 0.44344 | 1.1115 | 1.6205 | 1.5512 | 1.2302 | 1.2444 | 1.193 | 1.764 | 1.6969 | 1.1273 | 0.94116 | 0.93998 | 1.103 | 1.0696 | 1.0096 | 1.0107 | 0.97234 | 0.99892 | 0.78899
TSO | - | 15 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.56958 | 0.50315 | 0.40026 | 0.404 | 0.40308 | 0.43828 | 1.0884 | 1.7187 | 1.658 | 1.2853 | 1.3035 | 1.2198 | 1.7689 | 1.6532 | 1.0701 | 0.89323 | 0.92038 | 1.066 | 1.0702 | 1.0132 | 1.0151 | 0.97983 | 0.95188 | 0.74029
TSO | - | 15 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 12.1844 | 11.1182 | 10.47 | 10.2589 | 10.2584 | 10.2576 | 14.7609 | 19.9795 | 20.8252 | 20.6634 | 20.2322 | 20.9052 | 21.9951 | 21.4029 | 20.1349 | 18.4169 | 18.3885 | 18.6196 | 20.7178 | 19.2197 | 20.2869 | 21.5653 | 18.8432 | 14.7866
TSO | - | 15 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -3.8235 | -4.7059 | -4.4118 | -4.1176 | -4.4118 | -5 | -3.8235 | -2.0588 | 0 | 0 | 0 | -0.29412 | 0 | 1.4706 | 1.1765 | 0 | -1.7647 | -1.7647 | -0.88235 | -1.1765 | -1.1765 | -1.7647 | -1.7647 | -3.5294
TSO | - | 16 | 2020 | Summer | Pc, [MW] | 0 | 0 | 28.8906 | 26.4719 | 25.9344 | 24.8594 | 24.5906 | 24.4563 | 31.7125 | 36.4156 | 38.8344 | 40.3125 | 40.0438 | 40.9844 | 40.9844 | 43 | 39.2375 | 40.1781 | 39.6406 | 39.6406 | 38.1625 | 38.1625 | 37.7594 | 40.85 | 38.8344 | 33.4594
TSO | - | 16 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 1.287 | 1.1509 | 0.95314 | 0.94459 | 0.93197 | 1.0018 | 2.163 | 2.7747 | 3.3648 | 2.4566 | 2.5962 | 2.467 | 3.4543 | 3.5131 | 2.2559 | 2.2697 | 2.1042 | 2.4266 | 1.8661 | 1.8977 | 1.7878 | 1.7072 | 1.8848 | 1.6219
TSO | - | 16 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 1.439 | 1.2747 | 1.0404 | 1.0304 | 1.0159 | 1.1015 | 2.5707 | 3.2818 | 2.5889 | 2.438 | 2.4319 | 2.2572 | 3.1273 | 3.2313 | 2.0383 | 1.7426 | 1.9105 | 2.2005 | 2.0752 | 2.118 | 1.9819 | 1.9894 | 2.1457 | 1.85
TSO | - | 16 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 28.7387 | 26.3481 | 25.8472 | 24.7736 | 24.5067 | 24.3566 | 31.3048 | 35.9086 | 39.6103 | 40.3311 | 40.208 | 41.1942 | 41.3114 | 43.2818 | 39.4551 | 40.7053 | 39.8343 | 39.8667 | 37.9534 | 37.9422 | 37.5652 | 40.5678 | 38.5735 | 33.2312
TSO | - | 16 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.2449 | -0.30612 | -0.61224 | -0.61224 | -0.85714 | -0.85714 | 0.2449 | 1.4694 | 2.0816 | 2.449 | 1.9592 | 3 | 2.8776 | 3 | 2.6939 | 2.0816 | 1.898 | 2.0816 | 1.7143 | 1.9592 | 1.5306 | 1.5918 | 0.73469 | 0.36735
TSO | - | 17 | 2020 | Summer | Pc, [MW] | 0 | 0 | 26.6163 | 24.4186 | 23.9302 | 23.9302 | 24.6628 | 25.1512 | 33.4535 | 38.093 | 39.314 | 36.1395 | 37.1163 | 42 | 41.7558 | 40.5349 | 38.8256 | 36.3837 | 37.6047 | 37.8488 | 37.8488 | 36.1395 | 39.5581 | 38.3372 | 31.9884 | 29.5465
TSO | - | 17 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 1.2026 | 0.97735 | 0.8126 | 0.87845 | 0.81308 | 0.85518 | 2.3316 | 4.081 | 2.6934 | 1.7802 | 2.0737 | 2.1799 | 3.4851 | 3.1941 | 2.0724 | 2.0449 | 1.7576 | 2.0483 | 2.4342 | 2.287 | 2.3577 | 1.8418 | 1.6937 | 1.3744
TSO | - | 17 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 1.3089 | 1.2601 | 1.0268 | 1.0227 | 1.1405 | 1.3079 | 2.662 | 2.2545 | 3.3339 | 2.6077 | 2.5868 | 2.6613 | 3.2203 | 3.1637 | 2.1767 | 1.5885 | 2.0509 | 2.3697 | 1.4747 | 1.5158 | 1.5915 | 1.6274 | 1.6262 | 1.6915
TSO | - | 17 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 26.5099 | 24.1358 | 23.716 | 23.786 | 24.3354 | 24.6985 | 33.1231 | 39.9196 | 38.6734 | 35.312 | 36.6031 | 41.5185 | 42.0206 | 40.5652 | 38.7212 | 36.8402 | 37.3113 | 37.5275 | 38.8083 | 36.9107 | 40.3243 | 38.5516 | 32.0559 | 29.2295
TSO | - | 17 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -6.5455 | -6.5455 | -7.6364 | -7.6364 | -8 | -8 | -3.2727 | -1.4545 | 0 | -1.0909 | -2.1818 | -1.0909 | 0.72727 | 0 | -0.36364 | -2.1818 | -1.0909 | 0.36364 | 0 | -3.2727 | -2.1818 | -2.1818 | -5.0909 | -5.4545
TSO | - | 18 | 2020 | Summer | Pc, [MW] | 0 | 0 | 16.958 | 15.4469 | 13.2642 | 14.6074 | 15.1111 | 16.1185 | 21.9951 | 25.6889 | 27.2 | 26.6963 | 24.0099 | 27.2 | 26.5284 | 26.0247 | 21.9951 | 21.3235 | 20.9877 | 20.8198 | 20.484 | 22.6667 | 22.8346 | 24.3457 | 22.163 | 18.9728
TSO | - | 18 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.90977 | 0.75755 | 0.56246 | 0.66125 | 0.6794 | 0.92246 | 2.3006 | 1.9436 | 1.7399 | 1.496 | 1.1497 | 1.7543 | 2.1653 | 1.3671 | 1.083 | 1.015 | 0.85162 | 0.91719 | 1.2656 | 1.5209 | 1.5091 | 1.3232 | 0.99463 | 0.90181
TSO | - | 18 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.69035 | 0.65786 | 0.45712 | 0.49924 | 0.51758 | 0.46375 | 0.98257 | 2.3289 | 2.4302 | 1.7453 | 1.8651 | 1.381 | 2.0949 | 2.7148 | 1.3242 | 1.1144 | 1.2739 | 1.513 | 0.84988 | 0.86425 | 0.77057 | 0.87987 | 1.3056 | 1.0669
TSO | - | 18 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 17.1774 | 15.5466 | 13.3695 | 14.7694 | 15.2729 | 16.5772 | 23.3131 | 25.3036 | 26.5096 | 26.447 | 23.2945 | 27.5733 | 26.5988 | 24.677 | 21.7539 | 21.2241 | 20.5653 | 20.2239 | 20.8997 | 23.3233 | 23.5731 | 24.789 | 21.852 | 18.8077
TSO | - | 18 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -4.0091 | -5.3455 | -5.7909 | -4.9 | -4.4545 | -4.0091 | -0.89091 | 6.6818 | 6.6818 | 8.0182 | 6.2364 | 8.9091 | 9.8 | 9.3545 | 7.5727 | 5.7909 | 4.0091 | 3.5636 | 3.1182 | 4.0091 | 3.5636 | 2.2273 | 1.3364 | -0.89091
TSO | - | 19 | 2020 | Summer | Pc, [MW] | 0 | 0 | 2.2 | 2.2 | 2.75 | 0.55 | 1.1 | 2.75 | 2.2 | 1.1 | 0 | -3.3 | -3.3 | -2.75 | -2.75 | -1.65 | 1.1 | 1.1 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | -1.65 | -0.55
TSO | - | 19 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.10642 | 0.10033 | 0.10733 | 0.022061 | 0.044365 | 0.14279 | 0.1974 | 0.092775 | 0 | 0.11168 | 0.13613 | 0.11755 | 0.061986 | 0.039867 | 0.060227 | 0.055719 | 0 | 0 | 0.02881 | 0.029699 | 0.028468 | 0.025226 | 0.077154 | 0.024682
TSO | - | 19 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.10117 | 0.10126 | 0.10406 | 0.021633 | 0.042768 | 0.093717 | 0.131 | 0.090172 | 0 | 0.1643 | 0.16598 | 0.15065 | 0.074397 | 0.040294 | 0.060159 | 0.054131 | 0 | 0 | 0.027992 | 0.028175 | 0.026441 | 0.024545 | 0.082629 | 0.025205
TSO | - | 19 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 2.2053 | 2.1991 | 2.7533 | 0.55043 | 1.1016 | 2.7991 | 2.2664 | 1.1026 | 0 | -3.3526 | -3.3298 | -2.7831 | -2.7624 | -1.6504 | 1.1001 | 1.1016 | 0 | 0 | 0.55082 | 0.55152 | 0.55203 | 0.55068 | -1.6555 | -0.55052
TSO | - | 19 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.43846 | 0.39231 | 0.18462 | 0.32308 | 0.34615 | 0.18462 | 0.53077 | 0.41538 | 0.43846 | 0.53077 | 0.50769 | 0.57692 | 0.6 | 0.57692 | 0.48462 | 0.53077 | 0.57692 | 0.57692 | 0.53077 | 0.50769 | 0.55385 | 0.55385 | 0.53077 | 0.57692
TSO | - | 20 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.4522 | 1.362 | 1.3078 | 1.2898 | 1.3259 | 1.2718 | 1.5153 | 1.7318 | 1.822 | 1.8941 | 2.0384 | 2.3 | 1.5424 | 2.0745 | 1.9663 | 1.9122 | 2.0024 | 1.9031 | 1.7318 | 1.7949 | 1.8039 | 1.9122 | 1.5424 | 1.4071
TSO | - | 20 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.071993 | 0.062906 | 0.051535 | 0.053526 | 0.055185 | 0.053857 | 0.10949 | 0.16677 | 0.16007 | 0.095131 | 0.10977 | 0.12333 | 0.10738 | 0.15166 | 0.11073 | 0.10118 | 0.093626 | 0.10022 | 0.096334 | 0.10777 | 0.10742 | 0.093542 | 0.074852 | 0.069161
TSO | - | 20 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.065029 | 0.061891 | 0.048995 | 0.048943 | 0.04984 | 0.055516 | 0.1167 | 0.12125 | 0.11926 | 0.13484 | 0.14619 | 0.14178 | 0.1403 | 0.17372 | 0.10446 | 0.089779 | 0.10917 | 0.12193 | 0.082517 | 0.081101 | 0.072669 | 0.079493 | 0.085224 | 0.076843
TSO | - | 20 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.4591 | 1.363 | 1.3104 | 1.2944 | 1.3312 | 1.2701 | 1.5081 | 1.7773 | 1.8628 | 1.8544 | 2.002 | 2.2815 | 1.5094 | 2.0525 | 1.9725 | 1.9236 | 1.9868 | 1.8814 | 1.7456 | 1.8216 | 1.8387 | 1.9262 | 1.532 | 1.3994
TSO | - | 20 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.29412 | -0.47059 | -0.47059 | -0.52941 | -0.41176 | -0.76471 | -0.47059 | 0.23529 | 0.76471 | 0.70588 | 0.35294 | 1 | 0.76471 | 1 | 0.94118 | 0.35294 | 0.64706 | 0.41176 | 0.29412 | 0.35294 | 0.35294 | 0.17647 | -0.17647 | -0.70588
TSO | - | 21 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 23 | 2020 | Summer | Pc, [MW] | 0 | 0 | -0.31765 | -1.7294 | -1.9941 | -2.1706 | -1.2882 | -2.3471 | -0.75882 | -1.0235 | -1.2882 | 0.56471 | 0.91765 | 1.5353 | 3.9176 | 6.3 | 6.0353 | 5.5941 | 5.2412 | 5.0647 | 2.4176 | 2.9471 | 4.7118 | 5.5941 | 5.5941 | 6.1235
TSO | - | 23 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.014477 | 0.057429 | 0.047508 | 0.055213 | 0.030116 | 0.084191 | 0.040967 | 0.043432 | 0.034175 | 0.03401 | 0.057145 | 0.087103 | 0.30083 | 0.46142 | 0.29851 | 0.26879 | 0.26349 | 0.29591 | 0.12866 | 0.15899 | 0.23957 | 0.25845 | 0.31978 | 0.35821
TSO | - | 23 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.014331 | 0.05702 | 0.046057 | 0.050906 | 0.02908 | 0.080386 | 0.040458 | 0.044869 | 0.034535 | 0.034554 | 0.05808 | 0.089866 | 0.3283 | 0.52671 | 0.36199 | 0.28986 | 0.26732 | 0.29527 | 0.12103 | 0.15112 | 0.23083 | 0.24778 | 0.26082 | 0.27721
TSO | - | 23 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | -0.3175 | -1.729 | -1.9927 | -2.1663 | -1.2872 | -2.3433 | -0.75831 | -1.025 | -1.2886 | 0.56416 | 0.91671 | 1.5325 | 3.8902 | 6.2347 | 5.9718 | 5.573 | 5.2373 | 5.0653 | 2.4253 | 2.9549 | 4.7205 | 5.6048 | 5.6531 | 6.2045
TSO | - | 23 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.83276 | -1.0138 | -1.1948 | -1.7379 | -1.8284 | -2.1 | -1.4664 | -0.018103 | 0.525 | 1.4302 | 1.3397 | 0.88707 | 0.525 | -0.28966 | -0.10862 | -0.56121 | -0.56121 | -0.74224 | -0.018103 | -0.19914 | -0.74224 | -0.92328 | -0.92328 | -1.3759
TSO | - | 24 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 25 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.59062 | 6.3 | 3.15 | 0.49219 | 0.49219 | 0.59062 | 0.39375 | 0.19687 | 0.39375 | 3.7406 | 0.29531 | 0.7875 | 0.39375 | 0.49219 | 1.7719 | 0.49219 | 0.39375 | 0.39375 | 1.1812 | 0.19687 | 0.39375 | 0.19687 | 0.39375 | 0.19687
TSO | - | 25 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.028341 | 0.29782 | 0.12915 | 0.019933 | 0.0198 | 0.025771 | 0.029741 | 0.016351 | 0.030243 | 0.20887 | 0.018553 | 0.045318 | 0.031646 | 0.038582 | 0.0947 | 0.024569 | 0.019956 | 0.023018 | 0.06202 | 0.010368 | 0.01968 | 0.0089191 | 0.020579 | 0.01027
TSO | - | 25 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.027389 | 0.27945 | 0.11298 | 0.019169 | 0.019187 | 0.025023 | 0.029034 | 0.016393 | 0.030124 | 0.2453 | 0.018528 | 0.045455 | 0.031586 | 0.038616 | 0.099216 | 0.024583 | 0.019922 | 0.022943 | 0.059976 | 0.010348 | 0.01963 | 0.0088965 | 0.020287 | 0.010159
TSO | - | 25 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.59158 | 6.3184 | 3.1662 | 0.49295 | 0.4928 | 0.59137 | 0.39446 | 0.19683 | 0.39387 | 3.7042 | 0.29534 | 0.78736 | 0.39381 | 0.49215 | 1.7674 | 0.49217 | 0.39378 | 0.39382 | 1.1833 | 0.1969 | 0.3938 | 0.1969 | 0.39404 | 0.19699
TSO | - | 25 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.43636 | 3.2 | 1.7455 | 0.43636 | 0.21818 | 0.43636 | 0.43636 | 0.72727 | 0.72727 | 2.4 | 0.50909 | 1.0909 | 0.43636 | 0.72727 | 1.9636 | 0.65455 | 0.50909 | 0.43636 | 0 | 0.29091 | 0.29091 | 0.58182 | 0 | 0
TSO | - | 26 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 27 | 2020 | Summer | Pc, [MW] | 0 | 0 | 6.3047 | 6.2564 | 5.7491 | 6.0631 | 5.4834 | 6.0873 | 7.5366 | 9.1792 | 8.9377 | 9.3 | 8.6719 | 9.1551 | 9.0101 | 9.2034 | 9.0101 | 8.0681 | 8.213 | 8.1164 | 8.1405 | 8.4787 | 8.2613 | 8.2855 | 7.4642 | 7.2226
TSO | - | 27 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.31754 | 0.30437 | 0.22799 | 0.26778 | 0.22849 | 0.27248 | 0.62735 | 0.70658 | 0.66071 | 0.52795 | 0.52516 | 0.50565 | 0.69721 | 0.70311 | 0.46488 | 0.40132 | 0.41865 | 0.48033 | 0.43102 | 0.45041 | 0.41708 | 0.37371 | 0.40622 | 0.40293
TSO | - | 27 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.27736 | 0.26891 | 0.21393 | 0.21391 | 0.20586 | 0.25103 | 0.49765 | 0.82006 | 0.70954 | 0.60122 | 0.56373 | 0.54963 | 0.74971 | 0.74042 | 0.52119 | 0.40438 | 0.41314 | 0.46706 | 0.40971 | 0.44177 | 0.40768 | 0.37606 | 0.36846 | 0.34652
TSO | - | 27 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 6.3449 | 6.2918 | 5.7632 | 6.117 | 5.506 | 6.1087 | 7.6663 | 9.0657 | 8.8888 | 9.2267 | 8.6334 | 9.1111 | 8.9576 | 9.1661 | 8.9538 | 8.065 | 8.2185 | 8.1296 | 8.1618 | 8.4873 | 8.2707 | 8.2831 | 7.5019 | 7.279
TSO | - | 27 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.35 | -0.3375 | -0.4625 | -0.4625 | -0.5 | -0.4125 | -0.05 | 0.3125 | 0.325 | 0.2875 | 0.2625 | 0.4375 | 0.3875 | 0.4 | -0.2625 | 0.1125 | 0.1 | 0.0375 | -0.0625 | 0 | -0.05 | -0.1 | -0.2375 | -0.325
TSO | - | 28 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.1615 | 2.7876 | 2.5926 | 2.5357 | 2.5926 | 2.4057 | 2.877 | 3.4947 | 3.8848 | 4.0555 | 4.3643 | 4.535 | 4.47 | 4.6 | 4.2749 | 4.3318 | 4.1855 | 4.283 | 4.0392 | 4.023 | 4.0148 | 4.283 | 4.2668 | 3.6898
TSO | - | 28 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.15214 | 0.13054 | 0.099907 | 0.10374 | 0.10338 | 0.10346 | 0.22046 | 0.28661 | 0.29458 | 0.24251 | 0.27093 | 0.25726 | 0.35474 | 0.35871 | 0.23059 | 0.21605 | 0.21246 | 0.25113 | 0.21044 | 0.21258 | 0.20131 | 0.1936 | 0.2245 | 0.19553
TSO | - | 28 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.14617 | 0.12489 | 0.099376 | 0.097711 | 0.10199 | 0.10343 | 0.209 | 0.29461 | 0.30101 | 0.24988 | 0.27707 | 0.26547 | 0.36309 | 0.36279 | 0.23727 | 0.21654 | 0.21144 | 0.24881 | 0.20672 | 0.21073 | 0.19951 | 0.19398 | 0.21834 | 0.18734
TSO | - | 28 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.1675 | 2.7933 | 2.5931 | 2.5417 | 2.594 | 2.4057 | 2.8885 | 3.4867 | 3.8784 | 4.0481 | 4.3582 | 4.5268 | 4.4616 | 4.5959 | 4.2682 | 4.3313 | 4.1865 | 4.2854 | 4.0429 | 4.0248 | 4.0166 | 4.2827 | 4.273 | 3.698
TSO | - | 28 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.15 | -0.25 | -0.425 | -0.425 | -0.4 | -0.95 | -0.45 | 0.5 | 0.55 | 1.7 | 1.575 | 2.15 | 2.3 | 2.05 | 1.425 | 1.2 | 1.025 | 1.225 | 0.75 | 0.825 | 0.55 | 0.9 | 0.675 | 0.3
TSO | - | 29 | 2020 | Summer | Pc, [MW] | 0 | 0 | 4.4403 | 1.7761 | 2.4104 | 2.0299 | 0.50746 | 0.88806 | 4.694 | 10.403 | 13.0672 | 13.9552 | 13.9552 | 16.3657 | 15.7313 | 16.3657 | 15.6045 | 13.5746 | 13.194 | 12.9403 | 12.5597 | 12.306 | 13.194 | 16.1119 | 17 | 11.7985
TSO | - | 29 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.2127 | 0.082329 | 0.092192 | 0.081788 | 0.020077 | 0.038034 | 0.35892 | 0.85643 | 0.98135 | 0.83377 | 0.86252 | 0.90823 | 1.2427 | 1.2933 | 0.84044 | 0.68027 | 0.67484 | 0.76575 | 0.6644 | 0.65784 | 0.6692 | 0.73081 | 0.90443 | 0.63335
TSO | - | 29 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.20627 | 0.080418 | 0.093091 | 0.079474 | 0.02012 | 0.03834 | 0.34176 | 0.87375 | 1.022 | 0.86061 | 0.88977 | 0.97819 | 1.2835 | 1.2736 | 0.86733 | 0.67534 | 0.66141 | 0.74471 | 0.63272 | 0.63706 | 0.64801 | 0.72719 | 0.85996 | 0.59092
TSO | - | 29 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 4.4467 | 1.778 | 2.4095 | 2.0322 | 0.50742 | 0.88775 | 4.7112 | 10.3857 | 13.0265 | 13.9284 | 13.928 | 16.2957 | 15.6905 | 16.3853 | 15.5776 | 13.5796 | 13.2075 | 12.9613 | 12.5914 | 12.3267 | 13.2152 | 16.1156 | 17.0445 | 11.8409
TSO | - | 29 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.98621 | 0.71724 | 0.8069 | 0.44828 | 0.44828 | -0.17931 | 0.62759 | 1.9724 | 1.9724 | 2.0621 | 2.0621 | 2.6 | 2.4207 | 2.331 | 2.1517 | 1.6138 | 1.5241 | 1.7034 | 1.5241 | 1.6138 | 1.4345 | 1.7931 | 1.9724 | 1.5241
TSO | - | 30 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.7478 | 1.7583 | 1.7791 | 1.793 | 1.7965 | 1.8 | 1.76 | 1.6974 | 1.6678 | 1.6174 | 1.6296 | 1.6104 | 1.6296 | 1.6261 | 1.647 | 1.6783 | 1.6817 | 1.673 | 1.6852 | 1.6713 | 1.6991 | 1.68 | 1.687 | 1.6939
TSO | - | 31 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.5323 | 4.6872 | 5.8 | 4.9907 | 4.6198 | 3.6166 | 2.1413 | 0.8093 | 0.39622 | -0.48895 | -0.31192 | -1.0201 | -1.2561 | -1.5933 | -0.75029 | -0.10959 | 0.57326 | 0.69128 | 1.6692 | 1.7029 | 1.1718 | 0.5311 | 1.0116 | 1.1212
TSO | - | 31 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.17023 | 0.20328 | 0.21865 | 0.21287 | 0.19281 | 0.16308 | 0.16351 | 0.065296 | 0.030028 | 0.020229 | 0.014177 | 0.049071 | 0.030661 | 0.037913 | 0.033738 | 0.0049638 | 0.028481 | 0.039331 | 0.080535 | 0.080698 | 0.055838 | 0.023775 | 0.05209 | 0.059389
TSO | - | 31 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.16306 | 0.22621 | 0.22718 | 0.18362 | 0.17313 | 0.14795 | 0.15612 | 0.069303 | 0.030717 | 0.020662 | 0.014378 | 0.050411 | 0.031634 | 0.039495 | 0.0352 | 0.0049846 | 0.029576 | 0.041359 | 0.091853 | 0.098491 | 0.061148 | 0.024286 | 0.052904 | 0.056955
TSO | - | 31 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.5394 | 4.6643 | 5.7915 | 5.0199 | 4.6394 | 3.6317 | 2.1487 | 0.80529 | 0.39553 | -0.48939 | -0.31212 | -1.0214 | -1.2571 | -1.5949 | -0.75175 | -0.10961 | 0.57216 | 0.68925 | 1.6579 | 1.6851 | 1.1665 | 0.53059 | 1.0108 | 1.1237
TSO | - | 31 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.9276 | 1.3166 | 1.2134 | 1.2994 | 1.6264 | 1.5834 | 1.8846 | 1.6264 | 1.5404 | 1.876 | 2.0653 | 1.9878 | 2.2202 | 2.2976 | 2.2116 | 2.5644 | 2.7365 | 2.9 | 2.6332 | 2.6677 | 2.6418 | 2.289 | 2.6246 | 2.8742
TSO | - | 32 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.395 | 1.37 | 1.255 | 1.245 | 1.23 | 1.28 | 1.29 | 1.4 | 1.465 | 1.46 | 1.41 | 1.36 | 1.27 | 1.285 | 1.185 | 1.21 | 1.25 | 1.285 | 1.42 | 1.6 | 1.42 | 1.485 | 1.425 | 1.13
TSO | - | 32 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.067577 | 0.063039 | 0.048614 | 0.050661 | 0.049835 | 0.056654 | 0.10042 | 0.11821 | 0.11334 | 0.088385 | 0.087315 | 0.078282 | 0.097624 | 0.095502 | 0.064028 | 0.060459 | 0.06293 | 0.074703 | 0.072533 | 0.081316 | 0.069776 | 0.067103 | 0.07543 | 0.061283
TSO | - | 32 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.064052 | 0.062495 | 0.047854 | 0.048248 | 0.047596 | 0.053427 | 0.092135 | 0.11463 | 0.11126 | 0.088881 | 0.089732 | 0.078482 | 0.10632 | 0.10605 | 0.06566 | 0.060376 | 0.063666 | 0.075289 | 0.07412 | 0.087045 | 0.071988 | 0.067278 | 0.072467 | 0.055972
TSO | - | 32 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.3985 | 1.3705 | 1.2558 | 1.2474 | 1.2322 | 1.2832 | 1.2983 | 1.4036 | 1.4671 | 1.4595 | 1.4076 | 1.3598 | 1.2613 | 1.2745 | 1.1834 | 1.2101 | 1.2493 | 1.2844 | 1.4184 | 1.5943 | 1.4178 | 1.4848 | 1.428 | 1.1353
TSO | - | 32 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.69231 | -0.71538 | -0.7 | -0.71538 | -0.70769 | -0.8 | -0.66923 | -0.24615 | -0.18462 | -0.11538 | -0.13077 | 0.038462 | 0.13077 | 0.12308 | -0.030769 | -0.23077 | -0.14615 | -0.22308 | -0.33846 | -0.23077 | -0.36923 | -0.24615 | -0.40769 | -0.46154
TSO | - | 33 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.995 | 1.672 | 1.425 | 1.368 | 1.368 | 1.615 | 2.261 | 2.508 | 3.021 | 3.173 | 3.268 | 3.534 | 3.8 | 3.705 | 3.572 | 3.401 | 3.192 | 3.173 | 3.002 | 3.135 | 3.135 | 3.268 | 3.04 | 2.299
TSO | - | 33 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.10121 | 0.079436 | 0.056549 | 0.057037 | 0.056847 | 0.073422 | 0.18937 | 0.22707 | 0.24592 | 0.19695 | 0.20296 | 0.20369 | 0.256 | 0.24133 | 0.18752 | 0.17239 | 0.16308 | 0.1887 | 0.15609 | 0.15811 | 0.15494 | 0.15 | 0.16916 | 0.13517
TSO | - | 33 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.087033 | 0.07377 | 0.052986 | 0.051644 | 0.051514 | 0.06547 | 0.14813 | 0.19005 | 0.21724 | 0.1883 | 0.20739 | 0.20367 | 0.35424 | 0.33979 | 0.20341 | 0.16724 | 0.16019 | 0.18167 | 0.15395 | 0.17177 | 0.15804 | 0.14573 | 0.14635 | 0.10338
TSO | - | 33 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 2.0092 | 1.6777 | 1.4286 | 1.3734 | 1.3733 | 1.623 | 2.3022 | 2.545 | 3.0497 | 3.1817 | 3.2636 | 3.534 | 3.7018 | 3.6065 | 3.5561 | 3.4062 | 3.1949 | 3.18 | 3.0041 | 3.1213 | 3.1319 | 3.2723 | 3.0628 | 2.3308
TSO | - | 33 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -1.0419 | -1.2258 | -1.2871 | -1.3484 | -1.2871 | -1.9 | -1.4403 | -0.73548 | -0.21452 | -0.091935 | 0.030645 | 0.030645 | 0.45968 | 0.42903 | 0.42903 | -0.18387 | -0.030645 | -0.18387 | -0.52097 | -0.49032 | -0.45968 | -0.3371 | -0.52097 | -0.79677
TSO | - | 34 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 35 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.96 | 3.7886 | 3.6 | 3.7543 | 3.72 | 3.7543 | 5.04 | 5.6743 | 6 | 5.6743 | 5.5029 | 5.88 | 5.8457 | 5.4686 | 5.2286 | 5.04 | 5.04 | 4.8171 | 4.9543 | 5.2114 | 5.1257 | 5.4171 | 5.04 | 4.32
TSO | - | 35 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.19897 | 0.17957 | 0.14432 | 0.15889 | 0.15628 | 0.17112 | 0.40727 | 0.47373 | 0.46476 | 0.333 | 0.3379 | 0.3329 | 0.42992 | 0.38861 | 0.28161 | 0.25402 | 0.25675 | 0.28601 | 0.25053 | 0.26073 | 0.24606 | 0.24333 | 0.27426 | 0.25194
TSO | - | 35 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.17469 | 0.16758 | 0.1324 | 0.13937 | 0.13839 | 0.15175 | 0.34505 | 0.47 | 0.45511 | 0.35595 | 0.35307 | 0.34487 | 0.50883 | 0.46912 | 0.29061 | 0.24929 | 0.25368 | 0.27627 | 0.26113 | 0.28764 | 0.26566 | 0.24687 | 0.24883 | 0.19632
TSO | - | 35 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.9843 | 3.8006 | 3.6119 | 3.7738 | 3.7379 | 3.7737 | 5.1022 | 5.678 | 6.0096 | 5.6513 | 5.4877 | 5.868 | 5.7668 | 5.3881 | 5.2196 | 5.0447 | 5.0431 | 4.8269 | 4.9437 | 5.1845 | 5.1061 | 5.4136 | 5.0654 | 4.3756
TSO | - | 35 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.38889 | -0.5 | -0.5 | -0.38889 | -0.44444 | -0.55556 | 0.88889 | 2.1111 | 2.4444 | 2.1667 | 2.2222 | 3 | 2.8333 | 2.7778 | 1.8889 | 1.5 | 1.4444 | 1.0556 | 1.0556 | 0.94444 | 0.72222 | 1.3889 | 0.55556 | -0.055556
TSO | - | 36 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 38 | 2020 | Summer | Pc, [MW] | 0 | 0 | 10.7869 | 10.3279 | 10.3279 | 11.4754 | 10.3279 | 9.8689 | 9.8689 | 10.0984 | 10.5574 | 9.8689 | 12.623 | 9.8689 | 12.3934 | 13.082 | 12.8525 | 13.3115 | 12.8525 | 14 | 9.8689 | 8.7213 | 8.7213 | 9.1803 | 9.6393 | 0.68852
TSO | - | 38 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.52968 | 0.47168 | 0.40146 | 0.47474 | 0.4214 | 0.42305 | 0.73295 | 0.87124 | 0.84335 | 0.56817 | 0.80558 | 0.55324 | 0.96388 | 0.97998 | 0.70664 | 0.66902 | 0.65757 | 0.83985 | 0.49157 | 0.44081 | 0.412 | 0.40717 | 0.52513 | 0.03618
TSO | - | 38 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.48815 | 0.47467 | 0.39241 | 0.43693 | 0.39669 | 0.42568 | 0.74018 | 0.80827 | 0.77523 | 0.63007 | 0.77942 | 0.58431 | 1.0264 | 1.0719 | 0.69995 | 0.66031 | 0.64409 | 0.79431 | 0.52765 | 0.4769 | 0.45869 | 0.42357 | 0.47531 | 0.035265
TSO | - | 38 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 10.8284 | 10.3249 | 10.3369 | 11.5132 | 10.3526 | 9.8662 | 9.8616 | 10.1613 | 10.6255 | 9.8069 | 12.6491 | 9.8378 | 12.331 | 12.99 | 12.8591 | 13.3202 | 12.8659 | 14.0455 | 9.8328 | 8.6852 | 8.6746 | 9.1639 | 9.6892 | 0.68944
TSO | - | 38 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -3.5 | -4.2 | -3.5 | -4.2 | -3.5 | -4.2 | -7 | -2.1 | -2.8 | -3.5 | -2.8 | -3.5 | -2.1 | -1.4 | -1.4 | -0.7 | 5.6 | 5.6 | -0.7 | -0.7 | -0.7 | -1.4 | -2.1 | -5.6
TSO | - | 39 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 41 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.9924 | 3.6628 | 3.5895 | 3.5895 | 3.6994 | 3.7727 | 5.018 | 5.714 | 5.8971 | 5.4209 | 5.5674 | 6.3 | 6.2634 | 6.0802 | 5.8238 | 5.4576 | 5.6407 | 5.6773 | 5.6773 | 5.4209 | 5.9337 | 5.7506 | 4.7983 | 4.432
TSO | - | 41 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.19298 | 0.16709 | 0.13935 | 0.1473 | 0.14928 | 0.16422 | 0.38592 | 0.46437 | 0.43989 | 0.32634 | 0.34614 | 0.35828 | 0.49336 | 0.47184 | 0.32424 | 0.27812 | 0.29014 | 0.33809 | 0.30103 | 0.27494 | 0.28469 | 0.2654 | 0.25036 | 0.23717
TSO | - | 41 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.18374 | 0.16854 | 0.13657 | 0.13787 | 0.14375 | 0.16023 | 0.36312 | 0.48595 | 0.46421 | 0.33185 | 0.35294 | 0.36791 | 0.51247 | 0.48183 | 0.31313 | 0.26689 | 0.28113 | 0.32459 | 0.28531 | 0.29548 | 0.3077 | 0.25498 | 0.24764 | 0.22271
TSO | - | 41 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 4.0017 | 3.6613 | 3.5923 | 3.599 | 3.7049 | 3.7767 | 5.0408 | 5.6924 | 5.8728 | 5.4154 | 5.5606 | 6.2904 | 6.2443 | 6.0702 | 5.8349 | 5.4688 | 5.6497 | 5.6908 | 5.693 | 5.4004 | 5.9107 | 5.761 | 4.801 | 4.4464
TSO | - | 41 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -2.4545 | -2.4545 | -2.8636 | -2.8636 | -3 | -3 | -1.2273 | -0.54545 | 0 | -0.40909 | -0.81818 | -0.40909 | 0.27273 | 0 | -0.13636 | -0.81818 | -0.40909 | 0.13636 | 0 | -1.2273 | -0.81818 | -0.81818 | -1.9091 | -2.0455
TSO | - | 42 | 2020 | Summer | Pc, [MW] | 0 | 0 | 4.4265 | 4.0321 | 3.4623 | 3.813 | 3.9444 | 4.2074 | 5.7414 | 6.7056 | 7.1 | 6.9685 | 6.2673 | 7.1 | 6.9247 | 6.7932 | 5.7414 | 5.566 | 5.4784 | 5.4346 | 5.3469 | 5.9167 | 5.9605 | 6.3549 | 5.7852 | 4.9525
TSO | - | 42 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.21664 | 0.18795 | 0.13618 | 0.15891 | 0.16056 | 0.18606 | 0.45436 | 0.55328 | 0.51143 | 0.41048 | 0.3823 | 0.3951 | 0.5296 | 0.51325 | 0.32326 | 0.28858 | 0.28413 | 0.32777 | 0.28411 | 0.30025 | 0.28948 | 0.29424 | 0.31141 | 0.27705
TSO | - | 42 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.20104 | 0.18151 | 0.12996 | 0.14401 | 0.15188 | 0.17578 | 0.40265 | 0.56196 | 0.57709 | 0.43561 | 0.40465 | 0.4233 | 0.58242 | 0.55225 | 0.30508 | 0.26726 | 0.27071 | 0.30658 | 0.2681 | 0.32233 | 0.30558 | 0.28083 | 0.28901 | 0.23684
TSO | - | 42 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 4.4421 | 4.0385 | 3.4686 | 3.8279 | 3.9531 | 4.2177 | 5.7931 | 6.6969 | 7.0343 | 6.9434 | 6.2449 | 7.0718 | 6.8719 | 6.7542 | 5.7595 | 5.5874 | 5.4918 | 5.4558 | 5.3629 | 5.8946 | 5.9444 | 6.3683 | 5.8076 | 4.9927
TSO | - | 42 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -1.8 | -2.4 | -2.6 | -2.2 | -2 | -1.8 | -0.4 | 3 | 3 | 3.6 | 2.8 | 4 | 4.4 | 4.2 | 3.4 | 2.6 | 1.8 | 1.6 | 1.4 | 1.8 | 1.6 | 1 | 0.6 | -0.4
TSO | - | 43 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.3333 | 1.3333 | 1.6667 | 0.33333 | 0.66667 | 1.6667 | 1.3333 | 0.66667 | 0 | -2 | -2 | -1.6667 | -1.6667 | -1 | 0.66667 | 0.66667 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | -1 | -0.33333
TSO | - | 43 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.063379 | 0.060719 | 0.064337 | 0.013276 | 0.026473 | 0.071885 | 0.10009 | 0.055176 | 0 | 0.083491 | 0.091226 | 0.081007 | 0.041255 | 0.024274 | 0.036487 | 0.033301 | 0 | 0 | 0.017236 | 0.017487 | 0.016587 | 0.015098 | 0.048258 | 0.015114
TSO | - | 43 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.062431 | 0.061455 | 0.063774 | 0.013206 | 0.026335 | 0.07145 | 0.098933 | 0.055701 | 0 | 0.083769 | 0.091872 | 0.081537 | 0.041402 | 0.024309 | 0.036474 | 0.033275 | 0 | 0 | 0.01719 | 0.017588 | 0.016691 | 0.015066 | 0.04858 | 0.015121
TSO | - | 43 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.3343 | 1.3326 | 1.6672 | 0.3334 | 0.66681 | 1.6671 | 1.3345 | 0.66614 | 0 | -2.0003 | -2.0006 | -1.6672 | -1.6668 | -1 | 0.66668 | 0.66669 | 0 | 0 | 0.33338 | 0.33323 | 0.33323 | 0.33336 | -1.0003 | -0.33334
TSO | - | 43 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.73077 | 0.65385 | 0.30769 | 0.53846 | 0.57692 | 0.30769 | 0.88462 | 0.69231 | 0.73077 | 0.88462 | 0.84615 | 0.96154 | 1 | 0.96154 | 0.80769 | 0.88462 | 0.96154 | 0.96154 | 0.88462 | 0.84615 | 0.92308 | 0.92308 | 0.88462 | 0.96154
TSO | - | 44 | 2020 | Summer | Pc, [MW] | 0 | 0 | 7.5765 | 7.1059 | 6.8235 | 6.7294 | 6.9176 | 6.6353 | 7.9059 | 9.0353 | 9.5059 | 9.8824 | 10.6353 | 12 | 8.0471 | 10.8235 | 10.2588 | 9.9765 | 10.4471 | 9.9294 | 9.0353 | 9.3647 | 9.4118 | 9.9765 | 8.0471 | 7.3412
TSO | - | 44 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.36509 | 0.32557 | 0.2638 | 0.27172 | 0.27794 | 0.28401 | 0.58379 | 0.76633 | 0.74137 | 0.57417 | 0.67233 | 0.66334 | 0.63948 | 0.83344 | 0.56816 | 0.50375 | 0.53541 | 0.59289 | 0.45509 | 0.47671 | 0.44845 | 0.44424 | 0.43349 | 0.42258
TSO | - | 44 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.34981 | 0.32554 | 0.2607 | 0.2629 | 0.27002 | 0.28663 | 0.59633 | 0.73638 | 0.716 | 0.6257 | 0.6631 | 0.71986 | 0.65278 | 0.86421 | 0.55458 | 0.49254 | 0.52264 | 0.56612 | 0.47804 | 0.5087 | 0.49116 | 0.45855 | 0.40169 | 0.33918
TSO | - | 44 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 7.5917 | 7.1059 | 6.8266 | 6.7382 | 6.9256 | 6.6327 | 7.8933 | 9.0653 | 9.5313 | 9.8308 | 10.6445 | 11.9435 | 8.0338 | 10.7928 | 10.2724 | 9.9877 | 10.4598 | 9.9562 | 9.0123 | 9.3327 | 9.3691 | 9.9622 | 8.0789 | 7.4246
TSO | - | 44 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.52941 | -0.84706 | -0.84706 | -0.95294 | -0.74118 | -1.3765 | -0.84706 | 0.42353 | 1.3765 | 1.2706 | 0.63529 | 1.8 | 1.3765 | 1.8 | 1.6941 | 0.63529 | 1.1647 | 0.74118 | 0.52941 | 0.63529 | 0.63529 | 0.31765 | -0.31765 | -1.2706
TSO | - | 45 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 47 | 2020 | Summer | Pc, [MW] | 0 | 0 | -1.4975 | -8.1529 | -9.4008 | -10.2328 | -6.0731 | -11.0647 | -3.5773 | -4.8252 | -6.0731 | 2.6622 | 4.3261 | 7.2378 | 18.4689 | 29.7 | 28.4521 | 26.3723 | 24.7084 | 23.8765 | 11.3975 | 13.8933 | 22.2126 | 26.3723 | 26.3723 | 28.8681
TSO | - | 47 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.068009 | 0.2717 | 0.22197 | 0.25341 | 0.14014 | 0.38688 | 0.1919 | 0.20918 | 0.16196 | 0.15976 | 0.26561 | 0.40834 | 1.4936 | 2.4026 | 1.6127 | 1.3775 | 1.3232 | 1.5265 | 0.57553 | 0.70264 | 0.98242 | 1.0859 | 1.3422 | 1.403
TSO | - | 47 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.067804 | 0.26785 | 0.21912 | 0.24687 | 0.13892 | 0.38899 | 0.19196 | 0.2071 | 0.16196 | 0.16347 | 0.27759 | 0.42594 | 1.4723 | 2.2558 | 1.5011 | 1.2561 | 1.1792 | 1.2605 | 0.60156 | 0.75929 | 1.2352 | 1.3006 | 1.3949 | 1.5925
TSO | - | 47 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | -1.4973 | -8.1491 | -9.398 | -10.2262 | -6.0719 | -11.0668 | -3.5774 | -4.8231 | -6.0731 | 2.6585 | 4.3141 | 7.2202 | 18.4903 | 29.8468 | 28.5637 | 26.4937 | 24.8524 | 24.1424 | 11.3714 | 13.8366 | 21.9599 | 26.1575 | 26.3196 | 28.6785
TSO | - | 47 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -4.6 | -5.6 | -6.6 | -9.6 | -10.1 | -11.6 | -8.1 | -0.1 | 2.9 | 7.9 | 7.4 | 4.9 | 2.9 | -1.6 | -0.6 | -3.1 | -3.1 | -4.1 | -0.1 | -1.1 | -4.1 | -5.1 | -5.1 | -7.6
TSO | - | 48 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 49 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.6875 | 18 | 9 | 1.4062 | 1.4062 | 1.6875 | 1.125 | 0.5625 | 1.125 | 10.6875 | 0.84375 | 2.25 | 1.125 | 1.4062 | 5.0625 | 1.4062 | 1.125 | 1.125 | 3.375 | 0.5625 | 1.125 | 0.5625 | 1.125 | 0.5625
TSO | - | 49 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.079607 | 0.85444 | 0.35121 | 0.055921 | 0.055731 | 0.072436 | 0.083595 | 0.046693 | 0.085673 | 0.63723 | 0.052934 | 0.12898 | 0.088958 | 0.10822 | 0.26742 | 0.069578 | 0.056555 | 0.065057 | 0.16883 | 0.029396 | 0.055451 | 0.025332 | 0.057964 | 0.029077
TSO | - | 49 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.079622 | 0.79491 | 0.34059 | 0.055798 | 0.05566 | 0.07269 | 0.084334 | 0.04686 | 0.086803 | 0.6604 | 0.053012 | 0.13037 | 0.091704 | 0.11235 | 0.28663 | 0.070855 | 0.057382 | 0.066259 | 0.17973 | 0.029793 | 0.056863 | 0.02557 | 0.058797 | 0.029291
TSO | - | 49 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.6875 | 18.0595 | 9.0106 | 1.4064 | 1.4063 | 1.6872 | 1.1243 | 0.56233 | 1.1239 | 10.6643 | 0.84367 | 2.2486 | 1.1223 | 1.4021 | 5.0433 | 1.405 | 1.1242 | 1.1238 | 3.3641 | 0.5621 | 1.1236 | 0.56226 | 1.1242 | 0.56229
TSO | - | 49 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.1591 | 8.5 | 4.6364 | 1.1591 | 0.57955 | 1.1591 | 1.1591 | 1.9318 | 1.9318 | 6.375 | 1.3523 | 2.8977 | 1.1591 | 1.9318 | 5.2159 | 1.7386 | 1.3523 | 1.1591 | 0 | 0.77273 | 0.77273 | 1.5455 | 0 | 0
TSO | - | 50 | 2020 | Summer | Pc, [MW] | 0 | 0 | 14.7153 | 13.6423 | 13.3358 | 13.6423 | 13.5657 | 13.4124 | 14.562 | 18.7007 | 20.4635 | 19.6204 | 20.2336 | 20.9234 | 20.6168 | 21 | 18.854 | 19.3905 | 19.0073 | 19.4672 | 19.3905 | 19.927 | 19.927 | 20.4635 | 18.6241 | 17.0146
TSO | - | 50 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.73961 | 0.67424 | 0.54801 | 0.56888 | 0.56597 | 0.59705 | 1.1369 | 1.6704 | 1.5789 | 1.2752 | 1.3696 | 1.2564 | 1.5097 | 1.5061 | 1.0562 | 0.97763 | 0.96892 | 1.1188 | 0.93451 | 0.94091 | 0.89793 | 0.87185 | 0.95153 | 0.87084
TSO | - | 50 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.64889 | 0.57581 | 0.47707 | 0.51493 | 0.50859 | 0.55643 | 1.0367 | 1.4399 | 1.5584 | 1.107 | 1.1711 | 1.1554 | 1.8011 | 1.7877 | 1.0072 | 0.95878 | 0.95609 | 1.1535 | 1.0681 | 1.1559 | 1.0915 | 0.97994 | 0.98142 | 0.89469
TSO | - | 50 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 14.8061 | 13.7408 | 13.4067 | 13.6963 | 13.6231 | 13.453 | 14.6622 | 18.9312 | 20.484 | 19.7886 | 20.4321 | 21.0243 | 20.3254 | 20.7184 | 18.9031 | 19.4094 | 19.0201 | 19.4324 | 19.2569 | 19.712 | 19.7335 | 20.3554 | 18.5942 | 16.9908
TSO | - | 50 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -4.375 | -7.875 | -7.875 | -6.5625 | -6.5625 | -8.75 | -5.6875 | 4.8125 | 10.5 | 5.6875 | 9.625 | 10.5 | 10.5 | 10.0625 | 1.3125 | 3.0625 | 4.375 | 7.875 | 8.3125 | 3.9375 | 3.5 | 1.75 | 0.875 | -0.4375
TSO | - | 51 | 2020 | Summer | Pc, [MW] | 0 | 0 | 12.2026 | 12.1091 | 11.1273 | 11.7351 | 10.613 | 11.7818 | 14.587 | 17.7662 | 17.2987 | 18 | 16.7844 | 17.7195 | 17.439 | 17.813 | 17.439 | 15.6156 | 15.8961 | 15.7091 | 15.7558 | 16.4104 | 15.9896 | 16.0364 | 14.4468 | 13.9792
TSO | - | 51 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.5844 | 0.55901 | 0.4415 | 0.47459 | 0.4338 | 0.52805 | 1.1275 | 1.327 | 1.3574 | 1.1349 | 1.1076 | 1.0501 | 1.3916 | 1.3861 | 0.98056 | 0.79017 | 0.81687 | 0.92846 | 0.79575 | 0.81712 | 0.76255 | 0.70774 | 0.7338 | 0.70325
TSO | - | 51 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.56701 | 0.55055 | 0.41382 | 0.4577 | 0.40687 | 0.4852 | 1.0499 | 1.6278 | 1.2947 | 1.0506 | 0.99991 | 0.99241 | 1.4089 | 1.4078 | 0.92798 | 0.76926 | 0.79304 | 0.90519 | 0.83146 | 0.90967 | 0.83376 | 0.74342 | 0.76559 | 0.74731
TSO | - | 51 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 12.22 | 12.1175 | 11.155 | 11.7519 | 10.6399 | 11.8247 | 14.6646 | 17.4654 | 17.3615 | 18.0843 | 16.8921 | 17.7771 | 17.4217 | 17.7913 | 17.4915 | 15.6365 | 15.9199 | 15.7324 | 15.7201 | 16.3178 | 15.9184 | 16.0007 | 14.415 | 13.9352
TSO | - | 51 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -3.71 | -3.5775 | -4.9025 | -4.9025 | -5.3 | -4.3725 | -0.53 | 3.3125 | 3.445 | 3.0475 | 2.7825 | 4.6375 | 4.1075 | 4.24 | -2.7825 | 1.1925 | 1.06 | 0.3975 | -0.6625 | 0 | -0.53 | -1.06 | -2.5175 | -3.445
TSO | - | 52 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.3677 | 2.9694 | 2.7617 | 2.7011 | 2.7617 | 2.5625 | 3.0647 | 3.7226 | 4.1382 | 4.32 | 4.6489 | 4.8307 | 4.7615 | 4.9 | 4.5537 | 4.6143 | 4.4585 | 4.5624 | 4.3027 | 4.2853 | 4.2767 | 4.5624 | 4.5451 | 3.9304
TSO | - | 52 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.16567 | 0.14511 | 0.1054 | 0.11442 | 0.10725 | 0.10667 | 0.24203 | 0.31338 | 0.31326 | 0.26046 | 0.28855 | 0.26473 | 0.36878 | 0.37633 | 0.24687 | 0.22906 | 0.22709 | 0.26735 | 0.22585 | 0.22873 | 0.21587 | 0.20662 | 0.23467 | 0.20737
TSO | - | 52 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.15209 | 0.12698 | 0.10688 | 0.10016 | 0.1115 | 0.11371 | 0.21543 | 0.30575 | 0.32117 | 0.26405 | 0.29519 | 0.2921 | 0.39586 | 0.39222 | 0.25149 | 0.23174 | 0.22445 | 0.26519 | 0.21851 | 0.2222 | 0.21109 | 0.20623 | 0.23704 | 0.20047
TSO | - | 52 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.3812 | 2.9876 | 2.7602 | 2.7153 | 2.7574 | 2.5555 | 3.0913 | 3.7303 | 4.1302 | 4.3164 | 4.6423 | 4.8034 | 4.7344 | 4.8841 | 4.5491 | 4.6116 | 4.4611 | 4.5645 | 4.31 | 4.2919 | 4.2815 | 4.5628 | 4.5427 | 3.9373
TSO | - | 52 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.14348 | -0.23913 | -0.40652 | -0.40652 | -0.38261 | -0.9087 | -0.43043 | 0.47826 | 0.52609 | 1.6261 | 1.5065 | 2.0565 | 2.2 | 1.9609 | 1.363 | 1.1478 | 0.98043 | 1.1717 | 0.71739 | 0.78913 | 0.52609 | 0.86087 | 0.64565 | 0.28696
TSO | - | 53 | 2020 | Summer | Pc, [MW] | 0 | 0 | 5.2239 | 2.0896 | 2.8358 | 2.3881 | 0.59701 | 1.0448 | 5.5224 | 12.2388 | 15.3731 | 16.4179 | 16.4179 | 19.2537 | 18.5075 | 19.2537 | 18.3582 | 15.9701 | 15.5224 | 15.2239 | 14.7761 | 14.4776 | 15.5224 | 18.9552 | 20 | 13.8806
TSO | - | 53 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.27255 | 0.10182 | 0.10924 | 0.1036 | 0.023608 | 0.044831 | 0.48496 | 1.1155 | 1.1685 | 1.0105 | 1.0181 | 0.86535 | 1.2855 | 1.3999 | 0.99345 | 0.80584 | 0.83534 | 0.93894 | 0.83471 | 0.82709 | 0.83303 | 0.87903 | 1.0099 | 0.78662
TSO | - | 53 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.22036 | 0.089644 | 0.10874 | 0.08612 | 0.023683 | 0.045021 | 0.33937 | 0.91999 | 1.1884 | 0.98287 | 1.0434 | 1.354 | 1.6866 | 1.62 | 1.0157 | 0.789 | 0.73673 | 0.83807 | 0.69132 | 0.69632 | 0.71664 | 0.83627 | 1.0659 | 0.6537
TSO | - | 53 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 5.2761 | 2.1017 | 2.8363 | 2.4055 | 0.59694 | 1.0446 | 5.668 | 12.4343 | 15.3532 | 16.4456 | 16.3926 | 18.7651 | 18.1064 | 19.0336 | 18.336 | 15.987 | 15.621 | 15.3247 | 14.9195 | 14.6084 | 15.6388 | 18.998 | 19.944 | 14.0135
TSO | - | 53 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 3.7931 | 2.7586 | 3.1034 | 1.7241 | 1.7241 | -0.68966 | 2.4138 | 7.5862 | 7.5862 | 7.931 | 7.931 | 10 | 9.3103 | 8.9655 | 8.2759 | 6.2069 | 5.8621 | 6.5517 | 5.8621 | 6.2069 | 5.5172 | 6.8966 | 7.5862 | 5.8621
TSO | - | 54 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.3594 | 1.3675 | 1.3838 | 1.3946 | 1.3973 | 1.4 | 1.3689 | 1.3202 | 1.2972 | 1.258 | 1.2674 | 1.2526 | 1.2674 | 1.2647 | 1.281 | 1.3053 | 1.308 | 1.3013 | 1.3107 | 1.2999 | 1.3215 | 1.3067 | 1.3121 | 1.3175
TSO | - | 55 | 2020 | Summer | Pc, [MW] | 0 | 0 | 4.1413 | 5.4953 | 6.8 | 5.8512 | 5.4163 | 4.2401 | 2.5105 | 0.94884 | 0.46453 | -0.57326 | -0.3657 | -1.1959 | -1.4727 | -1.868 | -0.87965 | -0.12849 | 0.67209 | 0.81047 | 1.957 | 1.9965 | 1.3738 | 0.62267 | 1.186 | 1.3145
TSO | - | 55 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.19218 | 0.24204 | 0.27339 | 0.22437 | 0.22376 | 0.19168 | 0.18479 | 0.078156 | 0.035451 | 0.023904 | 0.016703 | 0.057821 | 0.036332 | 0.045121 | 0.040245 | 0.0058285 | 0.033912 | 0.04706 | 0.099978 | 0.10339 | 0.067866 | 0.028087 | 0.061021 | 0.067664
TSO | - | 55 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.19858 | 0.2615 | 0.2493 | 0.24047 | 0.20527 | 0.17297 | 0.18995 | 0.079651 | 0.035768 | 0.024037 | 0.016777 | 0.058814 | 0.036704 | 0.045632 | 0.040579 | 0.0058353 | 0.034156 | 0.047542 | 0.10213 | 0.10669 | 0.06929 | 0.02826 | 0.062076 | 0.06874
TSO | - | 55 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 4.1349 | 5.4759 | 6.8241 | 5.8351 | 5.4348 | 4.2588 | 2.5053 | 0.94734 | 0.46422 | -0.57339 | -0.36577 | -1.1969 | -1.473 | -1.8685 | -0.87998 | -0.1285 | 0.67185 | 0.80998 | 1.9548 | 1.9932 | 1.3724 | 0.6225 | 1.185 | 1.3135
TSO | - | 55 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 2.2599 | 1.5436 | 1.4226 | 1.5234 | 1.9068 | 1.8564 | 2.2095 | 1.9068 | 1.8059 | 2.1994 | 2.4214 | 2.3306 | 2.603 | 2.6938 | 2.5929 | 3.0065 | 3.2083 | 3.4 | 3.0872 | 3.1276 | 3.0973 | 2.6837 | 3.0772 | 3.3697
TSO | - | 56 | 2020 | Summer | Pc, [MW] | 0 | 0 | 6.6263 | 6.5075 | 5.9612 | 5.9137 | 5.8425 | 6.08 | 6.1275 | 6.65 | 6.9587 | 6.935 | 6.6975 | 6.46 | 6.0325 | 6.1037 | 5.6287 | 5.7475 | 5.9375 | 6.1037 | 6.745 | 7.6 | 6.745 | 7.0537 | 6.7687 | 5.3675
TSO | - | 56 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.33401 | 0.30255 | 0.24443 | 0.2651 | 0.26179 | 0.29086 | 0.49247 | 0.51331 | 0.50654 | 0.40538 | 0.40708 | 0.36329 | 0.45197 | 0.44885 | 0.30989 | 0.29194 | 0.30698 | 0.36528 | 0.34612 | 0.36179 | 0.31552 | 0.31887 | 0.35906 | 0.31081
TSO | - | 56 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.29123 | 0.29374 | 0.21379 | 0.20472 | 0.20101 | 0.23202 | 0.42219 | 0.59268 | 0.56032 | 0.43664 | 0.43389 | 0.38134 | 0.51678 | 0.50851 | 0.30613 | 0.28203 | 0.29436 | 0.34719 | 0.35048 | 0.43792 | 0.35787 | 0.31944 | 0.34345 | 0.24615
TSO | - | 56 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 6.669 | 6.5163 | 5.9919 | 5.9741 | 5.9033 | 6.1388 | 6.1978 | 6.5706 | 6.905 | 6.9037 | 6.6707 | 6.4419 | 5.9677 | 6.0441 | 5.6325 | 5.7574 | 5.9501 | 6.1218 | 6.7406 | 7.5239 | 6.7027 | 7.0532 | 6.7844 | 5.4322
TSO | - | 56 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -1.9038 | -1.9673 | -1.925 | -1.9673 | -1.9462 | -2.2 | -1.8404 | -0.67692 | -0.50769 | -0.31731 | -0.35962 | 0.10577 | 0.35962 | 0.33846 | -0.084615 | -0.63462 | -0.40192 | -0.61346 | -0.93077 | -0.63462 | -1.0154 | -0.67692 | -1.1212 | -1.2692
TSO | - | 57 | 2020 | Summer | Pc, [MW] | 0 | 0 | 3.5175 | 2.948 | 2.5125 | 2.412 | 2.412 | 2.8475 | 3.9865 | 4.422 | 5.3265 | 5.5945 | 5.762 | 6.231 | 6.7 | 6.5325 | 6.298 | 5.9965 | 5.628 | 5.5945 | 5.293 | 5.5275 | 5.5275 | 5.762 | 5.36 | 4.0535
TSO | - | 57 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.18411 | 0.14502 | 0.10336 | 0.10123 | 0.099258 | 0.12617 | 0.31919 | 0.37029 | 0.41944 | 0.33841 | 0.35874 | 0.35161 | 0.48345 | 0.46444 | 0.34156 | 0.30318 | 0.29292 | 0.33791 | 0.27511 | 0.27497 | 0.26419 | 0.26164 | 0.28784 | 0.23644
TSO | - | 57 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.14779 | 0.12511 | 0.089769 | 0.090394 | 0.091801 | 0.11872 | 0.27588 | 0.36516 | 0.39718 | 0.34085 | 0.36476 | 0.36662 | 0.59249 | 0.56017 | 0.3477 | 0.29565 | 0.27707 | 0.31511 | 0.27153 | 0.30666 | 0.28764 | 0.25977 | 0.26846 | 0.18418
TSO | - | 57 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 3.5538 | 2.9679 | 2.5261 | 2.4228 | 2.4195 | 2.855 | 4.0298 | 4.4271 | 5.3488 | 5.5921 | 5.756 | 6.216 | 6.591 | 6.4368 | 6.2919 | 6.004 | 5.6438 | 5.6173 | 5.2966 | 5.4958 | 5.5041 | 5.7639 | 5.3794 | 4.1058
TSO | - | 57 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -1.0968 | -1.2903 | -1.3548 | -1.4194 | -1.3548 | -2 | -1.5161 | -0.77419 | -0.22581 | -0.096774 | 0.032258 | 0.032258 | 0.48387 | 0.45161 | 0.45161 | -0.19355 | -0.032258 | -0.19355 | -0.54839 | -0.51613 | -0.48387 | -0.35484 | -0.54839 | -0.83871
TSO | - | 1 | 2020 | Summer | Pc, [MW] | Expected | - | 5.1562 | 55 | 27.5 | 4.2969 | 4.2969 | 5.1562 | 3.4375 | 1.7188 | 3.4375 | 32.6562 | 2.5781 | 6.875 | 3.4375 | 4.2969 | 15.4688 | 4.2969 | 3.4375 | 3.4375 | 10.3125 | 1.7188 | 3.4375 | 1.7188 | 3.4375 | 1.7188
TSO | - | 1 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.24327 | 2.5198 | 1.0569 | 0.17068 | 0.17018 | 0.22172 | 0.25656 | 0.14293 | 0.26351 | 1.9825 | 0.16186 | 0.39623 | 0.27601 | 0.33698 | 0.84646 | 0.21455 | 0.17407 | 0.20062 | 0.53252 | 0.090428 | 0.17159 | 0.077767 | 0.17838 | 0.089173
TSO | - | 1 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.24327 | 2.5198 | 1.0569 | 0.17068 | 0.17018 | 0.22172 | 0.25656 | 0.14293 | 0.26351 | 1.9825 | 0.16186 | 0.39623 | 0.27601 | 0.33698 | 0.84646 | 0.21455 | 0.17407 | 0.20062 | 0.53252 | 0.090428 | 0.17159 | 0.077767 | 0.17838 | 0.089173
TSO | - | 1 | 2020 | Summer | Pc_net, [MW] | Expected | - | 5.1562 | 55 | 27.5 | 4.2969 | 4.2969 | 5.1562 | 3.4375 | 1.7188 | 3.4375 | 32.6562 | 2.5781 | 6.875 | 3.4375 | 4.2969 | 15.4688 | 4.2969 | 3.4375 | 3.4375 | 10.3125 | 1.7188 | 3.4375 | 1.7188 | 3.4375 | 1.7188
TSO | - | 1 | 2020 | Summer | Qc, [MVAr] | Expected | - | 2.3182 | 17 | 9.2727 | 2.3182 | 1.1591 | 2.3182 | 2.3182 | 3.8636 | 3.8636 | 12.75 | 2.7045 | 5.7955 | 2.3182 | 3.8636 | 10.4318 | 3.4773 | 2.7045 | 2.3182 | 0 | 1.5455 | 1.5455 | 3.0909 | 0 | 0
TSO | - | 2 | 2020 | Summer | Pc, [MW] | Expected | - | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
TSO | - | 2 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 2 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 2 | 2020 | Summer | Pc_net, [MW] | Expected | - | 7.7545 | 7.3126 | 6.6642 | 6.8058 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.524 | 9.4179 | 9.3925 | 9.7543 | 10.4721 | 10.5048 | 9.5242 | 8.3131
TSO | - | 2 | 2020 | Summer | Qc, [MVAr] | Expected | - | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8578 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6312 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
TSO | - | 3 | 2020 | Summer | Pc, [MW] | Expected | - | 27.7948 | 27.5818 | 25.3455 | 26.7299 | 24.174 | 26.8364 | 33.226 | 40.4675 | 39.4026 | 41 | 38.2312 | 40.361 | 39.7221 | 40.574 | 39.7221 | 35.5688 | 36.2078 | 35.7818 | 35.8883 | 37.3792 | 36.4208 | 36.5273 | 32.9065 | 31.8416
TSO | - | 3 | 2020 | Summer | Flex Up, [MW] | Expected | - | 1.341 | 1.2839 | 0.99658 | 1.1035 | 0.9819 | 1.2044 | 2.5641 | 2.9952 | 2.9787 | 2.4638 | 2.3519 | 2.3472 | 3.2303 | 3.1512 | 2.2046 | 1.803 | 1.8296 | 2.0855 | 1.8874 | 1.9828 | 1.8345 | 1.6809 | 1.72 | 1.6742
TSO | - | 3 | 2020 | Summer | Flex Down, [MW] | Expected | - | 1.2817 | 1.2434 | 0.95164 | 1.0201 | 0.93297 | 1.1035 | 2.3955 | 3.7351 | 3.0622 | 2.5142 | 2.4486 | 2.3051 | 3.1486 | 3.2127 | 2.1426 | 1.7491 | 1.8374 | 2.0911 | 1.819 | 1.9505 | 1.8016 | 1.6245 | 1.6953 | 1.6299
TSO | - | 3 | 2020 | Summer | Pc_net, [MW] | Expected | - | 27.8541 | 27.6223 | 25.3904 | 26.8132 | 24.223 | 26.9373 | 33.3946 | 39.7276 | 39.319 | 40.9496 | 38.1345 | 40.4031 | 39.8039 | 40.5126 | 39.7841 | 35.6227 | 36.2 | 35.7762 | 35.9568 | 37.4115 | 36.4537 | 36.5837 | 32.9311 | 31.8859
TSO | - | 3 | 2020 | Summer | Qc, [MVAr] | Expected | - | -14.7 | -14.175 | -19.425 | -19.425 | -21 | -17.325 | -2.1 | 13.125 | 13.65 | 12.075 | 11.025 | 18.375 | 16.275 | 16.8 | -11.025 | 4.725 | 4.2 | 1.575 | -2.625 | 0 | -2.1 | -4.2 | -9.975 | -13.65
TSO | - | 4 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 4 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 5 | 2020 | Summer | Pc, [MW] | Expected | - | 3.3955 | 1.3582 | 1.8433 | 1.5522 | 0.38806 | 0.6791 | 3.5896 | 7.9552 | 9.9925 | 10.6716 | 10.6716 | 12.5149 | 12.0299 | 12.5149 | 11.9328 | 10.3806 | 10.0896 | 9.8955 | 9.6045 | 9.4104 | 10.0896 | 12.3209 | 13 | 9.0224
TSO | - | 5 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.15718 | 0.062034 | 0.069528 | 0.06029 | 0.0153 | 0.028953 | 0.26196 | 0.70574 | 0.77359 | 0.64419 | 0.66697 | 0.71893 | 0.95696 | 0.95959 | 0.64662 | 0.51567 | 0.5001 | 0.56574 | 0.49915 | 0.5133 | 0.52331 | 0.55444 | 0.67038 | 0.46614
TSO | - | 5 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.16321 | 0.062419 | 0.07216 | 0.063028 | 0.015439 | 0.029451 | 0.27385 | 0.61734 | 0.75839 | 0.65152 | 0.67301 | 0.72363 | 0.97489 | 1.0033 | 0.65932 | 0.52097 | 0.52174 | 0.58931 | 0.49276 | 0.47692 | 0.48397 | 0.5605 | 0.67885 | 0.47007
TSO | - | 5 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.3895 | 1.3578 | 1.8407 | 1.5495 | 0.38792 | 0.67861 | 3.5777 | 8.0436 | 10.0077 | 10.6643 | 10.6656 | 12.5102 | 12.0119 | 12.4712 | 11.9201 | 10.3753 | 10.0679 | 9.872 | 9.6109 | 9.4468 | 10.1289 | 12.3148 | 12.9915 | 9.0185
TSO | - | 5 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.5172 | 1.1034 | 1.2414 | 0.68966 | 0.68966 | -0.27586 | 0.96552 | 3.0345 | 3.0345 | 3.1724 | 3.1724 | 4 | 3.7241 | 3.5862 | 3.3103 | 2.4828 | 2.3448 | 2.6207 | 2.3448 | 2.4828 | 2.2069 | 2.7586 | 3.0345 | 2.3448
TSO | - | 6 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 6 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.942 | 1.9536 | 1.9768 | 1.9923 | 1.9961 | 2 | 1.9556 | 1.886 | 1.8531 | 1.7971 | 1.8106 | 1.7894 | 1.8106 | 1.8068 | 1.83 | 1.8647 | 1.8686 | 1.8589 | 1.8725 | 1.857 | 1.8879 | 1.8667 | 1.8744 | 1.8821
TSO | - | 7 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 7 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 8 | 2020 | Summer | Pc, [MW] | Expected | - | 130.7812 | 128.4375 | 117.6562 | 116.7188 | 115.3125 | 120 | 120.9375 | 131.25 | 137.3438 | 136.875 | 132.1875 | 127.5 | 119.0625 | 120.4688 | 111.0938 | 113.4375 | 117.1875 | 120.4688 | 133.125 | 150 | 133.125 | 139.2188 | 133.5938 | 105.9375
TSO | - | 8 | 2020 | Summer | Flex Up, [MW] | Expected | - | 6.1955 | 5.9131 | 4.5397 | 4.6697 | 4.5882 | 5.1831 | 9.1091 | 10.8551 | 10.4872 | 8.3003 | 8.2812 | 7.3263 | 9.5371 | 9.4595 | 6.0809 | 5.6695 | 5.9454 | 7.0451 | 6.8683 | 7.8449 | 6.6222 | 6.2813 | 6.9085 | 5.5099
TSO | - | 8 | 2020 | Summer | Flex Down, [MW] | Expected | - | 6.1447 | 5.8557 | 4.5042 | 4.6031 | 4.5459 | 5.137 | 8.9433 | 10.9738 | 10.5693 | 8.3185 | 8.3169 | 7.3703 | 9.5829 | 9.4358 | 6.0774 | 5.6587 | 5.9231 | 7.0166 | 6.8804 | 7.9389 | 6.6682 | 6.3169 | 6.9568 | 5.4827
TSO | - | 8 | 2020 | Summer | Pc_net, [MW] | Expected | - | 130.8321 | 128.4948 | 117.6918 | 116.7853 | 115.3547 | 120.0461 | 121.1033 | 131.1313 | 137.2616 | 136.8569 | 132.1518 | 127.456 | 119.0167 | 120.4925 | 111.0972 | 113.4483 | 117.2098 | 120.4973 | 133.1129 | 149.906 | 133.079 | 139.1832 | 133.5455 | 105.9647
TSO | - | 8 | 2020 | Summer | Qc, [MVAr] | Expected | - | -19.0385 | -19.6731 | -19.25 | -19.6731 | -19.4615 | -22 | -18.4038 | -6.7692 | -5.0769 | -3.1731 | -3.5962 | 1.0577 | 3.5962 | 3.3846 | -0.84615 | -6.3462 | -4.0192 | -6.1346 | -9.3077 | -6.3462 | -10.1538 | -6.7692 | -11.2115 | -12.6923
TSO | - | 9 | 2020 | Summer | Pc, [MW] | Expected | - | 63.525 | 53.24 | 45.375 | 43.56 | 43.56 | 51.425 | 71.995 | 79.86 | 96.195 | 101.035 | 104.06 | 112.53 | 121 | 117.975 | 113.74 | 108.295 | 101.64 | 101.035 | 95.59 | 99.825 | 99.825 | 104.06 | 96.8 | 73.205
TSO | - | 9 | 2020 | Summer | Flex Up, [MW] | Expected | - | 3.2298 | 2.3417 | 2.0182 | 1.8122 | 2.0013 | 2.6735 | 5.9159 | 6.1645 | 6.8716 | 6.2714 | 6.02 | 5.9272 | 8.7155 | 9.4566 | 6.9767 | 5.9578 | 5.5161 | 6.4138 | 5.3542 | 4.4612 | 4.1235 | 5.0337 | 4.7052 | 3.7693
TSO | - | 9 | 2020 | Summer | Flex Down, [MW] | Expected | - | 2.7642 | 2.5367 | 1.4696 | 1.6484 | 1.4492 | 1.7491 | 4.8308 | 7.1175 | 7.8763 | 5.9958 | 7.0463 | 7.0438 | 10.7157 | 9.0475 | 5.4711 | 4.857 | 4.7778 | 5.3795 | 4.5181 | 6.0429 | 5.8425 | 4.3829 | 5.3414 | 3.8269
TSO | - | 9 | 2020 | Summer | Pc_net, [MW] | Expected | - | 63.9906 | 53.045 | 45.9236 | 43.7238 | 44.1121 | 52.3495 | 73.0801 | 78.907 | 95.1903 | 101.3106 | 103.0338 | 111.4134 | 118.9998 | 118.3842 | 115.2455 | 109.3958 | 102.3783 | 102.0693 | 96.4261 | 98.2433 | 98.106 | 104.7108 | 96.1637 | 73.1474
TSO | - | 9 | 2020 | Summer | Qc, [MVAr] | Expected | - | -14.2581 | -16.7742 | -17.6129 | -18.4516 | -17.6129 | -26 | -19.7097 | -10.0645 | -2.9355 | -1.2581 | 0.41935 | 0.41935 | 6.2903 | 5.871 | 5.871 | -2.5161 | -0.41935 | -2.5161 | -7.129 | -6.7097 | -6.2903 | -4.6129 | -7.129 | -10.9032
TSO | - | 10 | 2020 | Summer | Pc, [MW] | Expected | - | 1.8 | 2.1333 | 1.7333 | 2 | 1.3333 | 0.66667 | 1.3333 | 2.6667 | 3.3333 | 2.7333 | 4.1333 | 2.4667 | 2.3333 | 5 | 2.4667 | 3.6667 | 3.5333 | 3.9333 | 2.2 | 2.9333 | 2.0667 | 2.8667 | 3.9333 | 2.0667
TSO | - | 10 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.08506 | 0.097682 | 0.066918 | 0.079609 | 0.053002 | 0.02873 | 0.099752 | 0.21875 | 0.25559 | 0.16642 | 0.26128 | 0.14241 | 0.18724 | 0.39243 | 0.13545 | 0.18369 | 0.17936 | 0.23017 | 0.11349 | 0.15333 | 0.10276 | 0.12942 | 0.20331 | 0.1069
TSO | - | 10 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.084784 | 0.097797 | 0.066318 | 0.079282 | 0.052614 | 0.028604 | 0.099275 | 0.22475 | 0.25545 | 0.16545 | 0.25772 | 0.14192 | 0.18747 | 0.39181 | 0.1345 | 0.18248 | 0.17849 | 0.22895 | 0.11372 | 0.15533 | 0.10357 | 0.12999 | 0.20492 | 0.10755
TSO | - | 10 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.8003 | 2.1332 | 1.7339 | 2.0003 | 1.3337 | 0.66679 | 1.3338 | 2.6607 | 3.3335 | 2.7343 | 4.1369 | 2.4672 | 2.3331 | 5.0006 | 2.4676 | 3.6679 | 3.5342 | 3.9345 | 2.1998 | 2.9313 | 2.0659 | 2.8661 | 3.9317 | 2.066
TSO | - | 10 | 2020 | Summer | Qc, [MVAr] | Expected | - | -2 | -1.9467 | -1.9467 | -1.8667 | -1.8933 | -1.8133 | -1.8933 | -1.6533 | -1.7067 | -1.9467 | -1.92 | -1.7333 | -1.4667 | -1.52 | -2 | -1.6 | -1.7333 | -1.6 | -1.92 | -1.6267 | -1.8667 | -1.5467 | 1.84 | -1.7333
TSO | - | 11 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 11 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 12 | 2020 | Summer | Pc, [MW] | Expected | - | 277.5714 | 252.7143 | 236.1429 | 265.1429 | 281.7143 | 240.2857 | 339.7143 | 306.5714 | 319 | 343.8571 | 294.1429 | 323.1429 | 314.8571 | 298.2857 | 310.7143 | 298.2857 | 331.4286 | 314.8571 | 306.5714 | 360.4286 | 352.1429 | 377 | 327.2857 | 343.8571
TSO | - | 12 | 2020 | Summer | Flex Up, [MW] | Expected | - | 13.6976 | 12.2454 | 9.4649 | 11.0166 | 11.6249 | 10.8563 | 25.5275 | 27.2344 | 25.8211 | 21.4079 | 19.5497 | 18.8737 | 25.5151 | 23.3602 | 16.7607 | 14.459 | 16.6909 | 18.5765 | 15.0646 | 17.8573 | 16.6277 | 11.1391 | 17.2949 | 18.3564
TSO | - | 12 | 2020 | Summer | Flex Down, [MW] | Expected | - | 12.4934 | 10.9109 | 8.6866 | 10.0477 | 10.6901 | 9.8085 | 25.1818 | 23.7532 | 23.0856 | 20.3418 | 17.3844 | 18.3741 | 25.0472 | 23.4252 | 17.2442 | 15.3289 | 16.8753 | 18.1753 | 16.5971 | 20.0689 | 18.5282 | 22.9764 | 16.6732 | 17.3241
TSO | - | 12 | 2020 | Summer | Pc_net, [MW] | Expected | - | 278.7756 | 254.0488 | 236.9211 | 266.1117 | 282.6491 | 241.3335 | 340.06 | 310.0526 | 321.7355 | 344.9233 | 296.3082 | 323.6424 | 315.325 | 298.2206 | 310.2308 | 297.4157 | 331.2442 | 315.2584 | 305.039 | 358.2169 | 350.2423 | 365.1626 | 327.9075 | 344.8894
TSO | - | 12 | 2020 | Summer | Qc, [MVAr] | Expected | - | -17.6 | -19.2 | -20.8 | -20.8 | -20.8 | -24 | -17.6 | -6.4 | -3.2 | 1.6 | 0 | 3.2 | 0 | 0 | 1.6 | -9.6 | -9.6 | -11.2 | -12.8 | -12.8 | -16 | -14.4 | -16 | -16
TSO | - | 13 | 2020 | Summer | Pc, [MW] | Expected | - | 6.75 | 4.5 | 0 | 6.75 | 0 | -18 | -6.75 | -4.5 | 6.75 | -6.75 | 6.75 | -9 | -11.25 | 15.75 | -11.25 | 15.75 | 6.75 | 4.5 | -11.25 | 2.25 | -6.75 | -2.25 | 13.5 | 4.5
TSO | - | 13 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.31891 | 0.20807 | 0 | 0.2685 | 0 | 0.63586 | 0.36248 | 0.19392 | 0.51752 | 0.28264 | 0.42465 | 0.43717 | 0.27778 | 1.2202 | 0.51784 | 0.7819 | 0.34215 | 0.26283 | 0.074726 | 0.11831 | 0.079672 | 0.073056 | 0.71072 | 0.23549
TSO | - | 13 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.31801 | 0.20427 | 0 | 0.26775 | 0 | 0.62632 | 0.36182 | 0.1943 | 0.51734 | 0.28186 | 0.42292 | 0.44057 | 0.28015 | 1.2501 | 0.51583 | 0.79095 | 0.34147 | 0.26244 | 0.074923 | 0.11845 | 0.079685 | 0.073399 | 0.69041 | 0.23146
TSO | - | 13 | 2020 | Summer | Pc_net, [MW] | Expected | - | 6.7509 | 4.5038 | 0 | 6.7507 | 0 | -17.9905 | -6.7493 | -4.5004 | 6.7502 | -6.7492 | 6.7517 | -9.0034 | -11.2524 | 15.7201 | -11.248 | 15.741 | 6.7507 | 4.5004 | -11.2502 | 2.2499 | -6.75 | -2.2503 | 13.5203 | 4.504
TSO | - | 13 | 2020 | Summer | Qc, [MVAr] | Expected | - | -2.0579 | -2.0579 | -2.1789 | -2.1789 | -2.1789 | -2.3 | -1.9368 | -1.3316 | -1.9368 | -1.8158 | -1.9368 | -1.4526 | -1.2105 | -1.4526 | -1.0895 | -1.6947 | -1.5737 | -1.3316 | -2.1789 | -1.6947 | -1.8158 | -1.3316 | -1.8158 | -1.6947
TSO | - | 14 | 2020 | Summer | Pc, [MW] | Expected | - | 8.0902 | 7.7459 | 7.7459 | 8.6066 | 7.7459 | 7.4016 | 7.4016 | 7.5738 | 7.918 | 7.4016 | 9.4672 | 7.4016 | 9.2951 | 9.8115 | 9.6393 | 9.9836 | 9.6393 | 10.5 | 7.4016 | 6.541 | 6.541 | 6.8852 | 7.2295 | 0.51639
TSO | - | 14 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.38103 | 0.35736 | 0.29724 | 0.34293 | 0.30725 | 0.31892 | 0.55255 | 0.6218 | 0.58285 | 0.43994 | 0.56778 | 0.42797 | 0.75949 | 0.77467 | 0.54493 | 0.51917 | 0.48949 | 0.62006 | 0.38152 | 0.34325 | 0.32605 | 0.30984 | 0.37683 | 0.02681
TSO | - | 14 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.38234 | 0.35241 | 0.29817 | 0.34081 | 0.30631 | 0.31763 | 0.5523 | 0.63784 | 0.63108 | 0.45873 | 0.62098 | 0.42519 | 0.73319 | 0.76424 | 0.51001 | 0.47783 | 0.48675 | 0.60555 | 0.3829 | 0.34502 | 0.32696 | 0.31322 | 0.3735 | 0.026774
TSO | - | 14 | 2020 | Summer | Pc_net, [MW] | Expected | - | 8.0889 | 7.7509 | 7.745 | 8.6087 | 7.7468 | 7.4029 | 7.4019 | 7.5577 | 7.8698 | 7.3828 | 9.414 | 7.4044 | 9.3214 | 9.8219 | 9.6743 | 10.025 | 9.6421 | 10.5145 | 7.4003 | 6.5392 | 6.5401 | 6.8819 | 7.2328 | 0.51643
TSO | - | 14 | 2020 | Summer | Qc, [MVAr] | Expected | - | -2.65 | -3.18 | -2.65 | -3.18 | -2.65 | -3.18 | -5.3 | -1.59 | -2.12 | -2.65 | -2.12 | -2.65 | -1.59 | -1.06 | -1.06 | -0.53 | 4.24 | 4.24 | -0.53 | -0.53 | -0.53 | -1.06 | -1.59 | -4.24
TSO | - | 15 | 2020 | Summer | Pc, [MW] | Expected | - | 12.1748 | 11.1068 | 10.466 | 10.2524 | 10.2524 | 10.2524 | 14.7379 | 20.0777 | 20.932 | 20.7184 | 20.2913 | 20.932 | 22 | 21.3592 | 20.0777 | 18.3689 | 18.3689 | 18.5825 | 20.7184 | 19.2233 | 20.2913 | 21.5728 | 18.7961 | 14.7379
TSO | - | 15 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.5792 | 0.51458 | 0.40423 | 0.4105 | 0.40903 | 0.44344 | 1.1115 | 1.6205 | 1.5512 | 1.2302 | 1.2444 | 1.193 | 1.764 | 1.6969 | 1.1273 | 0.94116 | 0.93998 | 1.103 | 1.0696 | 1.0096 | 1.0107 | 0.97234 | 0.99892 | 0.78899
TSO | - | 15 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.56958 | 0.50315 | 0.40026 | 0.404 | 0.40308 | 0.43828 | 1.0884 | 1.7187 | 1.658 | 1.2853 | 1.3035 | 1.2198 | 1.7689 | 1.6532 | 1.0701 | 0.89323 | 0.92038 | 1.066 | 1.0702 | 1.0132 | 1.0151 | 0.97983 | 0.95188 | 0.74029
TSO | - | 15 | 2020 | Summer | Pc_net, [MW] | Expected | - | 12.1844 | 11.1182 | 10.47 | 10.2589 | 10.2584 | 10.2576 | 14.7609 | 19.9795 | 20.8252 | 20.6634 | 20.2322 | 20.9052 | 21.9951 | 21.4029 | 20.1349 | 18.4169 | 18.3885 | 18.6196 | 20.7178 | 19.2197 | 20.2869 | 21.5653 | 18.8432 | 14.7866
TSO | - | 15 | 2020 | Summer | Qc, [MVAr] | Expected | - | -3.8235 | -4.7059 | -4.4118 | -4.1176 | -4.4118 | -5 | -3.8235 | -2.0588 | 0 | 0 | 0 | -0.29412 | 0 | 1.4706 | 1.1765 | 0 | -1.7647 | -1.7647 | -0.88235 | -1.1765 | -1.1765 | -1.7647 | -1.7647 | -3.5294
TSO | - | 16 | 2020 | Summer | Pc, [MW] | Expected | - | 28.8906 | 26.4719 | 25.9344 | 24.8594 | 24.5906 | 24.4563 | 31.7125 | 36.4156 | 38.8344 | 40.3125 | 40.0438 | 40.9844 | 40.9844 | 43 | 39.2375 | 40.1781 | 39.6406 | 39.6406 | 38.1625 | 38.1625 | 37.7594 | 40.85 | 38.8344 | 33.4594
TSO | - | 16 | 2020 | Summer | Flex Up, [MW] | Expected | - | 1.287 | 1.1509 | 0.95314 | 0.94459 | 0.93197 | 1.0018 | 2.163 | 2.7747 | 3.3648 | 2.4566 | 2.5962 | 2.467 | 3.4543 | 3.5131 | 2.2559 | 2.2697 | 2.1042 | 2.4266 | 1.8661 | 1.8977 | 1.7878 | 1.7072 | 1.8848 | 1.6219
TSO | - | 16 | 2020 | Summer | Flex Down, [MW] | Expected | - | 1.439 | 1.2747 | 1.0404 | 1.0304 | 1.0159 | 1.1015 | 2.5707 | 3.2818 | 2.5889 | 2.438 | 2.4319 | 2.2572 | 3.1273 | 3.2313 | 2.0383 | 1.7426 | 1.9105 | 2.2005 | 2.0752 | 2.118 | 1.9819 | 1.9894 | 2.1457 | 1.85
TSO | - | 16 | 2020 | Summer | Pc_net, [MW] | Expected | - | 28.7387 | 26.3481 | 25.8472 | 24.7736 | 24.5067 | 24.3566 | 31.3048 | 35.9086 | 39.6103 | 40.3311 | 40.208 | 41.1942 | 41.3114 | 43.2818 | 39.4551 | 40.7053 | 39.8343 | 39.8667 | 37.9534 | 37.9422 | 37.5652 | 40.5678 | 38.5735 | 33.2312
TSO | - | 16 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.2449 | -0.30612 | -0.61224 | -0.61224 | -0.85714 | -0.85714 | 0.2449 | 1.4694 | 2.0816 | 2.449 | 1.9592 | 3 | 2.8776 | 3 | 2.6939 | 2.0816 | 1.898 | 2.0816 | 1.7143 | 1.9592 | 1.5306 | 1.5918 | 0.73469 | 0.36735
TSO | - | 17 | 2020 | Summer | Pc, [MW] | Expected | - | 26.6163 | 24.4186 | 23.9302 | 23.9302 | 24.6628 | 25.1512 | 33.4535 | 38.093 | 39.314 | 36.1395 | 37.1163 | 42 | 41.7558 | 40.5349 | 38.8256 | 36.3837 | 37.6047 | 37.8488 | 37.8488 | 36.1395 | 39.5581 | 38.3372 | 31.9884 | 29.5465
TSO | - | 17 | 2020 | Summer | Flex Up, [MW] | Expected | - | 1.2026 | 0.97735 | 0.8126 | 0.87845 | 0.81308 | 0.85518 | 2.3316 | 4.081 | 2.6934 | 1.7802 | 2.0737 | 2.1799 | 3.4851 | 3.1941 | 2.0724 | 2.0449 | 1.7576 | 2.0483 | 2.4342 | 2.287 | 2.3577 | 1.8418 | 1.6937 | 1.3744
TSO | - | 17 | 2020 | Summer | Flex Down, [MW] | Expected | - | 1.3089 | 1.2601 | 1.0268 | 1.0227 | 1.1405 | 1.3079 | 2.662 | 2.2545 | 3.3339 | 2.6077 | 2.5868 | 2.6613 | 3.2203 | 3.1637 | 2.1767 | 1.5885 | 2.0509 | 2.3697 | 1.4747 | 1.5158 | 1.5915 | 1.6274 | 1.6262 | 1.6915
TSO | - | 17 | 2020 | Summer | Pc_net, [MW] | Expected | - | 26.5099 | 24.1358 | 23.716 | 23.786 | 24.3354 | 24.6985 | 33.1231 | 39.9196 | 38.6734 | 35.312 | 36.6031 | 41.5185 | 42.0206 | 40.5652 | 38.7212 | 36.8402 | 37.3113 | 37.5275 | 38.8083 | 36.9107 | 40.3243 | 38.5516 | 32.0559 | 29.2295
TSO | - | 17 | 2020 | Summer | Qc, [MVAr] | Expected | - | -6.5455 | -6.5455 | -7.6364 | -7.6364 | -8 | -8 | -3.2727 | -1.4545 | 0 | -1.0909 | -2.1818 | -1.0909 | 0.72727 | 0 | -0.36364 | -2.1818 | -1.0909 | 0.36364 | 0 | -3.2727 | -2.1818 | -2.1818 | -5.0909 | -5.4545
TSO | - | 18 | 2020 | Summer | Pc, [MW] | Expected | - | 16.958 | 15.4469 | 13.2642 | 14.6074 | 15.1111 | 16.1185 | 21.9951 | 25.6889 | 27.2 | 26.6963 | 24.0099 | 27.2 | 26.5284 | 26.0247 | 21.9951 | 21.3235 | 20.9877 | 20.8198 | 20.484 | 22.6667 | 22.8346 | 24.3457 | 22.163 | 18.9728
TSO | - | 18 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.90977 | 0.75755 | 0.56246 | 0.66125 | 0.6794 | 0.92246 | 2.3006 | 1.9436 | 1.7399 | 1.496 | 1.1497 | 1.7543 | 2.1653 | 1.3671 | 1.083 | 1.015 | 0.85162 | 0.91719 | 1.2656 | 1.5209 | 1.5091 | 1.3232 | 0.99463 | 0.90181
TSO | - | 18 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.69035 | 0.65786 | 0.45712 | 0.49924 | 0.51758 | 0.46375 | 0.98257 | 2.3289 | 2.4302 | 1.7453 | 1.8651 | 1.381 | 2.0949 | 2.7148 | 1.3242 | 1.1144 | 1.2739 | 1.513 | 0.84988 | 0.86425 | 0.77057 | 0.87987 | 1.3056 | 1.0669
TSO | - | 18 | 2020 | Summer | Pc_net, [MW] | Expected | - | 17.1774 | 15.5466 | 13.3695 | 14.7694 | 15.2729 | 16.5772 | 23.3131 | 25.3036 | 26.5096 | 26.447 | 23.2945 | 27.5733 | 26.5988 | 24.677 | 21.7539 | 21.2241 | 20.5653 | 20.2239 | 20.8997 | 23.3233 | 23.5731 | 24.789 | 21.852 | 18.8077
TSO | - | 18 | 2020 | Summer | Qc, [MVAr] | Expected | - | -4.0091 | -5.3455 | -5.7909 | -4.9 | -4.4545 | -4.0091 | -0.89091 | 6.6818 | 6.6818 | 8.0182 | 6.2364 | 8.9091 | 9.8 | 9.3545 | 7.5727 | 5.7909 | 4.0091 | 3.5636 | 3.1182 | 4.0091 | 3.5636 | 2.2273 | 1.3364 | -0.89091
TSO | - | 19 | 2020 | Summer | Pc, [MW] | Expected | - | 2.2 | 2.2 | 2.75 | 0.55 | 1.1 | 2.75 | 2.2 | 1.1 | 0 | -3.3 | -3.3 | -2.75 | -2.75 | -1.65 | 1.1 | 1.1 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | -1.65 | -0.55
TSO | - | 19 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.10642 | 0.10033 | 0.10733 | 0.022061 | 0.044365 | 0.14279 | 0.1974 | 0.092775 | 0 | 0.11168 | 0.13613 | 0.11755 | 0.061986 | 0.039867 | 0.060227 | 0.055719 | 0 | 0 | 0.02881 | 0.029699 | 0.028468 | 0.025226 | 0.077154 | 0.024682
TSO | - | 19 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.10117 | 0.10126 | 0.10406 | 0.021633 | 0.042768 | 0.093717 | 0.131 | 0.090172 | 0 | 0.1643 | 0.16598 | 0.15065 | 0.074397 | 0.040294 | 0.060159 | 0.054131 | 0 | 0 | 0.027992 | 0.028175 | 0.026441 | 0.024545 | 0.082629 | 0.025205
TSO | - | 19 | 2020 | Summer | Pc_net, [MW] | Expected | - | 2.2053 | 2.1991 | 2.7533 | 0.55043 | 1.1016 | 2.7991 | 2.2664 | 1.1026 | 0 | -3.3526 | -3.3298 | -2.7831 | -2.7624 | -1.6504 | 1.1001 | 1.1016 | 0 | 0 | 0.55082 | 0.55152 | 0.55203 | 0.55068 | -1.6555 | -0.55052
TSO | - | 19 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.43846 | 0.39231 | 0.18462 | 0.32308 | 0.34615 | 0.18462 | 0.53077 | 0.41538 | 0.43846 | 0.53077 | 0.50769 | 0.57692 | 0.6 | 0.57692 | 0.48462 | 0.53077 | 0.57692 | 0.57692 | 0.53077 | 0.50769 | 0.55385 | 0.55385 | 0.53077 | 0.57692
TSO | - | 20 | 2020 | Summer | Pc, [MW] | Expected | - | 1.4522 | 1.362 | 1.3078 | 1.2898 | 1.3259 | 1.2718 | 1.5153 | 1.7318 | 1.822 | 1.8941 | 2.0384 | 2.3 | 1.5424 | 2.0745 | 1.9663 | 1.9122 | 2.0024 | 1.9031 | 1.7318 | 1.7949 | 1.8039 | 1.9122 | 1.5424 | 1.4071
TSO | - | 20 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.071993 | 0.062906 | 0.051535 | 0.053526 | 0.055185 | 0.053857 | 0.10949 | 0.16677 | 0.16007 | 0.095131 | 0.10977 | 0.12333 | 0.10738 | 0.15166 | 0.11073 | 0.10118 | 0.093626 | 0.10022 | 0.096334 | 0.10777 | 0.10742 | 0.093542 | 0.074852 | 0.069161
TSO | - | 20 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.065029 | 0.061891 | 0.048995 | 0.048943 | 0.04984 | 0.055516 | 0.1167 | 0.12125 | 0.11926 | 0.13484 | 0.14619 | 0.14178 | 0.1403 | 0.17372 | 0.10446 | 0.089779 | 0.10917 | 0.12193 | 0.082517 | 0.081101 | 0.072669 | 0.079493 | 0.085224 | 0.076843
TSO | - | 20 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.4591 | 1.363 | 1.3104 | 1.2944 | 1.3312 | 1.2701 | 1.5081 | 1.7773 | 1.8628 | 1.8544 | 2.002 | 2.2815 | 1.5094 | 2.0525 | 1.9725 | 1.9236 | 1.9868 | 1.8814 | 1.7456 | 1.8216 | 1.8387 | 1.9262 | 1.532 | 1.3994
TSO | - | 20 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.29412 | -0.47059 | -0.47059 | -0.52941 | -0.41176 | -0.76471 | -0.47059 | 0.23529 | 0.76471 | 0.70588 | 0.35294 | 1 | 0.76471 | 1 | 0.94118 | 0.35294 | 0.64706 | 0.41176 | 0.29412 | 0.35294 | 0.35294 | 0.17647 | -0.17647 | -0.70588
TSO | - | 21 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 21 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 22 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 23 | 2020 | Summer | Pc, [MW] | Expected | - | -0.31765 | -1.7294 | -1.9941 | -2.1706 | -1.2882 | -2.3471 | -0.75882 | -1.0235 | -1.2882 | 0.56471 | 0.91765 | 1.5353 | 3.9176 | 6.3 | 6.0353 | 5.5941 | 5.2412 | 5.0647 | 2.4176 | 2.9471 | 4.7118 | 5.5941 | 5.5941 | 6.1235
TSO | - | 23 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.014477 | 0.057429 | 0.047508 | 0.055213 | 0.030116 | 0.084191 | 0.040967 | 0.043432 | 0.034175 | 0.03401 | 0.057145 | 0.087103 | 0.30083 | 0.46142 | 0.29851 | 0.26879 | 0.26349 | 0.29591 | 0.12866 | 0.15899 | 0.23957 | 0.25845 | 0.31978 | 0.35821
TSO | - | 23 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.014331 | 0.05702 | 0.046057 | 0.050906 | 0.02908 | 0.080386 | 0.040458 | 0.044869 | 0.034535 | 0.034554 | 0.05808 | 0.089866 | 0.3283 | 0.52671 | 0.36199 | 0.28986 | 0.26732 | 0.29527 | 0.12103 | 0.15112 | 0.23083 | 0.24778 | 0.26082 | 0.27721
TSO | - | 23 | 2020 | Summer | Pc_net, [MW] | Expected | - | -0.3175 | -1.729 | -1.9927 | -2.1663 | -1.2872 | -2.3433 | -0.75831 | -1.025 | -1.2886 | 0.56416 | 0.91671 | 1.5325 | 3.8902 | 6.2347 | 5.9718 | 5.573 | 5.2373 | 5.0653 | 2.4253 | 2.9549 | 4.7205 | 5.6048 | 5.6531 | 6.2045
TSO | - | 23 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.83276 | -1.0138 | -1.1948 | -1.7379 | -1.8284 | -2.1 | -1.4664 | -0.018103 | 0.525 | 1.4302 | 1.3397 | 0.88707 | 0.525 | -0.28966 | -0.10862 | -0.56121 | -0.56121 | -0.74224 | -0.018103 | -0.19914 | -0.74224 | -0.92328 | -0.92328 | -1.3759
TSO | - | 24 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 24 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 25 | 2020 | Summer | Pc, [MW] | Expected | - | 0.59062 | 6.3 | 3.15 | 0.49219 | 0.49219 | 0.59062 | 0.39375 | 0.19687 | 0.39375 | 3.7406 | 0.29531 | 0.7875 | 0.39375 | 0.49219 | 1.7719 | 0.49219 | 0.39375 | 0.39375 | 1.1812 | 0.19687 | 0.39375 | 0.19687 | 0.39375 | 0.19687
TSO | - | 25 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.028341 | 0.29782 | 0.12915 | 0.019933 | 0.0198 | 0.025771 | 0.029741 | 0.016351 | 0.030243 | 0.20887 | 0.018553 | 0.045318 | 0.031646 | 0.038582 | 0.0947 | 0.024569 | 0.019956 | 0.023018 | 0.06202 | 0.010368 | 0.01968 | 0.0089191 | 0.020579 | 0.01027
TSO | - | 25 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.027389 | 0.27945 | 0.11298 | 0.019169 | 0.019187 | 0.025023 | 0.029034 | 0.016393 | 0.030124 | 0.2453 | 0.018528 | 0.045455 | 0.031586 | 0.038616 | 0.099216 | 0.024583 | 0.019922 | 0.022943 | 0.059976 | 0.010348 | 0.01963 | 0.0088965 | 0.020287 | 0.010159
TSO | - | 25 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.59158 | 6.3184 | 3.1662 | 0.49295 | 0.4928 | 0.59137 | 0.39446 | 0.19683 | 0.39387 | 3.7042 | 0.29534 | 0.78736 | 0.39381 | 0.49215 | 1.7674 | 0.49217 | 0.39378 | 0.39382 | 1.1833 | 0.1969 | 0.3938 | 0.1969 | 0.39404 | 0.19699
TSO | - | 25 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.43636 | 3.2 | 1.7455 | 0.43636 | 0.21818 | 0.43636 | 0.43636 | 0.72727 | 0.72727 | 2.4 | 0.50909 | 1.0909 | 0.43636 | 0.72727 | 1.9636 | 0.65455 | 0.50909 | 0.43636 | 0 | 0.29091 | 0.29091 | 0.58182 | 0 | 0
TSO | - | 26 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 26 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 27 | 2020 | Summer | Pc, [MW] | Expected | - | 6.3047 | 6.2564 | 5.7491 | 6.0631 | 5.4834 | 6.0873 | 7.5366 | 9.1792 | 8.9377 | 9.3 | 8.6719 | 9.1551 | 9.0101 | 9.2034 | 9.0101 | 8.0681 | 8.213 | 8.1164 | 8.1405 | 8.4787 | 8.2613 | 8.2855 | 7.4642 | 7.2226
TSO | - | 27 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.31754 | 0.30437 | 0.22799 | 0.26778 | 0.22849 | 0.27248 | 0.62735 | 0.70658 | 0.66071 | 0.52795 | 0.52516 | 0.50565 | 0.69721 | 0.70311 | 0.46488 | 0.40132 | 0.41865 | 0.48033 | 0.43102 | 0.45041 | 0.41708 | 0.37371 | 0.40622 | 0.40293
TSO | - | 27 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.27736 | 0.26891 | 0.21393 | 0.21391 | 0.20586 | 0.25103 | 0.49765 | 0.82006 | 0.70954 | 0.60122 | 0.56373 | 0.54963 | 0.74971 | 0.74042 | 0.52119 | 0.40438 | 0.41314 | 0.46706 | 0.40971 | 0.44177 | 0.40768 | 0.37606 | 0.36846 | 0.34652
TSO | - | 27 | 2020 | Summer | Pc_net, [MW] | Expected | - | 6.3449 | 6.2918 | 5.7632 | 6.117 | 5.506 | 6.1087 | 7.6663 | 9.0657 | 8.8888 | 9.2267 | 8.6334 | 9.1111 | 8.9576 | 9.1661 | 8.9538 | 8.065 | 8.2185 | 8.1296 | 8.1618 | 8.4873 | 8.2707 | 8.2831 | 7.5019 | 7.279
TSO | - | 27 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.35 | -0.3375 | -0.4625 | -0.4625 | -0.5 | -0.4125 | -0.05 | 0.3125 | 0.325 | 0.2875 | 0.2625 | 0.4375 | 0.3875 | 0.4 | -0.2625 | 0.1125 | 0.1 | 0.0375 | -0.0625 | 0 | -0.05 | -0.1 | -0.2375 | -0.325
TSO | - | 28 | 2020 | Summer | Pc, [MW] | Expected | - | 3.1615 | 2.7876 | 2.5926 | 2.5357 | 2.5926 | 2.4057 | 2.877 | 3.4947 | 3.8848 | 4.0555 | 4.3643 | 4.535 | 4.47 | 4.6 | 4.2749 | 4.3318 | 4.1855 | 4.283 | 4.0392 | 4.023 | 4.0148 | 4.283 | 4.2668 | 3.6898
TSO | - | 28 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.15214 | 0.13054 | 0.099907 | 0.10374 | 0.10338 | 0.10346 | 0.22046 | 0.28661 | 0.29458 | 0.24251 | 0.27093 | 0.25726 | 0.35474 | 0.35871 | 0.23059 | 0.21605 | 0.21246 | 0.25113 | 0.21044 | 0.21258 | 0.20131 | 0.1936 | 0.2245 | 0.19553
TSO | - | 28 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.14617 | 0.12489 | 0.099376 | 0.097711 | 0.10199 | 0.10343 | 0.209 | 0.29461 | 0.30101 | 0.24988 | 0.27707 | 0.26547 | 0.36309 | 0.36279 | 0.23727 | 0.21654 | 0.21144 | 0.24881 | 0.20672 | 0.21073 | 0.19951 | 0.19398 | 0.21834 | 0.18734
TSO | - | 28 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.1675 | 2.7933 | 2.5931 | 2.5417 | 2.594 | 2.4057 | 2.8885 | 3.4867 | 3.8784 | 4.0481 | 4.3582 | 4.5268 | 4.4616 | 4.5959 | 4.2682 | 4.3313 | 4.1865 | 4.2854 | 4.0429 | 4.0248 | 4.0166 | 4.2827 | 4.273 | 3.698
TSO | - | 28 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.15 | -0.25 | -0.425 | -0.425 | -0.4 | -0.95 | -0.45 | 0.5 | 0.55 | 1.7 | 1.575 | 2.15 | 2.3 | 2.05 | 1.425 | 1.2 | 1.025 | 1.225 | 0.75 | 0.825 | 0.55 | 0.9 | 0.675 | 0.3
TSO | - | 29 | 2020 | Summer | Pc, [MW] | Expected | - | 4.4403 | 1.7761 | 2.4104 | 2.0299 | 0.50746 | 0.88806 | 4.694 | 10.403 | 13.0672 | 13.9552 | 13.9552 | 16.3657 | 15.7313 | 16.3657 | 15.6045 | 13.5746 | 13.194 | 12.9403 | 12.5597 | 12.306 | 13.194 | 16.1119 | 17 | 11.7985
TSO | - | 29 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.2127 | 0.082329 | 0.092192 | 0.081788 | 0.020077 | 0.038034 | 0.35892 | 0.85643 | 0.98135 | 0.83377 | 0.86252 | 0.90823 | 1.2427 | 1.2933 | 0.84044 | 0.68027 | 0.67484 | 0.76575 | 0.6644 | 0.65784 | 0.6692 | 0.73081 | 0.90443 | 0.63335
TSO | - | 29 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.20627 | 0.080418 | 0.093091 | 0.079474 | 0.02012 | 0.03834 | 0.34176 | 0.87375 | 1.022 | 0.86061 | 0.88977 | 0.97819 | 1.2835 | 1.2736 | 0.86733 | 0.67534 | 0.66141 | 0.74471 | 0.63272 | 0.63706 | 0.64801 | 0.72719 | 0.85996 | 0.59092
TSO | - | 29 | 2020 | Summer | Pc_net, [MW] | Expected | - | 4.4467 | 1.778 | 2.4095 | 2.0322 | 0.50742 | 0.88775 | 4.7112 | 10.3857 | 13.0265 | 13.9284 | 13.928 | 16.2957 | 15.6905 | 16.3853 | 15.5776 | 13.5796 | 13.2075 | 12.9613 | 12.5914 | 12.3267 | 13.2152 | 16.1156 | 17.0445 | 11.8409
TSO | - | 29 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.98621 | 0.71724 | 0.8069 | 0.44828 | 0.44828 | -0.17931 | 0.62759 | 1.9724 | 1.9724 | 2.0621 | 2.0621 | 2.6 | 2.4207 | 2.331 | 2.1517 | 1.6138 | 1.5241 | 1.7034 | 1.5241 | 1.6138 | 1.4345 | 1.7931 | 1.9724 | 1.5241
TSO | - | 30 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 30 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.7478 | 1.7583 | 1.7791 | 1.793 | 1.7965 | 1.8 | 1.76 | 1.6974 | 1.6678 | 1.6174 | 1.6296 | 1.6104 | 1.6296 | 1.6261 | 1.647 | 1.6783 | 1.6817 | 1.673 | 1.6852 | 1.6713 | 1.6991 | 1.68 | 1.687 | 1.6939
TSO | - | 31 | 2020 | Summer | Pc, [MW] | Expected | - | 3.5323 | 4.6872 | 5.8 | 4.9907 | 4.6198 | 3.6166 | 2.1413 | 0.8093 | 0.39622 | -0.48895 | -0.31192 | -1.0201 | -1.2561 | -1.5933 | -0.75029 | -0.10959 | 0.57326 | 0.69128 | 1.6692 | 1.7029 | 1.1718 | 0.5311 | 1.0116 | 1.1212
TSO | - | 31 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.17023 | 0.20328 | 0.21865 | 0.21287 | 0.19281 | 0.16308 | 0.16351 | 0.065296 | 0.030028 | 0.020229 | 0.014177 | 0.049071 | 0.030661 | 0.037913 | 0.033738 | 0.0049638 | 0.028481 | 0.039331 | 0.080535 | 0.080698 | 0.055838 | 0.023775 | 0.05209 | 0.059389
TSO | - | 31 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.16306 | 0.22621 | 0.22718 | 0.18362 | 0.17313 | 0.14795 | 0.15612 | 0.069303 | 0.030717 | 0.020662 | 0.014378 | 0.050411 | 0.031634 | 0.039495 | 0.0352 | 0.0049846 | 0.029576 | 0.041359 | 0.091853 | 0.098491 | 0.061148 | 0.024286 | 0.052904 | 0.056955
TSO | - | 31 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.5394 | 4.6643 | 5.7915 | 5.0199 | 4.6394 | 3.6317 | 2.1487 | 0.80529 | 0.39553 | -0.48939 | -0.31212 | -1.0214 | -1.2571 | -1.5949 | -0.75175 | -0.10961 | 0.57216 | 0.68925 | 1.6579 | 1.6851 | 1.1665 | 0.53059 | 1.0108 | 1.1237
TSO | - | 31 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.9276 | 1.3166 | 1.2134 | 1.2994 | 1.6264 | 1.5834 | 1.8846 | 1.6264 | 1.5404 | 1.876 | 2.0653 | 1.9878 | 2.2202 | 2.2976 | 2.2116 | 2.5644 | 2.7365 | 2.9 | 2.6332 | 2.6677 | 2.6418 | 2.289 | 2.6246 | 2.8742
TSO | - | 32 | 2020 | Summer | Pc, [MW] | Expected | - | 1.395 | 1.37 | 1.255 | 1.245 | 1.23 | 1.28 | 1.29 | 1.4 | 1.465 | 1.46 | 1.41 | 1.36 | 1.27 | 1.285 | 1.185 | 1.21 | 1.25 | 1.285 | 1.42 | 1.6 | 1.42 | 1.485 | 1.425 | 1.13
TSO | - | 32 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.067577 | 0.063039 | 0.048614 | 0.050661 | 0.049835 | 0.056654 | 0.10042 | 0.11821 | 0.11334 | 0.088385 | 0.087315 | 0.078282 | 0.097624 | 0.095502 | 0.064028 | 0.060459 | 0.06293 | 0.074703 | 0.072533 | 0.081316 | 0.069776 | 0.067103 | 0.07543 | 0.061283
TSO | - | 32 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.064052 | 0.062495 | 0.047854 | 0.048248 | 0.047596 | 0.053427 | 0.092135 | 0.11463 | 0.11126 | 0.088881 | 0.089732 | 0.078482 | 0.10632 | 0.10605 | 0.06566 | 0.060376 | 0.063666 | 0.075289 | 0.07412 | 0.087045 | 0.071988 | 0.067278 | 0.072467 | 0.055972
TSO | - | 32 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.3985 | 1.3705 | 1.2558 | 1.2474 | 1.2322 | 1.2832 | 1.2983 | 1.4036 | 1.4671 | 1.4595 | 1.4076 | 1.3598 | 1.2613 | 1.2745 | 1.1834 | 1.2101 | 1.2493 | 1.2844 | 1.4184 | 1.5943 | 1.4178 | 1.4848 | 1.428 | 1.1353
TSO | - | 32 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.69231 | -0.71538 | -0.7 | -0.71538 | -0.70769 | -0.8 | -0.66923 | -0.24615 | -0.18462 | -0.11538 | -0.13077 | 0.038462 | 0.13077 | 0.12308 | -0.030769 | -0.23077 | -0.14615 | -0.22308 | -0.33846 | -0.23077 | -0.36923 | -0.24615 | -0.40769 | -0.46154
TSO | - | 33 | 2020 | Summer | Pc, [MW] | Expected | - | 1.995 | 1.672 | 1.425 | 1.368 | 1.368 | 1.615 | 2.261 | 2.508 | 3.021 | 3.173 | 3.268 | 3.534 | 3.8 | 3.705 | 3.572 | 3.401 | 3.192 | 3.173 | 3.002 | 3.135 | 3.135 | 3.268 | 3.04 | 2.299
TSO | - | 33 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.10121 | 0.079436 | 0.056549 | 0.057037 | 0.056847 | 0.073422 | 0.18937 | 0.22707 | 0.24592 | 0.19695 | 0.20296 | 0.20369 | 0.256 | 0.24133 | 0.18752 | 0.17239 | 0.16308 | 0.1887 | 0.15609 | 0.15811 | 0.15494 | 0.15 | 0.16916 | 0.13517
TSO | - | 33 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.087033 | 0.07377 | 0.052986 | 0.051644 | 0.051514 | 0.06547 | 0.14813 | 0.19005 | 0.21724 | 0.1883 | 0.20739 | 0.20367 | 0.35424 | 0.33979 | 0.20341 | 0.16724 | 0.16019 | 0.18167 | 0.15395 | 0.17177 | 0.15804 | 0.14573 | 0.14635 | 0.10338
TSO | - | 33 | 2020 | Summer | Pc_net, [MW] | Expected | - | 2.0092 | 1.6777 | 1.4286 | 1.3734 | 1.3733 | 1.623 | 2.3022 | 2.545 | 3.0497 | 3.1817 | 3.2636 | 3.534 | 3.7018 | 3.6065 | 3.5561 | 3.4062 | 3.1949 | 3.18 | 3.0041 | 3.1213 | 3.1319 | 3.2723 | 3.0628 | 2.3308
TSO | - | 33 | 2020 | Summer | Qc, [MVAr] | Expected | - | -1.0419 | -1.2258 | -1.2871 | -1.3484 | -1.2871 | -1.9 | -1.4403 | -0.73548 | -0.21452 | -0.091935 | 0.030645 | 0.030645 | 0.45968 | 0.42903 | 0.42903 | -0.18387 | -0.030645 | -0.18387 | -0.52097 | -0.49032 | -0.45968 | -0.3371 | -0.52097 | -0.79677
TSO | - | 34 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 34 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 35 | 2020 | Summer | Pc, [MW] | Expected | - | 3.96 | 3.7886 | 3.6 | 3.7543 | 3.72 | 3.7543 | 5.04 | 5.6743 | 6 | 5.6743 | 5.5029 | 5.88 | 5.8457 | 5.4686 | 5.2286 | 5.04 | 5.04 | 4.8171 | 4.9543 | 5.2114 | 5.1257 | 5.4171 | 5.04 | 4.32
TSO | - | 35 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.19897 | 0.17957 | 0.14432 | 0.15889 | 0.15628 | 0.17112 | 0.40727 | 0.47373 | 0.46476 | 0.333 | 0.3379 | 0.3329 | 0.42992 | 0.38861 | 0.28161 | 0.25402 | 0.25675 | 0.28601 | 0.25053 | 0.26073 | 0.24606 | 0.24333 | 0.27426 | 0.25194
TSO | - | 35 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.17469 | 0.16758 | 0.1324 | 0.13937 | 0.13839 | 0.15175 | 0.34505 | 0.47 | 0.45511 | 0.35595 | 0.35307 | 0.34487 | 0.50883 | 0.46912 | 0.29061 | 0.24929 | 0.25368 | 0.27627 | 0.26113 | 0.28764 | 0.26566 | 0.24687 | 0.24883 | 0.19632
TSO | - | 35 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.9843 | 3.8006 | 3.6119 | 3.7738 | 3.7379 | 3.7737 | 5.1022 | 5.678 | 6.0096 | 5.6513 | 5.4877 | 5.868 | 5.7668 | 5.3881 | 5.2196 | 5.0447 | 5.0431 | 4.8269 | 4.9437 | 5.1845 | 5.1061 | 5.4136 | 5.0654 | 4.3756
TSO | - | 35 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.38889 | -0.5 | -0.5 | -0.38889 | -0.44444 | -0.55556 | 0.88889 | 2.1111 | 2.4444 | 2.1667 | 2.2222 | 3 | 2.8333 | 2.7778 | 1.8889 | 1.5 | 1.4444 | 1.0556 | 1.0556 | 0.94444 | 0.72222 | 1.3889 | 0.55556 | -0.055556
TSO | - | 36 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 36 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 37 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 38 | 2020 | Summer | Pc, [MW] | Expected | - | 10.7869 | 10.3279 | 10.3279 | 11.4754 | 10.3279 | 9.8689 | 9.8689 | 10.0984 | 10.5574 | 9.8689 | 12.623 | 9.8689 | 12.3934 | 13.082 | 12.8525 | 13.3115 | 12.8525 | 14 | 9.8689 | 8.7213 | 8.7213 | 9.1803 | 9.6393 | 0.68852
TSO | - | 38 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.52968 | 0.47168 | 0.40146 | 0.47474 | 0.4214 | 0.42305 | 0.73295 | 0.87124 | 0.84335 | 0.56817 | 0.80558 | 0.55324 | 0.96388 | 0.97998 | 0.70664 | 0.66902 | 0.65757 | 0.83985 | 0.49157 | 0.44081 | 0.412 | 0.40717 | 0.52513 | 0.03618
TSO | - | 38 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.48815 | 0.47467 | 0.39241 | 0.43693 | 0.39669 | 0.42568 | 0.74018 | 0.80827 | 0.77523 | 0.63007 | 0.77942 | 0.58431 | 1.0264 | 1.0719 | 0.69995 | 0.66031 | 0.64409 | 0.79431 | 0.52765 | 0.4769 | 0.45869 | 0.42357 | 0.47531 | 0.035265
TSO | - | 38 | 2020 | Summer | Pc_net, [MW] | Expected | - | 10.8284 | 10.3249 | 10.3369 | 11.5132 | 10.3526 | 9.8662 | 9.8616 | 10.1613 | 10.6255 | 9.8069 | 12.6491 | 9.8378 | 12.331 | 12.99 | 12.8591 | 13.3202 | 12.8659 | 14.0455 | 9.8328 | 8.6852 | 8.6746 | 9.1639 | 9.6892 | 0.68944
TSO | - | 38 | 2020 | Summer | Qc, [MVAr] | Expected | - | -3.5 | -4.2 | -3.5 | -4.2 | -3.5 | -4.2 | -7 | -2.1 | -2.8 | -3.5 | -2.8 | -3.5 | -2.1 | -1.4 | -1.4 | -0.7 | 5.6 | 5.6 | -0.7 | -0.7 | -0.7 | -1.4 | -2.1 | -5.6
TSO | - | 39 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 39 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 40 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 41 | 2020 | Summer | Pc, [MW] | Expected | - | 3.9924 | 3.6628 | 3.5895 | 3.5895 | 3.6994 | 3.7727 | 5.018 | 5.714 | 5.8971 | 5.4209 | 5.5674 | 6.3 | 6.2634 | 6.0802 | 5.8238 | 5.4576 | 5.6407 | 5.6773 | 5.6773 | 5.4209 | 5.9337 | 5.7506 | 4.7983 | 4.432
TSO | - | 41 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.19298 | 0.16709 | 0.13935 | 0.1473 | 0.14928 | 0.16422 | 0.38592 | 0.46437 | 0.43989 | 0.32634 | 0.34614 | 0.35828 | 0.49336 | 0.47184 | 0.32424 | 0.27812 | 0.29014 | 0.33809 | 0.30103 | 0.27494 | 0.28469 | 0.2654 | 0.25036 | 0.23717
TSO | - | 41 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.18374 | 0.16854 | 0.13657 | 0.13787 | 0.14375 | 0.16023 | 0.36312 | 0.48595 | 0.46421 | 0.33185 | 0.35294 | 0.36791 | 0.51247 | 0.48183 | 0.31313 | 0.26689 | 0.28113 | 0.32459 | 0.28531 | 0.29548 | 0.3077 | 0.25498 | 0.24764 | 0.22271
TSO | - | 41 | 2020 | Summer | Pc_net, [MW] | Expected | - | 4.0017 | 3.6613 | 3.5923 | 3.599 | 3.7049 | 3.7767 | 5.0408 | 5.6924 | 5.8728 | 5.4154 | 5.5606 | 6.2904 | 6.2443 | 6.0702 | 5.8349 | 5.4688 | 5.6497 | 5.6908 | 5.693 | 5.4004 | 5.9107 | 5.761 | 4.801 | 4.4464
TSO | - | 41 | 2020 | Summer | Qc, [MVAr] | Expected | - | -2.4545 | -2.4545 | -2.8636 | -2.8636 | -3 | -3 | -1.2273 | -0.54545 | 0 | -0.40909 | -0.81818 | -0.40909 | 0.27273 | 0 | -0.13636 | -0.81818 | -0.40909 | 0.13636 | 0 | -1.2273 | -0.81818 | -0.81818 | -1.9091 | -2.0455
TSO | - | 42 | 2020 | Summer | Pc, [MW] | Expected | - | 4.4265 | 4.0321 | 3.4623 | 3.813 | 3.9444 | 4.2074 | 5.7414 | 6.7056 | 7.1 | 6.9685 | 6.2673 | 7.1 | 6.9247 | 6.7932 | 5.7414 | 5.566 | 5.4784 | 5.4346 | 5.3469 | 5.9167 | 5.9605 | 6.3549 | 5.7852 | 4.9525
TSO | - | 42 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.21664 | 0.18795 | 0.13618 | 0.15891 | 0.16056 | 0.18606 | 0.45436 | 0.55328 | 0.51143 | 0.41048 | 0.3823 | 0.3951 | 0.5296 | 0.51325 | 0.32326 | 0.28858 | 0.28413 | 0.32777 | 0.28411 | 0.30025 | 0.28948 | 0.29424 | 0.31141 | 0.27705
TSO | - | 42 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.20104 | 0.18151 | 0.12996 | 0.14401 | 0.15188 | 0.17578 | 0.40265 | 0.56196 | 0.57709 | 0.43561 | 0.40465 | 0.4233 | 0.58242 | 0.55225 | 0.30508 | 0.26726 | 0.27071 | 0.30658 | 0.2681 | 0.32233 | 0.30558 | 0.28083 | 0.28901 | 0.23684
TSO | - | 42 | 2020 | Summer | Pc_net, [MW] | Expected | - | 4.4421 | 4.0385 | 3.4686 | 3.8279 | 3.9531 | 4.2177 | 5.7931 | 6.6969 | 7.0343 | 6.9434 | 6.2449 | 7.0718 | 6.8719 | 6.7542 | 5.7595 | 5.5874 | 5.4918 | 5.4558 | 5.3629 | 5.8946 | 5.9444 | 6.3683 | 5.8076 | 4.9927
TSO | - | 42 | 2020 | Summer | Qc, [MVAr] | Expected | - | -1.8 | -2.4 | -2.6 | -2.2 | -2 | -1.8 | -0.4 | 3 | 3 | 3.6 | 2.8 | 4 | 4.4 | 4.2 | 3.4 | 2.6 | 1.8 | 1.6 | 1.4 | 1.8 | 1.6 | 1 | 0.6 | -0.4
TSO | - | 43 | 2020 | Summer | Pc, [MW] | Expected | - | 1.3333 | 1.3333 | 1.6667 | 0.33333 | 0.66667 | 1.6667 | 1.3333 | 0.66667 | 0 | -2 | -2 | -1.6667 | -1.6667 | -1 | 0.66667 | 0.66667 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | -1 | -0.33333
TSO | - | 43 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.063379 | 0.060719 | 0.064337 | 0.013276 | 0.026473 | 0.071885 | 0.10009 | 0.055176 | 0 | 0.083491 | 0.091226 | 0.081007 | 0.041255 | 0.024274 | 0.036487 | 0.033301 | 0 | 0 | 0.017236 | 0.017487 | 0.016587 | 0.015098 | 0.048258 | 0.015114
TSO | - | 43 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.062431 | 0.061455 | 0.063774 | 0.013206 | 0.026335 | 0.07145 | 0.098933 | 0.055701 | 0 | 0.083769 | 0.091872 | 0.081537 | 0.041402 | 0.024309 | 0.036474 | 0.033275 | 0 | 0 | 0.01719 | 0.017588 | 0.016691 | 0.015066 | 0.04858 | 0.015121
TSO | - | 43 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.3343 | 1.3326 | 1.6672 | 0.3334 | 0.66681 | 1.6671 | 1.3345 | 0.66614 | 0 | -2.0003 | -2.0006 | -1.6672 | -1.6668 | -1 | 0.66668 | 0.66669 | 0 | 0 | 0.33338 | 0.33323 | 0.33323 | 0.33336 | -1.0003 | -0.33334
TSO | - | 43 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.73077 | 0.65385 | 0.30769 | 0.53846 | 0.57692 | 0.30769 | 0.88462 | 0.69231 | 0.73077 | 0.88462 | 0.84615 | 0.96154 | 1 | 0.96154 | 0.80769 | 0.88462 | 0.96154 | 0.96154 | 0.88462 | 0.84615 | 0.92308 | 0.92308 | 0.88462 | 0.96154
TSO | - | 44 | 2020 | Summer | Pc, [MW] | Expected | - | 7.5765 | 7.1059 | 6.8235 | 6.7294 | 6.9176 | 6.6353 | 7.9059 | 9.0353 | 9.5059 | 9.8824 | 10.6353 | 12 | 8.0471 | 10.8235 | 10.2588 | 9.9765 | 10.4471 | 9.9294 | 9.0353 | 9.3647 | 9.4118 | 9.9765 | 8.0471 | 7.3412
TSO | - | 44 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.36509 | 0.32557 | 0.2638 | 0.27172 | 0.27794 | 0.28401 | 0.58379 | 0.76633 | 0.74137 | 0.57417 | 0.67233 | 0.66334 | 0.63948 | 0.83344 | 0.56816 | 0.50375 | 0.53541 | 0.59289 | 0.45509 | 0.47671 | 0.44845 | 0.44424 | 0.43349 | 0.42258
TSO | - | 44 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.34981 | 0.32554 | 0.2607 | 0.2629 | 0.27002 | 0.28663 | 0.59633 | 0.73638 | 0.716 | 0.6257 | 0.6631 | 0.71986 | 0.65278 | 0.86421 | 0.55458 | 0.49254 | 0.52264 | 0.56612 | 0.47804 | 0.5087 | 0.49116 | 0.45855 | 0.40169 | 0.33918
TSO | - | 44 | 2020 | Summer | Pc_net, [MW] | Expected | - | 7.5917 | 7.1059 | 6.8266 | 6.7382 | 6.9256 | 6.6327 | 7.8933 | 9.0653 | 9.5313 | 9.8308 | 10.6445 | 11.9435 | 8.0338 | 10.7928 | 10.2724 | 9.9877 | 10.4598 | 9.9562 | 9.0123 | 9.3327 | 9.3691 | 9.9622 | 8.0789 | 7.4246
TSO | - | 44 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.52941 | -0.84706 | -0.84706 | -0.95294 | -0.74118 | -1.3765 | -0.84706 | 0.42353 | 1.3765 | 1.2706 | 0.63529 | 1.8 | 1.3765 | 1.8 | 1.6941 | 0.63529 | 1.1647 | 0.74118 | 0.52941 | 0.63529 | 0.63529 | 0.31765 | -0.31765 | -1.2706
TSO | - | 45 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 45 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 46 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 47 | 2020 | Summer | Pc, [MW] | Expected | - | -1.4975 | -8.1529 | -9.4008 | -10.2328 | -6.0731 | -11.0647 | -3.5773 | -4.8252 | -6.0731 | 2.6622 | 4.3261 | 7.2378 | 18.4689 | 29.7 | 28.4521 | 26.3723 | 24.7084 | 23.8765 | 11.3975 | 13.8933 | 22.2126 | 26.3723 | 26.3723 | 28.8681
TSO | - | 47 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.068009 | 0.2717 | 0.22197 | 0.25341 | 0.14014 | 0.38688 | 0.1919 | 0.20918 | 0.16196 | 0.15976 | 0.26561 | 0.40834 | 1.4936 | 2.4026 | 1.6127 | 1.3775 | 1.3232 | 1.5265 | 0.57553 | 0.70264 | 0.98242 | 1.0859 | 1.3422 | 1.403
TSO | - | 47 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.067804 | 0.26785 | 0.21912 | 0.24687 | 0.13892 | 0.38899 | 0.19196 | 0.2071 | 0.16196 | 0.16347 | 0.27759 | 0.42594 | 1.4723 | 2.2558 | 1.5011 | 1.2561 | 1.1792 | 1.2605 | 0.60156 | 0.75929 | 1.2352 | 1.3006 | 1.3949 | 1.5925
TSO | - | 47 | 2020 | Summer | Pc_net, [MW] | Expected | - | -1.4973 | -8.1491 | -9.398 | -10.2262 | -6.0719 | -11.0668 | -3.5774 | -4.8231 | -6.0731 | 2.6585 | 4.3141 | 7.2202 | 18.4903 | 29.8468 | 28.5637 | 26.4937 | 24.8524 | 24.1424 | 11.3714 | 13.8366 | 21.9599 | 26.1575 | 26.3196 | 28.6785
TSO | - | 47 | 2020 | Summer | Qc, [MVAr] | Expected | - | -4.6 | -5.6 | -6.6 | -9.6 | -10.1 | -11.6 | -8.1 | -0.1 | 2.9 | 7.9 | 7.4 | 4.9 | 2.9 | -1.6 | -0.6 | -3.1 | -3.1 | -4.1 | -0.1 | -1.1 | -4.1 | -5.1 | -5.1 | -7.6
TSO | - | 48 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 48 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 49 | 2020 | Summer | Pc, [MW] | Expected | - | 1.6875 | 18 | 9 | 1.4062 | 1.4062 | 1.6875 | 1.125 | 0.5625 | 1.125 | 10.6875 | 0.84375 | 2.25 | 1.125 | 1.4062 | 5.0625 | 1.4062 | 1.125 | 1.125 | 3.375 | 0.5625 | 1.125 | 0.5625 | 1.125 | 0.5625
TSO | - | 49 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.079607 | 0.85444 | 0.35121 | 0.055921 | 0.055731 | 0.072436 | 0.083595 | 0.046693 | 0.085673 | 0.63723 | 0.052934 | 0.12898 | 0.088958 | 0.10822 | 0.26742 | 0.069578 | 0.056555 | 0.065057 | 0.16883 | 0.029396 | 0.055451 | 0.025332 | 0.057964 | 0.029077
TSO | - | 49 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.079622 | 0.79491 | 0.34059 | 0.055798 | 0.05566 | 0.07269 | 0.084334 | 0.04686 | 0.086803 | 0.6604 | 0.053012 | 0.13037 | 0.091704 | 0.11235 | 0.28663 | 0.070855 | 0.057382 | 0.066259 | 0.17973 | 0.029793 | 0.056863 | 0.02557 | 0.058797 | 0.029291
TSO | - | 49 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.6875 | 18.0595 | 9.0106 | 1.4064 | 1.4063 | 1.6872 | 1.1243 | 0.56233 | 1.1239 | 10.6643 | 0.84367 | 2.2486 | 1.1223 | 1.4021 | 5.0433 | 1.405 | 1.1242 | 1.1238 | 3.3641 | 0.5621 | 1.1236 | 0.56226 | 1.1242 | 0.56229
TSO | - | 49 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.1591 | 8.5 | 4.6364 | 1.1591 | 0.57955 | 1.1591 | 1.1591 | 1.9318 | 1.9318 | 6.375 | 1.3523 | 2.8977 | 1.1591 | 1.9318 | 5.2159 | 1.7386 | 1.3523 | 1.1591 | 0 | 0.77273 | 0.77273 | 1.5455 | 0 | 0
TSO | - | 50 | 2020 | Summer | Pc, [MW] | Expected | - | 14.7153 | 13.6423 | 13.3358 | 13.6423 | 13.5657 | 13.4124 | 14.562 | 18.7007 | 20.4635 | 19.6204 | 20.2336 | 20.9234 | 20.6168 | 21 | 18.854 | 19.3905 | 19.0073 | 19.4672 | 19.3905 | 19.927 | 19.927 | 20.4635 | 18.6241 | 17.0146
TSO | - | 50 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.73961 | 0.67424 | 0.54801 | 0.56888 | 0.56597 | 0.59705 | 1.1369 | 1.6704 | 1.5789 | 1.2752 | 1.3696 | 1.2564 | 1.5097 | 1.5061 | 1.0562 | 0.97763 | 0.96892 | 1.1188 | 0.93451 | 0.94091 | 0.89793 | 0.87185 | 0.95153 | 0.87084
TSO | - | 50 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.64889 | 0.57581 | 0.47707 | 0.51493 | 0.50859 | 0.55643 | 1.0367 | 1.4399 | 1.5584 | 1.107 | 1.1711 | 1.1554 | 1.8011 | 1.7877 | 1.0072 | 0.95878 | 0.95609 | 1.1535 | 1.0681 | 1.1559 | 1.0915 | 0.97994 | 0.98142 | 0.89469
TSO | - | 50 | 2020 | Summer | Pc_net, [MW] | Expected | - | 14.8061 | 13.7408 | 13.4067 | 13.6963 | 13.6231 | 13.453 | 14.6622 | 18.9312 | 20.484 | 19.7886 | 20.4321 | 21.0243 | 20.3254 | 20.7184 | 18.9031 | 19.4094 | 19.0201 | 19.4324 | 19.2569 | 19.712 | 19.7335 | 20.3554 | 18.5942 | 16.9908
TSO | - | 50 | 2020 | Summer | Qc, [MVAr] | Expected | - | -4.375 | -7.875 | -7.875 | -6.5625 | -6.5625 | -8.75 | -5.6875 | 4.8125 | 10.5 | 5.6875 | 9.625 | 10.5 | 10.5 | 10.0625 | 1.3125 | 3.0625 | 4.375 | 7.875 | 8.3125 | 3.9375 | 3.5 | 1.75 | 0.875 | -0.4375
TSO | - | 51 | 2020 | Summer | Pc, [MW] | Expected | - | 12.2026 | 12.1091 | 11.1273 | 11.7351 | 10.613 | 11.7818 | 14.587 | 17.7662 | 17.2987 | 18 | 16.7844 | 17.7195 | 17.439 | 17.813 | 17.439 | 15.6156 | 15.8961 | 15.7091 | 15.7558 | 16.4104 | 15.9896 | 16.0364 | 14.4468 | 13.9792
TSO | - | 51 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.5844 | 0.55901 | 0.4415 | 0.47459 | 0.4338 | 0.52805 | 1.1275 | 1.327 | 1.3574 | 1.1349 | 1.1076 | 1.0501 | 1.3916 | 1.3861 | 0.98056 | 0.79017 | 0.81687 | 0.92846 | 0.79575 | 0.81712 | 0.76255 | 0.70774 | 0.7338 | 0.70325
TSO | - | 51 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.56701 | 0.55055 | 0.41382 | 0.4577 | 0.40687 | 0.4852 | 1.0499 | 1.6278 | 1.2947 | 1.0506 | 0.99991 | 0.99241 | 1.4089 | 1.4078 | 0.92798 | 0.76926 | 0.79304 | 0.90519 | 0.83146 | 0.90967 | 0.83376 | 0.74342 | 0.76559 | 0.74731
TSO | - | 51 | 2020 | Summer | Pc_net, [MW] | Expected | - | 12.22 | 12.1175 | 11.155 | 11.7519 | 10.6399 | 11.8247 | 14.6646 | 17.4654 | 17.3615 | 18.0843 | 16.8921 | 17.7771 | 17.4217 | 17.7913 | 17.4915 | 15.6365 | 15.9199 | 15.7324 | 15.7201 | 16.3178 | 15.9184 | 16.0007 | 14.415 | 13.9352
TSO | - | 51 | 2020 | Summer | Qc, [MVAr] | Expected | - | -3.71 | -3.5775 | -4.9025 | -4.9025 | -5.3 | -4.3725 | -0.53 | 3.3125 | 3.445 | 3.0475 | 2.7825 | 4.6375 | 4.1075 | 4.24 | -2.7825 | 1.1925 | 1.06 | 0.3975 | -0.6625 | 0 | -0.53 | -1.06 | -2.5175 | -3.445
TSO | - | 52 | 2020 | Summer | Pc, [MW] | Expected | - | 3.3677 | 2.9694 | 2.7617 | 2.7011 | 2.7617 | 2.5625 | 3.0647 | 3.7226 | 4.1382 | 4.32 | 4.6489 | 4.8307 | 4.7615 | 4.9 | 4.5537 | 4.6143 | 4.4585 | 4.5624 | 4.3027 | 4.2853 | 4.2767 | 4.5624 | 4.5451 | 3.9304
TSO | - | 52 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.16567 | 0.14511 | 0.1054 | 0.11442 | 0.10725 | 0.10667 | 0.24203 | 0.31338 | 0.31326 | 0.26046 | 0.28855 | 0.26473 | 0.36878 | 0.37633 | 0.24687 | 0.22906 | 0.22709 | 0.26735 | 0.22585 | 0.22873 | 0.21587 | 0.20662 | 0.23467 | 0.20737
TSO | - | 52 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.15209 | 0.12698 | 0.10688 | 0.10016 | 0.1115 | 0.11371 | 0.21543 | 0.30575 | 0.32117 | 0.26405 | 0.29519 | 0.2921 | 0.39586 | 0.39222 | 0.25149 | 0.23174 | 0.22445 | 0.26519 | 0.21851 | 0.2222 | 0.21109 | 0.20623 | 0.23704 | 0.20047
TSO | - | 52 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.3812 | 2.9876 | 2.7602 | 2.7153 | 2.7574 | 2.5555 | 3.0913 | 3.7303 | 4.1302 | 4.3164 | 4.6423 | 4.8034 | 4.7344 | 4.8841 | 4.5491 | 4.6116 | 4.4611 | 4.5645 | 4.31 | 4.2919 | 4.2815 | 4.5628 | 4.5427 | 3.9373
TSO | - | 52 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.14348 | -0.23913 | -0.40652 | -0.40652 | -0.38261 | -0.9087 | -0.43043 | 0.47826 | 0.52609 | 1.6261 | 1.5065 | 2.0565 | 2.2 | 1.9609 | 1.363 | 1.1478 | 0.98043 | 1.1717 | 0.71739 | 0.78913 | 0.52609 | 0.86087 | 0.64565 | 0.28696
TSO | - | 53 | 2020 | Summer | Pc, [MW] | Expected | - | 5.2239 | 2.0896 | 2.8358 | 2.3881 | 0.59701 | 1.0448 | 5.5224 | 12.2388 | 15.3731 | 16.4179 | 16.4179 | 19.2537 | 18.5075 | 19.2537 | 18.3582 | 15.9701 | 15.5224 | 15.2239 | 14.7761 | 14.4776 | 15.5224 | 18.9552 | 20 | 13.8806
TSO | - | 53 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.27255 | 0.10182 | 0.10924 | 0.1036 | 0.023608 | 0.044831 | 0.48496 | 1.1155 | 1.1685 | 1.0105 | 1.0181 | 0.86535 | 1.2855 | 1.3999 | 0.99345 | 0.80584 | 0.83534 | 0.93894 | 0.83471 | 0.82709 | 0.83303 | 0.87903 | 1.0099 | 0.78662
TSO | - | 53 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.22036 | 0.089644 | 0.10874 | 0.08612 | 0.023683 | 0.045021 | 0.33937 | 0.91999 | 1.1884 | 0.98287 | 1.0434 | 1.354 | 1.6866 | 1.62 | 1.0157 | 0.789 | 0.73673 | 0.83807 | 0.69132 | 0.69632 | 0.71664 | 0.83627 | 1.0659 | 0.6537
TSO | - | 53 | 2020 | Summer | Pc_net, [MW] | Expected | - | 5.2761 | 2.1017 | 2.8363 | 2.4055 | 0.59694 | 1.0446 | 5.668 | 12.4343 | 15.3532 | 16.4456 | 16.3926 | 18.7651 | 18.1064 | 19.0336 | 18.336 | 15.987 | 15.621 | 15.3247 | 14.9195 | 14.6084 | 15.6388 | 18.998 | 19.944 | 14.0135
TSO | - | 53 | 2020 | Summer | Qc, [MVAr] | Expected | - | 3.7931 | 2.7586 | 3.1034 | 1.7241 | 1.7241 | -0.68966 | 2.4138 | 7.5862 | 7.5862 | 7.931 | 7.931 | 10 | 9.3103 | 8.9655 | 8.2759 | 6.2069 | 5.8621 | 6.5517 | 5.8621 | 6.2069 | 5.5172 | 6.8966 | 7.5862 | 5.8621
TSO | - | 54 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSO | - | 54 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.3594 | 1.3675 | 1.3838 | 1.3946 | 1.3973 | 1.4 | 1.3689 | 1.3202 | 1.2972 | 1.258 | 1.2674 | 1.2526 | 1.2674 | 1.2647 | 1.281 | 1.3053 | 1.308 | 1.3013 | 1.3107 | 1.2999 | 1.3215 | 1.3067 | 1.3121 | 1.3175
TSO | - | 55 | 2020 | Summer | Pc, [MW] | Expected | - | 4.1413 | 5.4953 | 6.8 | 5.8512 | 5.4163 | 4.2401 | 2.5105 | 0.94884 | 0.46453 | -0.57326 | -0.3657 | -1.1959 | -1.4727 | -1.868 | -0.87965 | -0.12849 | 0.67209 | 0.81047 | 1.957 | 1.9965 | 1.3738 | 0.62267 | 1.186 | 1.3145
TSO | - | 55 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.19218 | 0.24204 | 0.27339 | 0.22437 | 0.22376 | 0.19168 | 0.18479 | 0.078156 | 0.035451 | 0.023904 | 0.016703 | 0.057821 | 0.036332 | 0.045121 | 0.040245 | 0.0058285 | 0.033912 | 0.04706 | 0.099978 | 0.10339 | 0.067866 | 0.028087 | 0.061021 | 0.067664
TSO | - | 55 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.19858 | 0.2615 | 0.2493 | 0.24047 | 0.20527 | 0.17297 | 0.18995 | 0.079651 | 0.035768 | 0.024037 | 0.016777 | 0.058814 | 0.036704 | 0.045632 | 0.040579 | 0.0058353 | 0.034156 | 0.047542 | 0.10213 | 0.10669 | 0.06929 | 0.02826 | 0.062076 | 0.06874
TSO | - | 55 | 2020 | Summer | Pc_net, [MW] | Expected | - | 4.1349 | 5.4759 | 6.8241 | 5.8351 | 5.4348 | 4.2588 | 2.5053 | 0.94734 | 0.46422 | -0.57339 | -0.36577 | -1.1969 | -1.473 | -1.8685 | -0.87998 | -0.1285 | 0.67185 | 0.80998 | 1.9548 | 1.9932 | 1.3724 | 0.6225 | 1.185 | 1.3135
TSO | - | 55 | 2020 | Summer | Qc, [MVAr] | Expected | - | 2.2599 | 1.5436 | 1.4226 | 1.5234 | 1.9068 | 1.8564 | 2.2095 | 1.9068 | 1.8059 | 2.1994 | 2.4214 | 2.3306 | 2.603 | 2.6938 | 2.5929 | 3.0065 | 3.2083 | 3.4 | 3.0872 | 3.1276 | 3.0973 | 2.6837 | 3.0772 | 3.3697
TSO | - | 56 | 2020 | Summer | Pc, [MW] | Expected | - | 6.6263 | 6.5075 | 5.9612 | 5.9137 | 5.8425 | 6.08 | 6.1275 | 6.65 | 6.9587 | 6.935 | 6.6975 | 6.46 | 6.0325 | 6.1037 | 5.6287 | 5.7475 | 5.9375 | 6.1037 | 6.745 | 7.6 | 6.745 | 7.0537 | 6.7687 | 5.3675
TSO | - | 56 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.33401 | 0.30255 | 0.24443 | 0.2651 | 0.26179 | 0.29086 | 0.49247 | 0.51331 | 0.50654 | 0.40538 | 0.40708 | 0.36329 | 0.45197 | 0.44885 | 0.30989 | 0.29194 | 0.30698 | 0.36528 | 0.34612 | 0.36179 | 0.31552 | 0.31887 | 0.35906 | 0.31081
TSO | - | 56 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.29123 | 0.29374 | 0.21379 | 0.20472 | 0.20101 | 0.23202 | 0.42219 | 0.59268 | 0.56032 | 0.43664 | 0.43389 | 0.38134 | 0.51678 | 0.50851 | 0.30613 | 0.28203 | 0.29436 | 0.34719 | 0.35048 | 0.43792 | 0.35787 | 0.31944 | 0.34345 | 0.24615
TSO | - | 56 | 2020 | Summer | Pc_net, [MW] | Expected | - | 6.669 | 6.5163 | 5.9919 | 5.9741 | 5.9033 | 6.1388 | 6.1978 | 6.5706 | 6.905 | 6.9037 | 6.6707 | 6.4419 | 5.9677 | 6.0441 | 5.6325 | 5.7574 | 5.9501 | 6.1218 | 6.7406 | 7.5239 | 6.7027 | 7.0532 | 6.7844 | 5.4322
TSO | - | 56 | 2020 | Summer | Qc, [MVAr] | Expected | - | -1.9038 | -1.9673 | -1.925 | -1.9673 | -1.9462 | -2.2 | -1.8404 | -0.67692 | -0.50769 | -0.31731 | -0.35962 | 0.10577 | 0.35962 | 0.33846 | -0.084615 | -0.63462 | -0.40192 | -0.61346 | -0.93077 | -0.63462 | -1.0154 | -0.67692 | -1.1212 | -1.2692
TSO | - | 57 | 2020 | Summer | Pc, [MW] | Expected | - | 3.5175 | 2.948 | 2.5125 | 2.412 | 2.412 | 2.8475 | 3.9865 | 4.422 | 5.3265 | 5.5945 | 5.762 | 6.231 | 6.7 | 6.5325 | 6.298 | 5.9965 | 5.628 | 5.5945 | 5.293 | 5.5275 | 5.5275 | 5.762 | 5.36 | 4.0535
TSO | - | 57 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.18411 | 0.14502 | 0.10336 | 0.10123 | 0.099258 | 0.12617 | 0.31919 | 0.37029 | 0.41944 | 0.33841 | 0.35874 | 0.35161 | 0.48345 | 0.46444 | 0.34156 | 0.30318 | 0.29292 | 0.33791 | 0.27511 | 0.27497 | 0.26419 | 0.26164 | 0.28784 | 0.23644
TSO | - | 57 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.14779 | 0.12511 | 0.089769 | 0.090394 | 0.091801 | 0.11872 | 0.27588 | 0.36516 | 0.39718 | 0.34085 | 0.36476 | 0.36662 | 0.59249 | 0.56017 | 0.3477 | 0.29565 | 0.27707 | 0.31511 | 0.27153 | 0.30666 | 0.28764 | 0.25977 | 0.26846 | 0.18418
TSO | - | 57 | 2020 | Summer | Pc_net, [MW] | Expected | - | 3.5538 | 2.9679 | 2.5261 | 2.4228 | 2.4195 | 2.855 | 4.0298 | 4.4271 | 5.3488 | 5.5921 | 5.756 | 6.216 | 6.591 | 6.4368 | 6.2919 | 6.004 | 5.6438 | 5.6173 | 5.2966 | 5.4958 | 5.5041 | 5.7639 | 5.3794 | 4.1058
TSO | - | 57 | 2020 | Summer | Qc, [MVAr] | Expected | - | -1.0968 | -1.2903 | -1.3548 | -1.4194 | -1.3548 | -2 | -1.5161 | -0.77419 | -0.22581 | -0.096774 | 0.032258 | 0.032258 | 0.48387 | 0.45161 | 0.45161 | -0.19355 | -0.032258 | -0.19355 | -0.54839 | -0.51613 | -0.48387 | -0.35484 | -0.54839 | -0.83871
DSO | 2 | 1 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 2 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.16852 | 0.15885 | 0.12871 | 0.1476 | 0.15023 | 0.14706 | 0.16487 | 0.17574 | 0.17878 | 0.17178 | 0.16983 | 0.18692 | 0.18187 | 0.1854 | 0.18157 | 0.1845 | 0.18127 | 0.15769 | 0.19601 | 0.2 | 0.1805 | 0.19065 | 0.18255 | 0.16117
DSO | 2 | 2 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.015956 | 0.014613 | 0.0099056 | 0.011757 | 0.011918 | 0.012668 | 0.024685 | 0.029538 | 0.02772 | 0.020656 | 0.020887 | 0.021739 | 0.028989 | 0.028281 | 0.019534 | 0.018258 | 0.018326 | 0.018572 | 0.02045 | 0.02125 | 0.018193 | 0.017385 | 0.019069 | 0.016828
DSO | 2 | 2 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.015847 | 0.014497 | 0.0098816 | 0.011696 | 0.011881 | 0.012626 | 0.024536 | 0.02892 | 0.027097 | 0.021058 | 0.021763 | 0.021352 | 0.029424 | 0.029878 | 0.020209 | 0.018591 | 0.018391 | 0.01824 | 0.020037 | 0.02084 | 0.017847 | 0.01712 | 0.018824 | 0.01662
DSO | 2 | 2 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.16863 | 0.15896 | 0.12873 | 0.14766 | 0.15026 | 0.1471 | 0.16502 | 0.17636 | 0.1794 | 0.17138 | 0.16896 | 0.18731 | 0.18144 | 0.1838 | 0.1809 | 0.18416 | 0.18121 | 0.15802 | 0.19643 | 0.20041 | 0.18085 | 0.19092 | 0.1828 | 0.16138
DSO | 2 | 2 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.10111 | 0.095308 | 0.077226 | 0.088561 | 0.090137 | 0.088234 | 0.098923 | 0.10545 | 0.10727 | 0.10307 | 0.1019 | 0.11215 | 0.10912 | 0.11124 | 0.10894 | 0.1107 | 0.10876 | 0.094613 | 0.11761 | 0.12 | 0.1083 | 0.11439 | 0.10953 | 0.096705
DSO | 2 | 3 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.33705 | 0.31769 | 0.25742 | 0.2952 | 0.30046 | 0.29411 | 0.32974 | 0.35149 | 0.35755 | 0.34356 | 0.33966 | 0.37384 | 0.36374 | 0.3708 | 0.36315 | 0.36899 | 0.36254 | 0.31538 | 0.39203 | 0.4 | 0.36101 | 0.3813 | 0.3651 | 0.32235
DSO | 2 | 3 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.032239 | 0.029569 | 0.019959 | 0.023749 | 0.024049 | 0.025574 | 0.049938 | 0.059813 | 0.055822 | 0.040999 | 0.04107 | 0.042524 | 0.056535 | 0.054969 | 0.038617 | 0.036292 | 0.036666 | 0.03745 | 0.04132 | 0.042941 | 0.036701 | 0.035029 | 0.038492 | 0.034036
DSO | 2 | 3 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.031367 | 0.028652 | 0.019616 | 0.023155 | 0.02355 | 0.025014 | 0.048503 | 0.057103 | 0.053812 | 0.042427 | 0.04423 | 0.043659 | 0.060291 | 0.061349 | 0.040869 | 0.037406 | 0.036768 | 0.036174 | 0.039654 | 0.04124 | 0.03538 | 0.033981 | 0.037294 | 0.032861
DSO | 2 | 3 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.33792 | 0.31861 | 0.25776 | 0.2958 | 0.30095 | 0.29467 | 0.33118 | 0.3542 | 0.35956 | 0.34213 | 0.3365 | 0.3727 | 0.35999 | 0.36442 | 0.36089 | 0.36788 | 0.36244 | 0.31665 | 0.39369 | 0.4017 | 0.36233 | 0.38235 | 0.3663 | 0.32352
DSO | 2 | 3 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.21066 | 0.19856 | 0.16089 | 0.1845 | 0.18778 | 0.18382 | 0.20609 | 0.21968 | 0.22347 | 0.21472 | 0.21229 | 0.23365 | 0.22734 | 0.23175 | 0.22697 | 0.23062 | 0.22659 | 0.19711 | 0.24502 | 0.25 | 0.22563 | 0.23832 | 0.22819 | 0.20147
DSO | 2 | 4 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.77255 | 0.69878 | 0.66068 | 0.65832 | 0.65832 | 0.65832 | 0.81629 | 1.0543 | 1.3178 | 1.5 | 1.4558 | 1.5 | 1.5 | 1.5 | 1.5 | 1.3746 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.1544 | 0.97094
DSO | 2 | 4 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.076806 | 0.067653 | 0.052903 | 0.054849 | 0.054391 | 0.059248 | 0.13041 | 0.19323 | 0.22028 | 0.17461 | 0.16059 | 0.15581 | 0.20685 | 0.19131 | 0.15126 | 0.13341 | 0.13704 | 0.16954 | 0.14955 | 0.15217 | 0.14375 | 0.12854 | 0.12877 | 0.10871
DSO | 2 | 4 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.068985 | 0.060406 | 0.048665 | 0.049751 | 0.049901 | 0.053983 | 0.11329 | 0.15747 | 0.1838 | 0.18964 | 0.205 | 0.18999 | 0.27491 | 0.27923 | 0.17706 | 0.14113 | 0.13148 | 0.13994 | 0.12427 | 0.12681 | 0.12094 | 0.11139 | 0.11085 | 0.092789
DSO | 2 | 4 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.78037 | 0.70602 | 0.66492 | 0.66341 | 0.66281 | 0.66358 | 0.83341 | 1.0901 | 1.3543 | 1.485 | 1.4113 | 1.4658 | 1.4319 | 1.4121 | 1.4742 | 1.3668 | 1.3312 | 1.3553 | 1.3509 | 1.351 | 1.3485 | 1.3428 | 1.1723 | 0.98686
DSO | 2 | 4 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.51907 | 0.51907 | 0.11872 | 0.064884 | 0.064884 | 0.064884 | 0.12882 | 0.69209 | 0.85428 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
DSO | 2 | 5 | 2020 | Summer | Pc, [MW] | 0 | 0 | 1.6151 | 1.4252 | 1.317 | 1.2821 | 1.3178 | 1.3481 | 2.0865 | 2.4806 | 2.7425 | 2.8268 | 2.371 | 2.9158 | 3 | 2.9043 | 2.683 | 2.5635 | 2.561 | 2.4993 | 2.2676 | 2.4539 | 2.6634 | 2.4607 | 1.9817 | 1.655
DSO | 2 | 5 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.17462 | 0.15058 | 0.11305 | 0.11497 | 0.11693 | 0.13126 | 0.37885 | 0.50415 | 0.47309 | 0.32063 | 0.24687 | 0.20976 | 0.30181 | 0.30227 | 0.26526 | 0.24822 | 0.27363 | 0.33851 | 0.27014 | 0.30025 | 0.3055 | 0.24973 | 0.23455 | 0.19964
DSO | 2 | 5 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.13017 | 0.1106 | 0.089417 | 0.088735 | 0.091843 | 0.10061 | 0.24404 | 0.32097 | 0.36781 | 0.36581 | 0.34856 | 0.46242 | 0.66172 | 0.60878 | 0.32201 | 0.26378 | 0.24511 | 0.24496 | 0.19823 | 0.21618 | 0.22629 | 0.19562 | 0.17679 | 0.14382
DSO | 2 | 5 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 1.6595 | 1.4652 | 1.3406 | 1.3083 | 1.3429 | 1.3787 | 2.2213 | 2.6638 | 2.8477 | 2.7817 | 2.2693 | 2.6631 | 2.6401 | 2.5978 | 2.6263 | 2.5479 | 2.5895 | 2.5929 | 2.3395 | 2.538 | 2.7426 | 2.5148 | 2.0394 | 1.7108
DSO | 2 | 5 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 1.2167 | 1.0737 | 0.99213 | 0.96582 | 0.99274 | 1.0156 | 1.5718 | 1.8687 | 2.066 | 2.1295 | 1.7861 | 2.1965 | 2.26 | 2.1879 | 2.0212 | 1.9312 | 1.9293 | 1.8828 | 1.7082 | 1.8486 | 2.0064 | 1.8537 | 1.4929 | 1.2467
DSO | 2 | 6 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.33553 | 0.31113 | 0.32626 | 0.31141 | 0.33069 | 0.31114 | 0.3048 | 0.49982 | 0.62689 | 0.6359 | 0.60372 | 0.55442 | 0.50512 | 0.50116 | 0.50453 | 0.58277 | 0.57937 | 0.5719 | 0.53794 | 0.61745 | 0.75955 | 0.8 | 0.65277 | 0.41683
DSO | 2 | 6 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.032992 | 0.029828 | 0.026086 | 0.025795 | 0.02729 | 0.027899 | 0.047833 | 0.088707 | 0.10064 | 0.074808 | 0.068855 | 0.054328 | 0.069754 | 0.069348 | 0.052132 | 0.056867 | 0.060293 | 0.070175 | 0.058265 | 0.068426 | 0.079664 | 0.075716 | 0.071611 | 0.04561
DSO | 2 | 6 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.030327 | 0.027189 | 0.024072 | 0.023686 | 0.0251 | 0.025618 | 0.043162 | 0.077548 | 0.091586 | 0.079608 | 0.082757 | 0.073484 | 0.092479 | 0.087863 | 0.058301 | 0.059527 | 0.057061 | 0.063335 | 0.052848 | 0.061516 | 0.071995 | 0.069072 | 0.063888 | 0.040895
DSO | 2 | 6 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.33819 | 0.31377 | 0.32828 | 0.31352 | 0.33288 | 0.31343 | 0.30947 | 0.51097 | 0.63594 | 0.6311 | 0.58982 | 0.53526 | 0.4824 | 0.48265 | 0.49836 | 0.58011 | 0.5826 | 0.57874 | 0.54336 | 0.62436 | 0.76722 | 0.80664 | 0.66049 | 0.42155
DSO | 2 | 6 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.20971 | 0.19446 | 0.20392 | 0.19463 | 0.20668 | 0.19447 | 0.1905 | 0.31239 | 0.39181 | 0.39743 | 0.37732 | 0.34651 | 0.3157 | 0.31323 | 0.31533 | 0.36423 | 0.3621 | 0.35744 | 0.33621 | 0.3859 | 0.47472 | 0.5 | 0.40798 | 0.26052
DSO | 2 | 7 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.10959 | 0.091255 | 0.091255 | 0.091255 | 0.091255 | 0.091255 | 0.11319 | 0.17784 | 0.19985 | 0.19985 | 0.18557 | 0.18594 | 0.18834 | 0.18834 | 0.17786 | 0.14634 | 0.14634 | 0.14634 | 0.14634 | 0.18126 | 0.2 | 0.2 | 0.16568 | 0.1473
DSO | 2 | 7 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.010577 | 0.0085464 | 0.0071454 | 0.0073954 | 0.007367 | 0.00801 | 0.017485 | 0.030949 | 0.031725 | 0.024069 | 0.022387 | 0.019847 | 0.027874 | 0.027785 | 0.018899 | 0.014514 | 0.015116 | 0.017514 | 0.015474 | 0.019621 | 0.020457 | 0.018487 | 0.017637 | 0.01577
DSO | 2 | 7 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.010104 | 0.008177 | 0.0068834 | 0.007104 | 0.0070899 | 0.007686 | 0.016308 | 0.028205 | 0.029555 | 0.024462 | 0.024214 | 0.023018 | 0.032615 | 0.031296 | 0.020032 | 0.014714 | 0.014525 | 0.016649 | 0.014753 | 0.018526 | 0.019476 | 0.01771 | 0.016754 | 0.014799
DSO | 2 | 7 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.11006 | 0.091624 | 0.091517 | 0.091546 | 0.091532 | 0.091579 | 0.11437 | 0.18058 | 0.20202 | 0.19946 | 0.18374 | 0.18276 | 0.1836 | 0.18483 | 0.17673 | 0.14614 | 0.14693 | 0.1472 | 0.14706 | 0.18236 | 0.20098 | 0.20078 | 0.16656 | 0.14827
DSO | 2 | 7 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.065753 | 0.054753 | 0.054753 | 0.054753 | 0.054753 | 0.054753 | 0.067916 | 0.1067 | 0.11991 | 0.11991 | 0.11134 | 0.11156 | 0.113 | 0.113 | 0.10672 | 0.087802 | 0.087802 | 0.087802 | 0.087802 | 0.10876 | 0.12 | 0.12 | 0.099408 | 0.088379
DSO | 2 | 8 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.74532 | 0.66961 | 0.64438 | 0.65079 | 0.64566 | 0.65796 | 0.68073 | 0.72983 | 0.82916 | 0.92201 | 1 | 0.97899 | 0.99845 | 0.92451 | 0.85711 | 0.83688 | 0.80862 | 0.80113 | 0.81112 | 0.83757 | 0.96252 | 0.99369 | 0.90902 | 0.74856
DSO | 2 | 8 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.083138 | 0.073198 | 0.057547 | 0.060638 | 0.059631 | 0.066774 | 0.12697 | 0.14897 | 0.15004 | 0.098463 | 0.090258 | 0.068695 | 0.08877 | 0.097812 | 0.074101 | 0.074386 | 0.093928 | 0.10852 | 0.096338 | 0.10166 | 0.10812 | 0.099966 | 0.10898 | 0.092291
DSO | 2 | 8 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.057515 | 0.049516 | 0.041516 | 0.042767 | 0.042657 | 0.046396 | 0.07626 | 0.093793 | 0.1042 | 0.12543 | 0.16087 | 0.157 | 0.23191 | 0.1922 | 0.11351 | 0.092762 | 0.069862 | 0.078503 | 0.071202 | 0.074611 | 0.084066 | 0.079877 | 0.07971 | 0.063058
DSO | 2 | 8 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.77094 | 0.69329 | 0.66041 | 0.66867 | 0.66263 | 0.67834 | 0.73143 | 0.78501 | 0.87501 | 0.89505 | 0.92939 | 0.89069 | 0.85532 | 0.83012 | 0.81771 | 0.8185 | 0.83269 | 0.83115 | 0.83626 | 0.86462 | 0.98657 | 1.0138 | 0.93829 | 0.77779
DSO | 2 | 8 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.4621 | 0.41516 | 0.39951 | 0.40349 | 0.40031 | 0.40794 | 0.42205 | 0.45249 | 0.51408 | 0.57165 | 0.62 | 0.60697 | 0.61904 | 0.5732 | 0.53141 | 0.51887 | 0.50134 | 0.4967 | 0.50289 | 0.51929 | 0.59676 | 0.61609 | 0.56359 | 0.46411
DSO | 2 | 9 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.37266 | 0.33481 | 0.32219 | 0.3254 | 0.32283 | 0.32898 | 0.34036 | 0.36492 | 0.41458 | 0.46101 | 0.5 | 0.4895 | 0.49923 | 0.46225 | 0.42856 | 0.41844 | 0.40431 | 0.40056 | 0.40556 | 0.41878 | 0.48126 | 0.49685 | 0.45451 | 0.37428
DSO | 2 | 9 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.03865 | 0.032719 | 0.025565 | 0.026837 | 0.026091 | 0.029201 | 0.055477 | 0.069214 | 0.062982 | 0.051735 | 0.055666 | 0.053594 | 0.070929 | 0.061205 | 0.044616 | 0.040409 | 0.040703 | 0.047928 | 0.042994 | 0.045734 | 0.049192 | 0.045097 | 0.055156 | 0.042897
DSO | 2 | 9 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.031676 | 0.028638 | 0.023967 | 0.024865 | 0.025053 | 0.027384 | 0.046135 | 0.052168 | 0.064139 | 0.060212 | 0.069899 | 0.059252 | 0.089411 | 0.083801 | 0.049187 | 0.043165 | 0.041192 | 0.045584 | 0.040775 | 0.042399 | 0.0469 | 0.044824 | 0.039189 | 0.034778
DSO | 2 | 9 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.37963 | 0.33889 | 0.32379 | 0.32737 | 0.32387 | 0.3308 | 0.34971 | 0.38196 | 0.41342 | 0.45253 | 0.48577 | 0.48384 | 0.48075 | 0.43966 | 0.42398 | 0.41568 | 0.40382 | 0.40291 | 0.40778 | 0.42212 | 0.48355 | 0.49712 | 0.47048 | 0.3824
DSO | 2 | 9 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.24901 | -0.23919 | -0.23177 | -0.23414 | -0.21874 | -0.22035 | -0.31 | -0.24481 | -0.19856 | -0.11844 | -0.15135 | -0.15355 | -0.15355 | -0.14273 | -0.2322 | -0.21881 | -0.2237 | -0.22526 | -0.22851 | -0.2536 | -0.23227 | -0.18265 | -0.19727 | -0.19918
DSO | 2 | 20 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.74532 | 0.66961 | 0.64438 | 0.65079 | 0.64566 | 0.65796 | 0.68073 | 0.72983 | 0.82916 | 0.92201 | 1 | 0.97899 | 0.99845 | 0.92451 | 0.85711 | 0.83688 | 0.80862 | 0.80113 | 0.81112 | 0.83757 | 0.96252 | 0.99369 | 0.90902 | 0.74856
DSO | 2 | 20 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.06902 | 0.060623 | 0.048999 | 0.051098 | 0.050507 | 0.055841 | 0.098619 | 0.11861 | 0.12981 | 0.10012 | 0.12092 | 0.1369 | 0.1808 | 0.14904 | 0.089457 | 0.074328 | 0.084271 | 0.091829 | 0.082067 | 0.086073 | 0.093901 | 0.087937 | 0.092102 | 0.076303
DSO | 2 | 20 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.071633 | 0.06209 | 0.050064 | 0.052307 | 0.05178 | 0.05733 | 0.10461 | 0.12415 | 0.12443 | 0.12377 | 0.13021 | 0.088786 | 0.13988 | 0.14097 | 0.09815 | 0.092819 | 0.079519 | 0.095195 | 0.085473 | 0.090195 | 0.098283 | 0.091905 | 0.096588 | 0.079046
DSO | 2 | 20 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.74271 | 0.66814 | 0.64331 | 0.64959 | 0.64439 | 0.65647 | 0.67474 | 0.72429 | 0.83454 | 0.89837 | 0.99071 | 1.0271 | 1.0394 | 0.93257 | 0.84842 | 0.81839 | 0.81337 | 0.79776 | 0.80771 | 0.83345 | 0.95813 | 0.98972 | 0.90454 | 0.74581
DSO | 2 | 20 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.49801 | -0.47837 | -0.46355 | -0.46828 | -0.43747 | -0.44071 | -0.62 | -0.48961 | -0.39713 | -0.23688 | -0.30269 | -0.3071 | -0.3071 | -0.28546 | -0.46441 | -0.43762 | -0.44741 | -0.45051 | -0.45702 | -0.5072 | -0.46453 | -0.3653 | -0.39453 | -0.39836
DSO | 2 | 21 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.19307 | 0.16941 | 0.1613 | 0.14892 | 0.14992 | 0.15317 | 0.18853 | 0.23541 | 0.26782 | 0.27307 | 0.27333 | 0.29445 | 0.2966 | 0.29769 | 0.28015 | 0.26735 | 0.26583 | 0.26861 | 0.27575 | 0.28856 | 0.29606 | 0.3 | 0.27432 | 0.23493
DSO | 2 | 21 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.018039 | 0.015418 | 0.012356 | 0.011771 | 0.011826 | 0.013122 | 0.027722 | 0.03817 | 0.041084 | 0.031799 | 0.034501 | 0.037145 | 0.050746 | 0.048678 | 0.030395 | 0.025474 | 0.027649 | 0.030623 | 0.027799 | 0.02956 | 0.028788 | 0.02656 | 0.027918 | 0.023998
DSO | 2 | 21 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.018397 | 0.015628 | 0.012442 | 0.011891 | 0.011925 | 0.013224 | 0.02856 | 0.040135 | 0.041035 | 0.034511 | 0.03414 | 0.030735 | 0.044514 | 0.044707 | 0.030924 | 0.027923 | 0.026197 | 0.032085 | 0.029158 | 0.031168 | 0.030326 | 0.027735 | 0.029024 | 0.024757
DSO | 2 | 21 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.19272 | 0.1692 | 0.16122 | 0.1488 | 0.14982 | 0.15307 | 0.18769 | 0.23344 | 0.26787 | 0.27036 | 0.27369 | 0.30086 | 0.30283 | 0.30166 | 0.27962 | 0.2649 | 0.26728 | 0.26715 | 0.27439 | 0.28695 | 0.29452 | 0.29882 | 0.27322 | 0.23417
DSO | 2 | 21 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.12662 | 0.10789 | 0.1071 | 0.097069 | 0.10959 | 0.099924 | 0.10719 | 0.14759 | 0.17363 | 0.17926 | 0.18642 | 0.18884 | 0.18794 | 0.19 | 0.17288 | 0.16123 | 0.15244 | 0.15393 | 0.1552 | 0.1538 | 0.15455 | 0.16696 | 0.14649 | 0.14038
DSO | 2 | 22 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.11295 | 0.10107 | 0.094729 | 0.094577 | 0.096623 | 0.098436 | 0.118 | 0.14713 | 0.16499 | 0.17382 | 0.17816 | 0.19376 | 0.19601 | 0.2 | 0.18991 | 0.18008 | 0.1677 | 0.16358 | 0.15659 | 0.15583 | 0.15467 | 0.15573 | 0.14636 | 0.12546
DSO | 2 | 22 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.01116 | 0.0096841 | 0.0075635 | 0.0078056 | 0.007957 | 0.008892 | 0.01909 | 0.026084 | 0.020933 | 0.019499 | 0.021556 | 0.023056 | 0.031295 | 0.03077 | 0.01979 | 0.01662 | 0.0161 | 0.020211 | 0.016792 | 0.017053 | 0.016033 | 0.014596 | 0.015868 | 0.013617
DSO | 2 | 22 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.010157 | 0.0088374 | 0.0069995 | 0.0072218 | 0.0073503 | 0.0080391 | 0.016138 | 0.022855 | 0.029658 | 0.022709 | 0.023184 | 0.021614 | 0.03166 | 0.031969 | 0.021777 | 0.019348 | 0.017868 | 0.017976 | 0.015553 | 0.015741 | 0.014849 | 0.013588 | 0.014513 | 0.012421
DSO | 2 | 22 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.11396 | 0.10191 | 0.095293 | 0.095161 | 0.097229 | 0.099289 | 0.12095 | 0.15036 | 0.15627 | 0.17061 | 0.17653 | 0.19521 | 0.19565 | 0.1988 | 0.18792 | 0.17735 | 0.16593 | 0.16581 | 0.15783 | 0.15714 | 0.15585 | 0.15673 | 0.14772 | 0.12666
DSO | 2 | 22 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.06145 | 0.06145 | 0.06145 | 0.06145 | 0.06145 | 0.049485 | 0.047445 | 0.078364 | 0.089463 | 0.10209 | 0.10422 | 0.11582 | 0.11516 | 0.12 | 0.11467 | 0.11365 | 0.088404 | 0.078137 | 0.077338 | 0.074333 | 0.073554 | 0.074093 | 0.071288 | 0.070393
DSO | 2 | 23 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.53759 | 0.67402 | 0.35985 | 0.58757 | 0.50555 | 0.48152 | 0.64649 | 0.63833 | 0.72785 | 0.74796 | 0.6424 | 0.67292 | 0.70504 | 0.68958 | 0.71947 | 0.78058 | 0.8 | 0.77532 | 0.68602 | 0.76435 | 0.77242 | 0.72717 | 0.70702 | 0.76916
DSO | 2 | 23 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.049105 | 0.059785 | 0.027601 | 0.045715 | 0.039685 | 0.041206 | 0.091124 | 0.095274 | 0.11211 | 0.079489 | 0.088216 | 0.097261 | 0.13997 | 0.13287 | 0.081435 | 0.065925 | 0.095115 | 0.08063 | 0.064051 | 0.071236 | 0.068276 | 0.060347 | 0.068187 | 0.073945
DSO | 2 | 23 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.052347 | 0.063736 | 0.027719 | 0.047644 | 0.040406 | 0.041617 | 0.10188 | 0.11705 | 0.11107 | 0.10214 | 0.073111 | 0.05787 | 0.086473 | 0.083444 | 0.076045 | 0.089977 | 0.066929 | 0.10037 | 0.077649 | 0.089623 | 0.085952 | 0.07126 | 0.078572 | 0.08568
DSO | 2 | 23 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.53435 | 0.67007 | 0.35973 | 0.58564 | 0.50483 | 0.48111 | 0.63573 | 0.61655 | 0.72889 | 0.72531 | 0.65751 | 0.71231 | 0.75853 | 0.739 | 0.72486 | 0.75652 | 0.82819 | 0.75558 | 0.67242 | 0.74597 | 0.75475 | 0.71626 | 0.69663 | 0.75743
DSO | 2 | 23 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.336 | 0.42126 | 0.2249 | 0.36723 | 0.31597 | 0.30095 | 0.40406 | 0.39896 | 0.4549 | 0.46747 | 0.4015 | 0.42057 | 0.44065 | 0.43099 | 0.44967 | 0.48786 | 0.5 | 0.48457 | 0.42876 | 0.47772 | 0.48276 | 0.45448 | 0.44189 | 0.48073
DSO | 2 | 24 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.39869 | 0.39459 | 0.3803 | 0.37336 | 0.37088 | 0.37619 | 0.37311 | 0.45608 | 0.49071 | 0.48433 | 0.47629 | 0.48215 | 0.5 | 0.49041 | 0.45245 | 0.46639 | 0.47176 | 0.45613 | 0.43299 | 0.42755 | 0.42625 | 0.42145 | 0.38948 | 0.37661
DSO | 2 | 24 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.037816 | 0.03659 | 0.030097 | 0.030128 | 0.030015 | 0.03325 | 0.056532 | 0.073726 | 0.07992 | 0.047703 | 0.059213 | 0.063984 | 0.088042 | 0.084025 | 0.046776 | 0.038115 | 0.048469 | 0.05195 | 0.043024 | 0.04314 | 0.040971 | 0.037155 | 0.039981 | 0.038978
DSO | 2 | 24 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.037422 | 0.035724 | 0.028368 | 0.029195 | 0.028741 | 0.031456 | 0.054858 | 0.077981 | 0.070544 | 0.069909 | 0.060398 | 0.047168 | 0.072547 | 0.069814 | 0.052258 | 0.055036 | 0.047088 | 0.054535 | 0.046412 | 0.046839 | 0.044139 | 0.039121 | 0.040866 | 0.03918
DSO | 2 | 24 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.39908 | 0.39546 | 0.38203 | 0.37429 | 0.37216 | 0.37799 | 0.37479 | 0.45183 | 0.50009 | 0.46213 | 0.47511 | 0.49897 | 0.51549 | 0.50462 | 0.44697 | 0.44947 | 0.47314 | 0.45355 | 0.42961 | 0.42385 | 0.42309 | 0.41948 | 0.3886 | 0.3764
DSO | 2 | 24 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0.26121 | 0.24621 | 0.1995 | 0.22878 | 0.23285 | 0.22794 | 0.25555 | 0.2724 | 0.2771 | 0.26626 | 0.26324 | 0.28972 | 0.2819 | 0.28737 | 0.28144 | 0.28597 | 0.28097 | 0.24442 | 0.30382 | 0.31 | 0.27978 | 0.29551 | 0.28295 | 0.24982
DSO | 2 | 25 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.70949 | 0.66817 | 0.64254 | 0.58426 | 0.56296 | 0.5921 | 0.62975 | 0.8457 | 0.92388 | 0.98505 | 0.89745 | 0.94242 | 0.94334 | 0.92037 | 0.79214 | 0.82573 | 0.87409 | 0.86895 | 0.90759 | 0.95532 | 1 | 0.91806 | 0.7879 | 0.72722
DSO | 2 | 25 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.064879 | 0.059485 | 0.050029 | 0.046608 | 0.044962 | 0.050431 | 0.088415 | 0.11675 | 0.14714 | 0.089568 | 0.12851 | 0.14599 | 0.19998 | 0.19247 | 0.088812 | 0.064251 | 0.098889 | 0.086764 | 0.079155 | 0.083709 | 0.081973 | 0.072922 | 0.074707 | 0.069669
DSO | 2 | 25 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.069013 | 0.062966 | 0.04875 | 0.046225 | 0.044225 | 0.051411 | 0.099592 | 0.16456 | 0.13614 | 0.14963 | 0.096866 | 0.071273 | 0.10299 | 0.096246 | 0.084573 | 0.10067 | 0.078162 | 0.11609 | 0.10831 | 0.11734 | 0.1177 | 0.093231 | 0.08884 | 0.081252
DSO | 2 | 25 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.70535 | 0.66469 | 0.64382 | 0.58464 | 0.5637 | 0.59112 | 0.61857 | 0.79789 | 0.93488 | 0.92498 | 0.9291 | 1.0171 | 1.0403 | 1.0166 | 0.79638 | 0.78931 | 0.89482 | 0.83962 | 0.87844 | 0.92169 | 0.96428 | 0.89775 | 0.77376 | 0.71564
DSO | 2 | 25 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.17656 | -0.41419 | -0.091097 | -0.075434 | -0.26769 | -0.62 | -0.48637 | -0.40024 | -0.35462 | -0.35462 | -0.40772 | -0.35469 | -0.35469 | -0.38208 | -0.42278 | -0.47339 | -0.49103 | -0.41523 | -0.36887 | -0.044674 | 0.083546 | -0.12485 | -0.34788 | -0.48569
DSO | 2 | 26 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0.11291 | 0.10611 | 0.097702 | 0.10179 | 0.099852 | 0.10193 | 0.14441 | 0.18488 | 0.19388 | 0.18176 | 0.17786 | 0.19116 | 0.2 | 0.18566 | 0.16925 | 0.16055 | 0.16404 | 0.15861 | 0.1549 | 0.16874 | 0.1768 | 0.16502 | 0.1446 | 0.12043
DSO | 2 | 26 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0.011256 | 0.01028 | 0.0075995 | 0.0085478 | 0.0083688 | 0.0092826 | 0.022957 | 0.031318 | 0.025574 | 0.019594 | 0.021513 | 0.023019 | 0.032144 | 0.029051 | 0.017608 | 0.014561 | 0.015983 | 0.020489 | 0.016442 | 0.018203 | 0.017956 | 0.015332 | 0.015692 | 0.013103
DSO | 2 | 26 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0.010053 | 0.0091652 | 0.0074206 | 0.007625 | 0.0074502 | 0.0082489 | 0.020156 | 0.030178 | 0.033875 | 0.024543 | 0.023151 | 0.02105 | 0.032091 | 0.029189 | 0.019439 | 0.017505 | 0.017244 | 0.016537 | 0.015553 | 0.017308 | 0.017347 | 0.014534 | 0.014323 | 0.011889
DSO | 2 | 26 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0.11412 | 0.10722 | 0.097881 | 0.10271 | 0.10077 | 0.10296 | 0.14721 | 0.18602 | 0.18558 | 0.17681 | 0.17622 | 0.19313 | 0.20005 | 0.18552 | 0.16742 | 0.1576 | 0.16278 | 0.16256 | 0.15579 | 0.16963 | 0.17741 | 0.16582 | 0.14597 | 0.12164
DSO | 2 | 26 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | -0.019413 | -0.0161 | -0.12 | -0.0025763 | -0.0016692 | 0.0072622 | -0.036265 | -0.076026 | -0.082404 | -0.053662 | -0.056092 | -0.060049 | -0.045626 | -0.051249 | -0.10035 | -0.031616 | -0.034006 | -0.03626 | -0.02921 | -0.012766 | -0.020353 | -0.011326 | 0.0090538 | 0.033922
DSO | 2 | 50 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Pc, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Flex Up, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Flex Down, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Pc_net, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Qc, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 1 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 2 | 2020 | Summer | Pc, [MW] | Expected | - | 0.16852 | 0.15885 | 0.12871 | 0.1476 | 0.15023 | 0.14706 | 0.16487 | 0.17574 | 0.17878 | 0.17178 | 0.16983 | 0.18692 | 0.18187 | 0.1854 | 0.18157 | 0.1845 | 0.18127 | 0.15769 | 0.19601 | 0.2 | 0.1805 | 0.19065 | 0.18255 | 0.16117
DSO | 2 | 2 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.015956 | 0.014613 | 0.0099056 | 0.011757 | 0.011918 | 0.012668 | 0.024685 | 0.029538 | 0.02772 | 0.020656 | 0.020887 | 0.021739 | 0.028989 | 0.028281 | 0.019534 | 0.018258 | 0.018326 | 0.018572 | 0.02045 | 0.02125 | 0.018193 | 0.017385 | 0.019069 | 0.016828
DSO | 2 | 2 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.015847 | 0.014497 | 0.0098816 | 0.011696 | 0.011881 | 0.012626 | 0.024536 | 0.02892 | 0.027097 | 0.021058 | 0.021763 | 0.021352 | 0.029424 | 0.029878 | 0.020209 | 0.018591 | 0.018391 | 0.01824 | 0.020037 | 0.02084 | 0.017847 | 0.01712 | 0.018824 | 0.01662
DSO | 2 | 2 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.16863 | 0.15896 | 0.12873 | 0.14766 | 0.15026 | 0.1471 | 0.16502 | 0.17636 | 0.1794 | 0.17138 | 0.16896 | 0.18731 | 0.18144 | 0.1838 | 0.1809 | 0.18416 | 0.18121 | 0.15802 | 0.19643 | 0.20041 | 0.18085 | 0.19092 | 0.1828 | 0.16138
DSO | 2 | 2 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.10111 | 0.095308 | 0.077226 | 0.088561 | 0.090137 | 0.088234 | 0.098923 | 0.10545 | 0.10727 | 0.10307 | 0.1019 | 0.11215 | 0.10912 | 0.11124 | 0.10894 | 0.1107 | 0.10876 | 0.094613 | 0.11761 | 0.12 | 0.1083 | 0.11439 | 0.10953 | 0.096705
DSO | 2 | 3 | 2020 | Summer | Pc, [MW] | Expected | - | 0.33705 | 0.31769 | 0.25742 | 0.2952 | 0.30046 | 0.29411 | 0.32974 | 0.35149 | 0.35755 | 0.34356 | 0.33966 | 0.37384 | 0.36374 | 0.3708 | 0.36315 | 0.36899 | 0.36254 | 0.31538 | 0.39203 | 0.4 | 0.36101 | 0.3813 | 0.3651 | 0.32235
DSO | 2 | 3 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.032239 | 0.029569 | 0.019959 | 0.023749 | 0.024049 | 0.025574 | 0.049938 | 0.059813 | 0.055822 | 0.040999 | 0.04107 | 0.042524 | 0.056535 | 0.054969 | 0.038617 | 0.036292 | 0.036666 | 0.03745 | 0.04132 | 0.042941 | 0.036701 | 0.035029 | 0.038492 | 0.034036
DSO | 2 | 3 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.031367 | 0.028652 | 0.019616 | 0.023155 | 0.02355 | 0.025014 | 0.048503 | 0.057103 | 0.053812 | 0.042427 | 0.04423 | 0.043659 | 0.060291 | 0.061349 | 0.040869 | 0.037406 | 0.036768 | 0.036174 | 0.039654 | 0.04124 | 0.03538 | 0.033981 | 0.037294 | 0.032861
DSO | 2 | 3 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.33792 | 0.31861 | 0.25776 | 0.2958 | 0.30095 | 0.29467 | 0.33118 | 0.3542 | 0.35956 | 0.34213 | 0.3365 | 0.3727 | 0.35999 | 0.36442 | 0.36089 | 0.36788 | 0.36244 | 0.31665 | 0.39369 | 0.4017 | 0.36233 | 0.38235 | 0.3663 | 0.32352
DSO | 2 | 3 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.21066 | 0.19856 | 0.16089 | 0.1845 | 0.18778 | 0.18382 | 0.20609 | 0.21968 | 0.22347 | 0.21472 | 0.21229 | 0.23365 | 0.22734 | 0.23175 | 0.22697 | 0.23062 | 0.22659 | 0.19711 | 0.24502 | 0.25 | 0.22563 | 0.23832 | 0.22819 | 0.20147
DSO | 2 | 4 | 2020 | Summer | Pc, [MW] | Expected | - | 0.77255 | 0.69878 | 0.66068 | 0.65832 | 0.65832 | 0.65832 | 0.81629 | 1.0543 | 1.3178 | 1.5 | 1.4558 | 1.5 | 1.5 | 1.5 | 1.5 | 1.3746 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.1544 | 0.97094
DSO | 2 | 4 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.076806 | 0.067653 | 0.052903 | 0.054849 | 0.054391 | 0.059248 | 0.13041 | 0.19323 | 0.22028 | 0.17461 | 0.16059 | 0.15581 | 0.20685 | 0.19131 | 0.15126 | 0.13341 | 0.13704 | 0.16954 | 0.14955 | 0.15217 | 0.14375 | 0.12854 | 0.12877 | 0.10871
DSO | 2 | 4 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.068985 | 0.060406 | 0.048665 | 0.049751 | 0.049901 | 0.053983 | 0.11329 | 0.15747 | 0.1838 | 0.18964 | 0.205 | 0.18999 | 0.27491 | 0.27923 | 0.17706 | 0.14113 | 0.13148 | 0.13994 | 0.12427 | 0.12681 | 0.12094 | 0.11139 | 0.11085 | 0.092789
DSO | 2 | 4 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.78037 | 0.70602 | 0.66492 | 0.66341 | 0.66281 | 0.66358 | 0.83341 | 1.0901 | 1.3543 | 1.485 | 1.4113 | 1.4658 | 1.4319 | 1.4121 | 1.4742 | 1.3668 | 1.3312 | 1.3553 | 1.3509 | 1.351 | 1.3485 | 1.3428 | 1.1723 | 0.98686
DSO | 2 | 4 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.51907 | 0.51907 | 0.11872 | 0.064884 | 0.064884 | 0.064884 | 0.12882 | 0.69209 | 0.85428 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
DSO | 2 | 5 | 2020 | Summer | Pc, [MW] | Expected | - | 1.6151 | 1.4252 | 1.317 | 1.2821 | 1.3178 | 1.3481 | 2.0865 | 2.4806 | 2.7425 | 2.8268 | 2.371 | 2.9158 | 3 | 2.9043 | 2.683 | 2.5635 | 2.561 | 2.4993 | 2.2676 | 2.4539 | 2.6634 | 2.4607 | 1.9817 | 1.655
DSO | 2 | 5 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.17462 | 0.15058 | 0.11305 | 0.11497 | 0.11693 | 0.13126 | 0.37885 | 0.50415 | 0.47309 | 0.32063 | 0.24687 | 0.20976 | 0.30181 | 0.30227 | 0.26526 | 0.24822 | 0.27363 | 0.33851 | 0.27014 | 0.30025 | 0.3055 | 0.24973 | 0.23455 | 0.19964
DSO | 2 | 5 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.13017 | 0.1106 | 0.089417 | 0.088735 | 0.091843 | 0.10061 | 0.24404 | 0.32097 | 0.36781 | 0.36581 | 0.34856 | 0.46242 | 0.66172 | 0.60878 | 0.32201 | 0.26378 | 0.24511 | 0.24496 | 0.19823 | 0.21618 | 0.22629 | 0.19562 | 0.17679 | 0.14382
DSO | 2 | 5 | 2020 | Summer | Pc_net, [MW] | Expected | - | 1.6595 | 1.4652 | 1.3406 | 1.3083 | 1.3429 | 1.3787 | 2.2213 | 2.6638 | 2.8477 | 2.7817 | 2.2693 | 2.6631 | 2.6401 | 2.5978 | 2.6263 | 2.5479 | 2.5895 | 2.5929 | 2.3395 | 2.538 | 2.7426 | 2.5148 | 2.0394 | 1.7108
DSO | 2 | 5 | 2020 | Summer | Qc, [MVAr] | Expected | - | 1.2167 | 1.0737 | 0.99213 | 0.96582 | 0.99274 | 1.0156 | 1.5718 | 1.8687 | 2.066 | 2.1295 | 1.7861 | 2.1965 | 2.26 | 2.1879 | 2.0212 | 1.9312 | 1.9293 | 1.8828 | 1.7082 | 1.8486 | 2.0064 | 1.8537 | 1.4929 | 1.2467
DSO | 2 | 6 | 2020 | Summer | Pc, [MW] | Expected | - | 0.33553 | 0.31113 | 0.32626 | 0.31141 | 0.33069 | 0.31114 | 0.3048 | 0.49982 | 0.62689 | 0.6359 | 0.60372 | 0.55442 | 0.50512 | 0.50116 | 0.50453 | 0.58277 | 0.57937 | 0.5719 | 0.53794 | 0.61745 | 0.75955 | 0.8 | 0.65277 | 0.41683
DSO | 2 | 6 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.032992 | 0.029828 | 0.026086 | 0.025795 | 0.02729 | 0.027899 | 0.047833 | 0.088707 | 0.10064 | 0.074808 | 0.068855 | 0.054328 | 0.069754 | 0.069348 | 0.052132 | 0.056867 | 0.060293 | 0.070175 | 0.058265 | 0.068426 | 0.079664 | 0.075716 | 0.071611 | 0.04561
DSO | 2 | 6 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.030327 | 0.027189 | 0.024072 | 0.023686 | 0.0251 | 0.025618 | 0.043162 | 0.077548 | 0.091586 | 0.079608 | 0.082757 | 0.073484 | 0.092479 | 0.087863 | 0.058301 | 0.059527 | 0.057061 | 0.063335 | 0.052848 | 0.061516 | 0.071995 | 0.069072 | 0.063888 | 0.040895
DSO | 2 | 6 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.33819 | 0.31377 | 0.32828 | 0.31352 | 0.33288 | 0.31343 | 0.30947 | 0.51097 | 0.63594 | 0.6311 | 0.58982 | 0.53526 | 0.4824 | 0.48265 | 0.49836 | 0.58011 | 0.5826 | 0.57874 | 0.54336 | 0.62436 | 0.76722 | 0.80664 | 0.66049 | 0.42155
DSO | 2 | 6 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.20971 | 0.19446 | 0.20392 | 0.19463 | 0.20668 | 0.19447 | 0.1905 | 0.31239 | 0.39181 | 0.39743 | 0.37732 | 0.34651 | 0.3157 | 0.31323 | 0.31533 | 0.36423 | 0.3621 | 0.35744 | 0.33621 | 0.3859 | 0.47472 | 0.5 | 0.40798 | 0.26052
DSO | 2 | 7 | 2020 | Summer | Pc, [MW] | Expected | - | 0.10959 | 0.091255 | 0.091255 | 0.091255 | 0.091255 | 0.091255 | 0.11319 | 0.17784 | 0.19985 | 0.19985 | 0.18557 | 0.18594 | 0.18834 | 0.18834 | 0.17786 | 0.14634 | 0.14634 | 0.14634 | 0.14634 | 0.18126 | 0.2 | 0.2 | 0.16568 | 0.1473
DSO | 2 | 7 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.010577 | 0.0085464 | 0.0071454 | 0.0073954 | 0.007367 | 0.00801 | 0.017485 | 0.030949 | 0.031725 | 0.024069 | 0.022387 | 0.019847 | 0.027874 | 0.027785 | 0.018899 | 0.014514 | 0.015116 | 0.017514 | 0.015474 | 0.019621 | 0.020457 | 0.018487 | 0.017637 | 0.01577
DSO | 2 | 7 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.010104 | 0.008177 | 0.0068834 | 0.007104 | 0.0070899 | 0.007686 | 0.016308 | 0.028205 | 0.029555 | 0.024462 | 0.024214 | 0.023018 | 0.032615 | 0.031296 | 0.020032 | 0.014714 | 0.014525 | 0.016649 | 0.014753 | 0.018526 | 0.019476 | 0.01771 | 0.016754 | 0.014799
DSO | 2 | 7 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.11006 | 0.091624 | 0.091517 | 0.091546 | 0.091532 | 0.091579 | 0.11437 | 0.18058 | 0.20202 | 0.19946 | 0.18374 | 0.18276 | 0.1836 | 0.18483 | 0.17673 | 0.14614 | 0.14693 | 0.1472 | 0.14706 | 0.18236 | 0.20098 | 0.20078 | 0.16656 | 0.14827
DSO | 2 | 7 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.065753 | 0.054753 | 0.054753 | 0.054753 | 0.054753 | 0.054753 | 0.067916 | 0.1067 | 0.11991 | 0.11991 | 0.11134 | 0.11156 | 0.113 | 0.113 | 0.10672 | 0.087802 | 0.087802 | 0.087802 | 0.087802 | 0.10876 | 0.12 | 0.12 | 0.099408 | 0.088379
DSO | 2 | 8 | 2020 | Summer | Pc, [MW] | Expected | - | 0.74532 | 0.66961 | 0.64438 | 0.65079 | 0.64566 | 0.65796 | 0.68073 | 0.72983 | 0.82916 | 0.92201 | 1 | 0.97899 | 0.99845 | 0.92451 | 0.85711 | 0.83688 | 0.80862 | 0.80113 | 0.81112 | 0.83757 | 0.96252 | 0.99369 | 0.90902 | 0.74856
DSO | 2 | 8 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.083138 | 0.073198 | 0.057547 | 0.060638 | 0.059631 | 0.066774 | 0.12697 | 0.14897 | 0.15004 | 0.098463 | 0.090258 | 0.068695 | 0.08877 | 0.097812 | 0.074101 | 0.074386 | 0.093928 | 0.10852 | 0.096338 | 0.10166 | 0.10812 | 0.099966 | 0.10898 | 0.092291
DSO | 2 | 8 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.057515 | 0.049516 | 0.041516 | 0.042767 | 0.042657 | 0.046396 | 0.07626 | 0.093793 | 0.1042 | 0.12543 | 0.16087 | 0.157 | 0.23191 | 0.1922 | 0.11351 | 0.092762 | 0.069862 | 0.078503 | 0.071202 | 0.074611 | 0.084066 | 0.079877 | 0.07971 | 0.063058
DSO | 2 | 8 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.77094 | 0.69329 | 0.66041 | 0.66867 | 0.66263 | 0.67834 | 0.73143 | 0.78501 | 0.87501 | 0.89505 | 0.92939 | 0.89069 | 0.85532 | 0.83012 | 0.81771 | 0.8185 | 0.83269 | 0.83115 | 0.83626 | 0.86462 | 0.98657 | 1.0138 | 0.93829 | 0.77779
DSO | 2 | 8 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.4621 | 0.41516 | 0.39951 | 0.40349 | 0.40031 | 0.40794 | 0.42205 | 0.45249 | 0.51408 | 0.57165 | 0.62 | 0.60697 | 0.61904 | 0.5732 | 0.53141 | 0.51887 | 0.50134 | 0.4967 | 0.50289 | 0.51929 | 0.59676 | 0.61609 | 0.56359 | 0.46411
DSO | 2 | 9 | 2020 | Summer | Pc, [MW] | Expected | - | 0.37266 | 0.33481 | 0.32219 | 0.3254 | 0.32283 | 0.32898 | 0.34036 | 0.36492 | 0.41458 | 0.46101 | 0.5 | 0.4895 | 0.49923 | 0.46225 | 0.42856 | 0.41844 | 0.40431 | 0.40056 | 0.40556 | 0.41878 | 0.48126 | 0.49685 | 0.45451 | 0.37428
DSO | 2 | 9 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.03865 | 0.032719 | 0.025565 | 0.026837 | 0.026091 | 0.029201 | 0.055477 | 0.069214 | 0.062982 | 0.051735 | 0.055666 | 0.053594 | 0.070929 | 0.061205 | 0.044616 | 0.040409 | 0.040703 | 0.047928 | 0.042994 | 0.045734 | 0.049192 | 0.045097 | 0.055156 | 0.042897
DSO | 2 | 9 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.031676 | 0.028638 | 0.023967 | 0.024865 | 0.025053 | 0.027384 | 0.046135 | 0.052168 | 0.064139 | 0.060212 | 0.069899 | 0.059252 | 0.089411 | 0.083801 | 0.049187 | 0.043165 | 0.041192 | 0.045584 | 0.040775 | 0.042399 | 0.0469 | 0.044824 | 0.039189 | 0.034778
DSO | 2 | 9 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.37963 | 0.33889 | 0.32379 | 0.32737 | 0.32387 | 0.3308 | 0.34971 | 0.38196 | 0.41342 | 0.45253 | 0.48577 | 0.48384 | 0.48075 | 0.43966 | 0.42398 | 0.41568 | 0.40382 | 0.40291 | 0.40778 | 0.42212 | 0.48355 | 0.49712 | 0.47048 | 0.3824
DSO | 2 | 9 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.24901 | -0.23919 | -0.23177 | -0.23414 | -0.21874 | -0.22035 | -0.31 | -0.24481 | -0.19856 | -0.11844 | -0.15135 | -0.15355 | -0.15355 | -0.14273 | -0.2322 | -0.21881 | -0.2237 | -0.22526 | -0.22851 | -0.2536 | -0.23227 | -0.18265 | -0.19727 | -0.19918
DSO | 2 | 20 | 2020 | Summer | Pc, [MW] | Expected | - | 0.74532 | 0.66961 | 0.64438 | 0.65079 | 0.64566 | 0.65796 | 0.68073 | 0.72983 | 0.82916 | 0.92201 | 1 | 0.97899 | 0.99845 | 0.92451 | 0.85711 | 0.83688 | 0.80862 | 0.80113 | 0.81112 | 0.83757 | 0.96252 | 0.99369 | 0.90902 | 0.74856
DSO | 2 | 20 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.06902 | 0.060623 | 0.048999 | 0.051098 | 0.050507 | 0.055841 | 0.098619 | 0.11861 | 0.12981 | 0.10012 | 0.12092 | 0.1369 | 0.1808 | 0.14904 | 0.089457 | 0.074328 | 0.084271 | 0.091829 | 0.082067 | 0.086073 | 0.093901 | 0.087937 | 0.092102 | 0.076303
DSO | 2 | 20 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.071633 | 0.06209 | 0.050064 | 0.052307 | 0.05178 | 0.05733 | 0.10461 | 0.12415 | 0.12443 | 0.12377 | 0.13021 | 0.088786 | 0.13988 | 0.14097 | 0.09815 | 0.092819 | 0.079519 | 0.095195 | 0.085473 | 0.090195 | 0.098283 | 0.091905 | 0.096588 | 0.079046
DSO | 2 | 20 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.74271 | 0.66814 | 0.64331 | 0.64959 | 0.64439 | 0.65647 | 0.67474 | 0.72429 | 0.83454 | 0.89837 | 0.99071 | 1.0271 | 1.0394 | 0.93257 | 0.84842 | 0.81839 | 0.81337 | 0.79776 | 0.80771 | 0.83345 | 0.95813 | 0.98972 | 0.90454 | 0.74581
DSO | 2 | 20 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.49801 | -0.47837 | -0.46355 | -0.46828 | -0.43747 | -0.44071 | -0.62 | -0.48961 | -0.39713 | -0.23688 | -0.30269 | -0.3071 | -0.3071 | -0.28546 | -0.46441 | -0.43762 | -0.44741 | -0.45051 | -0.45702 | -0.5072 | -0.46453 | -0.3653 | -0.39453 | -0.39836
DSO | 2 | 21 | 2020 | Summer | Pc, [MW] | Expected | - | 0.19307 | 0.16941 | 0.1613 | 0.14892 | 0.14992 | 0.15317 | 0.18853 | 0.23541 | 0.26782 | 0.27307 | 0.27333 | 0.29445 | 0.2966 | 0.29769 | 0.28015 | 0.26735 | 0.26583 | 0.26861 | 0.27575 | 0.28856 | 0.29606 | 0.3 | 0.27432 | 0.23493
DSO | 2 | 21 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.018039 | 0.015418 | 0.012356 | 0.011771 | 0.011826 | 0.013122 | 0.027722 | 0.03817 | 0.041084 | 0.031799 | 0.034501 | 0.037145 | 0.050746 | 0.048678 | 0.030395 | 0.025474 | 0.027649 | 0.030623 | 0.027799 | 0.02956 | 0.028788 | 0.02656 | 0.027918 | 0.023998
DSO | 2 | 21 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.018397 | 0.015628 | 0.012442 | 0.011891 | 0.011925 | 0.013224 | 0.02856 | 0.040135 | 0.041035 | 0.034511 | 0.03414 | 0.030735 | 0.044514 | 0.044707 | 0.030924 | 0.027923 | 0.026197 | 0.032085 | 0.029158 | 0.031168 | 0.030326 | 0.027735 | 0.029024 | 0.024757
DSO | 2 | 21 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.19272 | 0.1692 | 0.16122 | 0.1488 | 0.14982 | 0.15307 | 0.18769 | 0.23344 | 0.26787 | 0.27036 | 0.27369 | 0.30086 | 0.30283 | 0.30166 | 0.27962 | 0.2649 | 0.26728 | 0.26715 | 0.27439 | 0.28695 | 0.29452 | 0.29882 | 0.27322 | 0.23417
DSO | 2 | 21 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.12662 | 0.10789 | 0.1071 | 0.097069 | 0.10959 | 0.099924 | 0.10719 | 0.14759 | 0.17363 | 0.17926 | 0.18642 | 0.18884 | 0.18794 | 0.19 | 0.17288 | 0.16123 | 0.15244 | 0.15393 | 0.1552 | 0.1538 | 0.15455 | 0.16696 | 0.14649 | 0.14038
DSO | 2 | 22 | 2020 | Summer | Pc, [MW] | Expected | - | 0.11295 | 0.10107 | 0.094729 | 0.094577 | 0.096623 | 0.098436 | 0.118 | 0.14713 | 0.16499 | 0.17382 | 0.17816 | 0.19376 | 0.19601 | 0.2 | 0.18991 | 0.18008 | 0.1677 | 0.16358 | 0.15659 | 0.15583 | 0.15467 | 0.15573 | 0.14636 | 0.12546
DSO | 2 | 22 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.01116 | 0.0096841 | 0.0075635 | 0.0078056 | 0.007957 | 0.008892 | 0.01909 | 0.026084 | 0.020933 | 0.019499 | 0.021556 | 0.023056 | 0.031295 | 0.03077 | 0.01979 | 0.01662 | 0.0161 | 0.020211 | 0.016792 | 0.017053 | 0.016033 | 0.014596 | 0.015868 | 0.013617
DSO | 2 | 22 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.010157 | 0.0088374 | 0.0069995 | 0.0072218 | 0.0073503 | 0.0080391 | 0.016138 | 0.022855 | 0.029658 | 0.022709 | 0.023184 | 0.021614 | 0.03166 | 0.031969 | 0.021777 | 0.019348 | 0.017868 | 0.017976 | 0.015553 | 0.015741 | 0.014849 | 0.013588 | 0.014513 | 0.012421
DSO | 2 | 22 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.11396 | 0.10191 | 0.095293 | 0.095161 | 0.097229 | 0.099289 | 0.12095 | 0.15036 | 0.15627 | 0.17061 | 0.17653 | 0.19521 | 0.19565 | 0.1988 | 0.18792 | 0.17735 | 0.16593 | 0.16581 | 0.15783 | 0.15714 | 0.15585 | 0.15673 | 0.14772 | 0.12666
DSO | 2 | 22 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.06145 | 0.06145 | 0.06145 | 0.06145 | 0.06145 | 0.049485 | 0.047445 | 0.078364 | 0.089463 | 0.10209 | 0.10422 | 0.11582 | 0.11516 | 0.12 | 0.11467 | 0.11365 | 0.088404 | 0.078137 | 0.077338 | 0.074333 | 0.073554 | 0.074093 | 0.071288 | 0.070393
DSO | 2 | 23 | 2020 | Summer | Pc, [MW] | Expected | - | 0.53759 | 0.67402 | 0.35985 | 0.58757 | 0.50555 | 0.48152 | 0.64649 | 0.63833 | 0.72785 | 0.74796 | 0.6424 | 0.67292 | 0.70504 | 0.68958 | 0.71947 | 0.78058 | 0.8 | 0.77532 | 0.68602 | 0.76435 | 0.77242 | 0.72717 | 0.70702 | 0.76916
DSO | 2 | 23 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.049105 | 0.059785 | 0.027601 | 0.045715 | 0.039685 | 0.041206 | 0.091124 | 0.095274 | 0.11211 | 0.079489 | 0.088216 | 0.097261 | 0.13997 | 0.13287 | 0.081435 | 0.065925 | 0.095115 | 0.08063 | 0.064051 | 0.071236 | 0.068276 | 0.060347 | 0.068187 | 0.073945
DSO | 2 | 23 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.052347 | 0.063736 | 0.027719 | 0.047644 | 0.040406 | 0.041617 | 0.10188 | 0.11705 | 0.11107 | 0.10214 | 0.073111 | 0.05787 | 0.086473 | 0.083444 | 0.076045 | 0.089977 | 0.066929 | 0.10037 | 0.077649 | 0.089623 | 0.085952 | 0.07126 | 0.078572 | 0.08568
DSO | 2 | 23 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.53435 | 0.67007 | 0.35973 | 0.58564 | 0.50483 | 0.48111 | 0.63573 | 0.61655 | 0.72889 | 0.72531 | 0.65751 | 0.71231 | 0.75853 | 0.739 | 0.72486 | 0.75652 | 0.82819 | 0.75558 | 0.67242 | 0.74597 | 0.75475 | 0.71626 | 0.69663 | 0.75743
DSO | 2 | 23 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.336 | 0.42126 | 0.2249 | 0.36723 | 0.31597 | 0.30095 | 0.40406 | 0.39896 | 0.4549 | 0.46747 | 0.4015 | 0.42057 | 0.44065 | 0.43099 | 0.44967 | 0.48786 | 0.5 | 0.48457 | 0.42876 | 0.47772 | 0.48276 | 0.45448 | 0.44189 | 0.48073
DSO | 2 | 24 | 2020 | Summer | Pc, [MW] | Expected | - | 0.39869 | 0.39459 | 0.3803 | 0.37336 | 0.37088 | 0.37619 | 0.37311 | 0.45608 | 0.49071 | 0.48433 | 0.47629 | 0.48215 | 0.5 | 0.49041 | 0.45245 | 0.46639 | 0.47176 | 0.45613 | 0.43299 | 0.42755 | 0.42625 | 0.42145 | 0.38948 | 0.37661
DSO | 2 | 24 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.037816 | 0.03659 | 0.030097 | 0.030128 | 0.030015 | 0.03325 | 0.056532 | 0.073726 | 0.07992 | 0.047703 | 0.059213 | 0.063984 | 0.088042 | 0.084025 | 0.046776 | 0.038115 | 0.048469 | 0.05195 | 0.043024 | 0.04314 | 0.040971 | 0.037155 | 0.039981 | 0.038978
DSO | 2 | 24 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.037422 | 0.035724 | 0.028368 | 0.029195 | 0.028741 | 0.031456 | 0.054858 | 0.077981 | 0.070544 | 0.069909 | 0.060398 | 0.047168 | 0.072547 | 0.069814 | 0.052258 | 0.055036 | 0.047088 | 0.054535 | 0.046412 | 0.046839 | 0.044139 | 0.039121 | 0.040866 | 0.03918
DSO | 2 | 24 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.39908 | 0.39546 | 0.38203 | 0.37429 | 0.37216 | 0.37799 | 0.37479 | 0.45183 | 0.50009 | 0.46213 | 0.47511 | 0.49897 | 0.51549 | 0.50462 | 0.44697 | 0.44947 | 0.47314 | 0.45355 | 0.42961 | 0.42385 | 0.42309 | 0.41948 | 0.3886 | 0.3764
DSO | 2 | 24 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0.26121 | 0.24621 | 0.1995 | 0.22878 | 0.23285 | 0.22794 | 0.25555 | 0.2724 | 0.2771 | 0.26626 | 0.26324 | 0.28972 | 0.2819 | 0.28737 | 0.28144 | 0.28597 | 0.28097 | 0.24442 | 0.30382 | 0.31 | 0.27978 | 0.29551 | 0.28295 | 0.24982
DSO | 2 | 25 | 2020 | Summer | Pc, [MW] | Expected | - | 0.70949 | 0.66817 | 0.64254 | 0.58426 | 0.56296 | 0.5921 | 0.62975 | 0.8457 | 0.92388 | 0.98505 | 0.89745 | 0.94242 | 0.94334 | 0.92037 | 0.79214 | 0.82573 | 0.87409 | 0.86895 | 0.90759 | 0.95532 | 1 | 0.91806 | 0.7879 | 0.72722
DSO | 2 | 25 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.064879 | 0.059485 | 0.050029 | 0.046608 | 0.044962 | 0.050431 | 0.088415 | 0.11675 | 0.14714 | 0.089568 | 0.12851 | 0.14599 | 0.19998 | 0.19247 | 0.088812 | 0.064251 | 0.098889 | 0.086764 | 0.079155 | 0.083709 | 0.081973 | 0.072922 | 0.074707 | 0.069669
DSO | 2 | 25 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.069013 | 0.062966 | 0.04875 | 0.046225 | 0.044225 | 0.051411 | 0.099592 | 0.16456 | 0.13614 | 0.14963 | 0.096866 | 0.071273 | 0.10299 | 0.096246 | 0.084573 | 0.10067 | 0.078162 | 0.11609 | 0.10831 | 0.11734 | 0.1177 | 0.093231 | 0.08884 | 0.081252
DSO | 2 | 25 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.70535 | 0.66469 | 0.64382 | 0.58464 | 0.5637 | 0.59112 | 0.61857 | 0.79789 | 0.93488 | 0.92498 | 0.9291 | 1.0171 | 1.0403 | 1.0166 | 0.79638 | 0.78931 | 0.89482 | 0.83962 | 0.87844 | 0.92169 | 0.96428 | 0.89775 | 0.77376 | 0.71564
DSO | 2 | 25 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.17656 | -0.41419 | -0.091097 | -0.075434 | -0.26769 | -0.62 | -0.48637 | -0.40024 | -0.35462 | -0.35462 | -0.40772 | -0.35469 | -0.35469 | -0.38208 | -0.42278 | -0.47339 | -0.49103 | -0.41523 | -0.36887 | -0.044674 | 0.083546 | -0.12485 | -0.34788 | -0.48569
DSO | 2 | 26 | 2020 | Summer | Pc, [MW] | Expected | - | 0.11291 | 0.10611 | 0.097702 | 0.10179 | 0.099852 | 0.10193 | 0.14441 | 0.18488 | 0.19388 | 0.18176 | 0.17786 | 0.19116 | 0.2 | 0.18566 | 0.16925 | 0.16055 | 0.16404 | 0.15861 | 0.1549 | 0.16874 | 0.1768 | 0.16502 | 0.1446 | 0.12043
DSO | 2 | 26 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0.011256 | 0.01028 | 0.0075995 | 0.0085478 | 0.0083688 | 0.0092826 | 0.022957 | 0.031318 | 0.025574 | 0.019594 | 0.021513 | 0.023019 | 0.032144 | 0.029051 | 0.017608 | 0.014561 | 0.015983 | 0.020489 | 0.016442 | 0.018203 | 0.017956 | 0.015332 | 0.015692 | 0.013103
DSO | 2 | 26 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0.010053 | 0.0091652 | 0.0074206 | 0.007625 | 0.0074502 | 0.0082489 | 0.020156 | 0.030178 | 0.033875 | 0.024543 | 0.023151 | 0.02105 | 0.032091 | 0.029189 | 0.019439 | 0.017505 | 0.017244 | 0.016537 | 0.015553 | 0.017308 | 0.017347 | 0.014534 | 0.014323 | 0.011889
DSO | 2 | 26 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0.11412 | 0.10722 | 0.097881 | 0.10271 | 0.10077 | 0.10296 | 0.14721 | 0.18602 | 0.18558 | 0.17681 | 0.17622 | 0.19313 | 0.20005 | 0.18552 | 0.16742 | 0.1576 | 0.16278 | 0.16256 | 0.15579 | 0.16963 | 0.17741 | 0.16582 | 0.14597 | 0.12164
DSO | 2 | 26 | 2020 | Summer | Qc, [MVAr] | Expected | - | -0.019413 | -0.0161 | -0.12 | -0.0025763 | -0.0016692 | 0.0072622 | -0.036265 | -0.076026 | -0.082404 | -0.053662 | -0.056092 | -0.060049 | -0.045626 | -0.051249 | -0.10035 | -0.031616 | -0.034006 | -0.03626 | -0.02921 | -0.012766 | -0.020353 | -0.011326 | 0.0090538 | 0.033922
DSO | 2 | 50 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 50 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Pc, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Flex Up, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Flex Down, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Pc_net, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 2020 | Summer | Qc, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Generation
Operator | Connection Node ID | Network Node ID | Generator ID | Type | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
TSO | - | 1 | 1 | Reference (TN) | 2020 | Summer | Pg, [MW] | 0 | 0 | 191.6556 | 229.8015 | 227.8261 | 206.5103 | 202.0283 | 209.0349 | 175.8402 | 18.6888 | 82.2133 | 116.687 | 75.2624 | 120.5428 | 120.5391 | 107.7732 | 197.1494 | 179.0357 | 102.5145 | 111.2828 | 107.276 | 76.2859 | 79.0377 | 176.7954 | 163.6219 | 170.3303
TSO | - | 1 | 1 | Reference (TN) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0.75143 | -13.8656 | -33.8587 | -32.5548 | -34.9898 | -55.8432 | 4.5107 | 100.5886 | 84.5638 | 28.9332 | 69.2353 | 56.0253 | 46.4999 | 40.5987 | -19.2892 | 13.8544 | 11.7265 | 35.3727 | 88.4502 | 60.3495 | 68.5283 | 28.8574 | 22.0261 | 31.3849
TSO | - | 2 | 2 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 15.7412 | 22.379 | 13.1491 | 9.9512 | 13.7853 | 9.443 | 16.1767 | 57.2105 | 67.2148 | 74.3149 | 72.4693 | 53.8023 | 52.4158 | 63.7772 | 14.1561 | 17.6284 | 73.86 | 65.5626 | 44.013 | 74.1959 | 73.0988 | 14.2648 | 18.769 | 14.525
TSO | - | 2 | 2 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | -8.9974 | -11.4691 | -12.8876 | -12.8767 | -12.7779 | -14.0106 | -8.8798 | 11.9046 | 9.8943 | -0.33581 | 7.2132 | 2.5634 | 3.7905 | 4.7305 | -2.5705 | -6.2788 | -6.7116 | -5.4773 | 1.1993 | 1.9353 | -0.5551 | 13.1552 | 18.1393 | -5.1256
TSO | - | 3 | 3 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 25.0267 | 31.8542 | 19.0753 | 12.7084 | 17.1494 | 12.4199 | 30.0258 | 127.0536 | 96.141 | 94.4547 | 106.0377 | 59.1451 | 58.539 | 90.7848 | 48.1262 | 41.6295 | 83.0956 | 80.8352 | 37.7628 | 57.8309 | 54.3424 | 36.8854 | 57.6116 | 42.904
TSO | - | 3 | 3 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | -7.5327 | -7.8702 | -8.577 | -8.7395 | -8.7066 | -8.9837 | -7.3293 | 2.8991 | 1.1928 | 0.15223 | 15.0836 | -0.62947 | 3.6754 | 7.2483 | -4.3732 | -4.258 | -5.6525 | -5.2128 | 33.2415 | 18.5703 | 5.9948 | 18.3366 | -0.38319 | -6.5643
TSO | - | 6 | 4 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 14.6653 | 6.7169 | 18.6529 | 13.3787 | 13.0432 | 11.6601 | 12.4868 | 12.5926 | 29.5612 | 46.4389 | 41.31 | 28.7728 | 30.1018 | 60.329 | 32.7606 | 29.1362 | 44.7707 | 44.6712 | 16.8115 | 11.1257 | 11.3048 | 23.3442 | 23.7247 | 16.2537
TSO | - | 6 | 4 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 21.0188 | 19.8348 | 20.4087 | 19.729 | 19.2095 | 16.8731 | 19.6352 | 13.9955 | 15.0559 | 14.8401 | 16.8899 | 9.1127 | 10.9175 | 11.022 | 16.9677 | 15.7955 | 16.1202 | 16.1068 | 12.2343 | 11.1216 | 10.0585 | 12.2466 | 15.2864 | 20.2239
TSO | - | 8 | 5 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 187.7891 | 179.1866 | 177.0623 | 146.9088 | 169.9599 | 177.2551 | 169.6989 | 266.2298 | 256.6415 | 239.1045 | 248.4171 | 259.4319 | 247.7745 | 220.699 | 226.5452 | 218.3418 | 208.7104 | 210.4766 | 238.8423 | 285.6084 | 267.9114 | 262.4154 | 266.5057 | 200.4451
TSO | - | 8 | 5 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | -80.5199 | -81.9019 | -83.2043 | -91.4189 | -88.7891 | -102.4429 | -89.4713 | -23.8343 | -63.1064 | -67.2905 | -49.529 | -46.0193 | -45.1751 | -44.0421 | -61.5347 | -77.7468 | -81.9149 | -83.9399 | -23.1812 | -16.7709 | -25.0266 | -16.2015 | -31.7516 | -60.3034
TSO | - | 9 | 6 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 58.7354 | 90.3158 | 7.3323 | 55.5997 | 7.0535 | 6.7088 | 71.6999 | 89.165 | 88.7871 | 84.3462 | 89.4437 | 89.7169 | 89.1296 | 84.9282 | 70.6478 | 71.6489 | 77.4065 | 76.4484 | 73.907 | 92.2402 | 92.9314 | 76.6878 | 89.5658 | 86.6474
TSO | - | 9 | 6 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0.72608 | 1.0631 | -0.13521 | -0.36568 | -0.70846 | -1.0096 | 0.64755 | 3.1675 | 2.0736 | 1.6656 | 2.0206 | 2.0211 | 2.1531 | 2.2309 | 1.4935 | 1.645 | 1.4843 | 1.5006 | 3.4936 | 3.567 | 3.2805 | 3.3474 | 2.7824 | 0.99976
TSO | - | 12 | 7 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | 0 | 0 | 233.7955 | 173.1466 | 183.5681 | 198.3137 | 224.0082 | 176.0632 | 319.3247 | 263.8661 | 276.0866 | 302.3945 | 246.5716 | 311.9556 | 317.8241 | 324.0822 | 333.6878 | 344.4803 | 327.6351 | 314.1197 | 352.5293 | 352.6648 | 352.6576 | 392.5277 | 305.3251 | 293.6388
TSO | - | 12 | 7 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | -145.5508 | -145.9267 | -147.0771 | -147.4769 | -147.4814 | -148.0725 | -144.8998 | -124.3358 | 6.8658 | 63.5552 | -4.9952 | 72.9777 | 75.5566 | 72.5417 | 43.7172 | 15.1029 | 47.4072 | 48.6105 | -138.8276 | -133.0043 | -134.7929 | -139.6447 | -139.667 | -144.8624
TSO | - | 1 | 1 | Reference (TN) | 2020 | Summer | Pg, [MW] | Expected | - | 191.6556 | 229.8015 | 227.8261 | 206.5103 | 202.0283 | 209.0349 | 175.8402 | 18.6888 | 82.2133 | 116.687 | 75.2624 | 120.5428 | 120.5391 | 107.7732 | 197.1494 | 179.0357 | 102.5145 | 111.2828 | 107.276 | 76.2859 | 79.0377 | 176.7954 | 163.6219 | 170.3303
TSO | - | 1 | 1 | Reference (TN) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0.75143 | -13.8656 | -33.8587 | -32.5548 | -34.9898 | -55.8432 | 4.5107 | 100.5886 | 84.5638 | 28.9332 | 69.2353 | 56.0253 | 46.4999 | 40.5987 | -19.2892 | 13.8544 | 11.7265 | 35.3727 | 88.4502 | 60.3495 | 68.5283 | 28.8574 | 22.0261 | 31.3849
TSO | - | 2 | 2 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 15.7412 | 22.379 | 13.1491 | 9.9512 | 13.7853 | 9.443 | 16.1767 | 57.2105 | 67.2148 | 74.3149 | 72.4693 | 53.8023 | 52.4158 | 63.7772 | 14.1561 | 17.6284 | 73.86 | 65.5626 | 44.013 | 74.1959 | 73.0988 | 14.2648 | 18.769 | 14.525
TSO | - | 2 | 2 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | -8.9974 | -11.4691 | -12.8876 | -12.8767 | -12.7779 | -14.0106 | -8.8798 | 11.9046 | 9.8943 | -0.33581 | 7.2132 | 2.5634 | 3.7905 | 4.7305 | -2.5705 | -6.2788 | -6.7116 | -5.4773 | 1.1993 | 1.9353 | -0.5551 | 13.1552 | 18.1393 | -5.1256
TSO | - | 3 | 3 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 25.0267 | 31.8542 | 19.0753 | 12.7084 | 17.1494 | 12.4199 | 30.0258 | 127.0536 | 96.141 | 94.4547 | 106.0377 | 59.1451 | 58.539 | 90.7848 | 48.1262 | 41.6295 | 83.0956 | 80.8352 | 37.7628 | 57.8309 | 54.3424 | 36.8854 | 57.6116 | 42.904
TSO | - | 3 | 3 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | -7.5327 | -7.8702 | -8.577 | -8.7395 | -8.7066 | -8.9837 | -7.3293 | 2.8991 | 1.1928 | 0.15223 | 15.0836 | -0.62947 | 3.6754 | 7.2483 | -4.3732 | -4.258 | -5.6525 | -5.2128 | 33.2415 | 18.5703 | 5.9948 | 18.3366 | -0.38319 | -6.5643
TSO | - | 6 | 4 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 14.6653 | 6.7169 | 18.6529 | 13.3787 | 13.0432 | 11.6601 | 12.4868 | 12.5926 | 29.5612 | 46.4389 | 41.31 | 28.7728 | 30.1018 | 60.329 | 32.7606 | 29.1362 | 44.7707 | 44.6712 | 16.8115 | 11.1257 | 11.3048 | 23.3442 | 23.7247 | 16.2537
TSO | - | 6 | 4 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | 21.0188 | 19.8348 | 20.4087 | 19.729 | 19.2095 | 16.8731 | 19.6352 | 13.9955 | 15.0559 | 14.8401 | 16.8899 | 9.1127 | 10.9175 | 11.022 | 16.9677 | 15.7955 | 16.1202 | 16.1068 | 12.2343 | 11.1216 | 10.0585 | 12.2466 | 15.2864 | 20.2239
TSO | - | 8 | 5 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 187.7891 | 179.1866 | 177.0623 | 146.9088 | 169.9599 | 177.2551 | 169.6989 | 266.2298 | 256.6415 | 239.1045 | 248.4171 | 259.4319 | 247.7745 | 220.699 | 226.5452 | 218.3418 | 208.7104 | 210.4766 | 238.8423 | 285.6084 | 267.9114 | 262.4154 | 266.5057 | 200.4451
TSO | - | 8 | 5 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | -80.5199 | -81.9019 | -83.2043 | -91.4189 | -88.7891 | -102.4429 | -89.4713 | -23.8343 | -63.1064 | -67.2905 | -49.529 | -46.0193 | -45.1751 | -44.0421 | -61.5347 | -77.7468 | -81.9149 | -83.9399 | -23.1812 | -16.7709 | -25.0266 | -16.2015 | -31.7516 | -60.3034
TSO | - | 9 | 6 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 58.7354 | 90.3158 | 7.3323 | 55.5997 | 7.0535 | 6.7088 | 71.6999 | 89.165 | 88.7871 | 84.3462 | 89.4437 | 89.7169 | 89.1296 | 84.9282 | 70.6478 | 71.6489 | 77.4065 | 76.4484 | 73.907 | 92.2402 | 92.9314 | 76.6878 | 89.5658 | 86.6474
TSO | - | 9 | 6 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0.72608 | 1.0631 | -0.13521 | -0.36568 | -0.70846 | -1.0096 | 0.64755 | 3.1675 | 2.0736 | 1.6656 | 2.0206 | 2.0211 | 2.1531 | 2.2309 | 1.4935 | 1.645 | 1.4843 | 1.5006 | 3.4936 | 3.567 | 3.2805 | 3.3474 | 2.7824 | 0.99976
TSO | - | 12 | 7 | Conventional (Gas) | 2020 | Summer | Pg, [MW] | Expected | - | 233.7955 | 173.1466 | 183.5681 | 198.3137 | 224.0082 | 176.0632 | 319.3247 | 263.8661 | 276.0866 | 302.3945 | 246.5716 | 311.9556 | 317.8241 | 324.0822 | 333.6878 | 344.4803 | 327.6351 | 314.1197 | 352.5293 | 352.6648 | 352.6576 | 392.5277 | 305.3251 | 293.6388
TSO | - | 12 | 7 | Conventional (Gas) | 2020 | Summer | Qg, [MVAr] | Expected | - | -145.5508 | -145.9267 | -147.0771 | -147.4769 | -147.4814 | -148.0725 | -144.8998 | -124.3358 | 6.8658 | 63.5552 | -4.9952 | 72.9777 | 75.5566 | 72.5417 | 43.7172 | 15.1029 | 47.4072 | 48.6105 | -138.8276 | -133.0043 | -134.7929 | -139.6447 | -139.667 | -144.8624
DSO | 2 | 51 | 1 | Reference (TN) | 2020 | Summer | Pg, [MW] | 0 | 0 | 7.7545 | 7.3126 | 6.6642 | 6.8059 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.5241 | 9.4179 | 9.3925 | 9.7543 | 10.4722 | 10.5048 | 9.5242 | 8.3132
DSO | 2 | 51 | 1 | Reference (TN) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8577 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6311 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
DSO | 2 | 22 | 2 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.283 | 1.1099 | 1.6258 | 1.975 | 1.8245 | 1.9369 | 1.411 | 1.0337 | 0.55396 | 0.038135 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 22 | 2 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 24 | 3 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29017 | 1.138 | 1.6669 | 2.025 | 1.8707 | 1.9859 | 1.4467 | 1.0598 | 0.56799 | 0.039101 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 24 | 3 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 26 | 4 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5875 | 2.3042 | 3.375 | 4.1 | 3.7875 | 4.0208 | 2.9292 | 2.1458 | 1.15 | 0.079167 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 26 | 4 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 9 | 5 | Renewable (Wind) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0.33351 | 0.3399 | 0.36511 | 0.36511 | 0.39013 | 0.37753 | 0.37132 | 0.37753 | 0.6294 | 0.75524 | 0.75524 | 0.66081 | 0.69223 | 0.66081 | 0.6294 | 0.67342 | 0.75524 | 0.78666 | 0.81825 | 0.9125 | 0.81825 | 0.59798 | 0.40913 | 0.36511
DSO | 2 | 9 | 5 | Renewable (Wind) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 4 | 6 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13971 | 0.54794 | 0.80259 | 0.975 | 0.90069 | 0.95617 | 0.69657 | 0.51029 | 0.27348 | 0.018826 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 4 | 6 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 6 | 7 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14867 | 0.58307 | 0.85404 | 1.0375 | 0.95842 | 1.0175 | 0.74122 | 0.543 | 0.29101 | 0.020033 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 6 | 7 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 8 | 8 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28659 | 1.124 | 1.6463 | 2 | 1.8476 | 1.9614 | 1.4289 | 1.0467 | 0.56098 | 0.038618 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 8 | 8 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 51 | 1 | Reference (TN) | 2020 | Summer | Pg, [MW] | Expected | - | 7.7545 | 7.3126 | 6.6642 | 6.8059 | 6.7487 | 6.8718 | 8.2487 | 9.5784 | 8.692 | 3.6894 | 0.2238 | -1.0812 | -0.32762 | -1.206 | 1.5662 | 3.5577 | 6.5241 | 9.4179 | 9.3925 | 9.7543 | 10.4722 | 10.5048 | 9.5242 | 8.3132
DSO | 2 | 51 | 1 | Reference (TN) | 2020 | Summer | Qg, [MVAr] | Expected | - | 16.3199 | 17.1923 | 18.3955 | 17.7112 | 18.186 | 18.8577 | 16.9471 | 13.9749 | 13.6991 | 16.7046 | 19.3271 | 19.0418 | 18.6311 | 19.2272 | 18.8607 | 17.7638 | 15.8458 | 13.3443 | 13.4269 | 11.9396 | 10.6325 | 11.2087 | 13.4521 | 15.2621
DSO | 2 | 22 | 2 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.283 | 1.1099 | 1.6258 | 1.975 | 1.8245 | 1.9369 | 1.411 | 1.0337 | 0.55396 | 0.038135 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 22 | 2 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 24 | 3 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29017 | 1.138 | 1.6669 | 2.025 | 1.8707 | 1.9859 | 1.4467 | 1.0598 | 0.56799 | 0.039101 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 24 | 3 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 26 | 4 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5875 | 2.3042 | 3.375 | 4.1 | 3.7875 | 4.0208 | 2.9292 | 2.1458 | 1.15 | 0.079167 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 26 | 4 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 9 | 5 | Renewable (Wind) | 2020 | Summer | Pg, [MW] | Expected | - | 0.33351 | 0.3399 | 0.36511 | 0.36511 | 0.39013 | 0.37753 | 0.37132 | 0.37753 | 0.6294 | 0.75524 | 0.75524 | 0.66081 | 0.69223 | 0.66081 | 0.6294 | 0.67342 | 0.75524 | 0.78666 | 0.81825 | 0.9125 | 0.81825 | 0.59798 | 0.40913 | 0.36511
DSO | 2 | 9 | 5 | Renewable (Wind) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 4 | 6 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13971 | 0.54794 | 0.80259 | 0.975 | 0.90069 | 0.95617 | 0.69657 | 0.51029 | 0.27348 | 0.018826 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 4 | 6 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 6 | 7 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14867 | 0.58307 | 0.85404 | 1.0375 | 0.95842 | 1.0175 | 0.74122 | 0.543 | 0.29101 | 0.020033 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 6 | 7 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 8 | 8 | Renewable (Solar) | 2020 | Summer | Pg, [MW] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28659 | 1.124 | 1.6463 | 2 | 1.8476 | 1.9614 | 1.4289 | 1.0467 | 0.56098 | 0.038618 | 0 | 0 | 0 | 0 | 0 | 0
DSO | 2 | 8 | 8 | Renewable (Solar) | 2020 | Summer | Qg, [MVAr] | Expected | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Branch Losses
Operator | Connection Node ID | From Node ID | To Node ID | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
TSO | - | 1 | 2 | 2020 | Summer | P, [MW] | 0 | 0 | 64.8218 | 44.2433 | 74.9292 | 83.4301 | 73.113 | 85.2738 | 60.8658 | 122.33 | 91.4701 | 97.2487 | 109.0723 | 37.6244 | 33.1464 | 69.0375 | 56.8499 | 53.752 | 81.8558 | 66.3919 | 13.4489 | 77.1495 | 73.3743 | 62.4534 | 31.8666 | 46.917
TSO | - | 2 | 3 | 2020 | Summer | P, [MW] | 0 | 0 | 91.3487 | 84.3095 | 96.3852 | 98.4274 | 95.8615 | 99.1693 | 88.3009 | 13.7152 | 36.4833 | 45.3413 | 29.5268 | 63.2835 | 65.1004 | 51.9182 | 79.2668 | 82.8893 | 59.9775 | 58.6032 | 68.4966 | 65.1142 | 66.6804 | 84.5499 | 63.7538 | 70.7099
TSO | - | 3 | 4 | 2020 | Summer | P, [MW] | 0 | 0 | 37.7861 | 34.7146 | 34.9732 | 35.724 | 36.9852 | 39.9248 | 46.6308 | 29.5983 | 34.6396 | 31.5883 | 26.6972 | 27.5147 | 26.4178 | 26.3133 | 31.3839 | 31.6176 | 33.6438 | 32.5684 | 25.5821 | 26.3648 | 26.5453 | 32.1096 | 26.4479 | 28.5851
TSO | - | 4 | 5 | 2020 | Summer | P, [MW] | 0 | 0 | 1.3326 | 0.29021 | 2.1861 | 2.8821 | 2.1429 | 2.0964 | 0.88721 | 6.7198 | 4.1499 | 3.8996 | 3.7792 | 5.7951 | 5.6125 | 5.6801 | 2.0574 | 1.9492 | 0.79376 | 1.0177 | 3.8135 | 5.8207 | 5.7488 | 3.5629 | 2.4703 | 0.63916
TSO | - | 4 | 6 | 2020 | Summer | P, [MW] | 0 | 0 | 3.4856 | 3.1703 | 0.94066 | 0.25006 | 0.24209 | 0.24177 | 4.3387 | 17.8987 | 16.4997 | 16.7471 | 16.6275 | 20.5096 | 19.8755 | 20.4465 | 15.5668 | 14.0895 | 12.3211 | 12.3944 | 15.748 | 18.1661 | 18.7404 | 17.8219 | 17.1236 | 11.2324
TSO | - | 6 | 7 | 2020 | Summer | P, [MW] | 0 | 0 | 20.0055 | 12.6603 | 25.993 | 20.452 | 20.4459 | 18.4088 | 16.6498 | 8.5192 | 26.7354 | 44.0404 | 39.3249 | 22.7312 | 24.7146 | 55.4561 | 31.683 | 28.5439 | 46.1593 | 45.9191 | 14.5603 | 7.5263 | 7.262 | 20.3858 | 21.7929 | 17.1481
TSO | - | 6 | 8 | 2020 | Summer | P, [MW] | 0 | 0 | 0.13512 | 5.0669 | 8.6005 | 6.0703 | 6.9813 | 5.1403 | 2.539 | 24.2804 | 8.541 | 6.5408 | 1.2445 | 16.7871 | 14.2944 | 13.7321 | 7.9313 | 7.34 | 9.7899 | 9.9335 | 19.96 | 28.421 | 29.683 | 19.9985 | 20.2407 | 14.8377
TSO | - | 8 | 9 | 2020 | Summer | P, [MW] | 0 | 0 | 86.1674 | 66.28 | 111.2336 | 52.0932 | 103.9593 | 105.7009 | 65.0799 | 174.6444 | 171.1682 | 163.7908 | 180.5237 | 173.4362 | 172.8204 | 167.7256 | 158.5997 | 143.9942 | 150.6675 | 148.4257 | 122.5321 | 163.1689 | 157.4874 | 148.955 | 165.6386 | 114.2022
TSO | - | 9 | 10 | 2020 | Summer | P, [MW] | 0 | 0 | 24.7397 | 41.4735 | 17.1311 | 25.8702 | 16.5261 | 15.1462 | 22.0701 | 55.1973 | 48.4764 | 45.2885 | 49.0081 | 41.1423 | 36.6723 | 33.524 | 25.7102 | 21.299 | 33.6132 | 32.9669 | 22.0704 | 40.9057 | 39.344 | 26.1109 | 40.4166 | 40.0054
TSO | - | 9 | 11 | 2020 | Summer | P, [MW] | 0 | 0 | 21.499 | 37.7281 | 6.0946 | 17.7334 | 5.5599 | 0.356 | 19.6644 | 54.7797 | 42.4099 | 31.6901 | 39.4138 | 35.3561 | 32.1569 | 31.8353 | 22.3408 | 25.983 | 28.5992 | 27.5817 | 27.3608 | 46.2937 | 45.8137 | 32.0302 | 44.5951 | 38.8411
TSO | - | 9 | 12 | 2020 | Summer | P, [MW] | 0 | 0 | 9.195 | 23.9036 | 3.359 | 12.1693 | 4.5774 | 3.8225 | 5.4285 | 33.5389 | 26.0091 | 21.128 | 25.7141 | 16.7617 | 12.1972 | 5.5104 | 0.41577 | 4.2168 | 9.5223 | 8.5565 | 1.2029 | 17.131 | 15.7506 | 1.3144 | 17.2054 | 20.6764
TSO | - | 9 | 13 | 2020 | Summer | P, [MW] | 0 | 0 | 7.566 | 23.8448 | 5.9404 | 6.6654 | 5.5853 | 11.904 | 4.196 | 37.5937 | 25.2296 | 16.0831 | 24.2822 | 18.4279 | 15.2854 | 14.3897 | 4.4255 | 8.7283 | 12.1391 | 11.058 | 10.3495 | 28.4272 | 27.6949 | 13.5219 | 28.6266 | 25.0711
TSO | - | 13 | 14 | 2020 | Summer | P, [MW] | 0 | 0 | 21.1917 | 22.2895 | 31.9169 | 29.0174 | 31.4674 | 28.7935 | 9.2477 | 5.3169 | 17.5417 | 12.5739 | 16.718 | 6.1915 | 14.8947 | 5.5632 | 18.8447 | 13.3425 | 0.69775 | 1.7153 | 21.9807 | 7.0581 | 17.6749 | 16.1787 | 0.30117 | 8.6881
TSO | - | 13 | 15 | 2020 | Summer | P, [MW] | 0 | 0 | 51.9568 | 53.2984 | 60.5532 | 54.9763 | 59.128 | 53.1809 | 37.2815 | 31.4257 | 47.1081 | 49.4064 | 54.4139 | 29.6738 | 28.7176 | 49.1215 | 34.002 | 37.6702 | 51.7862 | 50.1648 | 13.0966 | 29.1738 | 22.821 | 29.1669 | 45.5259 | 44.8819
TSO | - | 1 | 15 | 2020 | Summer | P, [MW] | 0 | 0 | 133.6565 | 126.1558 | 142.9069 | 139.8056 | 140.2146 | 138.9093 | 120.7611 | 21.3159 | 74.3004 | 85.6992 | 76.0854 | 94.8788 | 100.1 | 105.5652 | 134.2417 | 135.1853 | 104.6333 | 106.6643 | 88.0768 | 83.4166 | 83.4389 | 129.8033 | 119.5768 | 118.4949
TSO | - | 1 | 16 | 2020 | Summer | P, [MW] | 0 | 0 | 77.3247 | 80.4134 | 82.1773 | 81.0688 | 81.1156 | 81.4988 | 68.4154 | 51.6063 | 73.2771 | 78.0688 | 76.5112 | 69.6826 | 68.0465 | 71.0162 | 72.0186 | 67.7247 | 74.5933 | 74.4506 | 45.2869 | 58.1351 | 54.9929 | 65.122 | 74.1038 | 75.723
TSO | - | 1 | 17 | 2020 | Summer | P, [MW] | 0 | 0 | 94.8635 | 96.376 | 97.9448 | 97.5475 | 98.4595 | 99.378 | 92.6835 | 81.7507 | 99.4862 | 99.7132 | 99.8792 | 98.4916 | 97.3376 | 97.4382 | 98.3266 | 90.9934 | 98.9571 | 99.0193 | 72.6631 | 83.2306 | 84.6337 | 90.7677 | 92.7939 | 94.0216
TSO | - | 3 | 15 | 2020 | Summer | P, [MW] | 0 | 0 | 47.1714 | 57.3596 | 47.9833 | 33.7207 | 43.956 | 29.4401 | 34.2302 | 130.5504 | 114.7929 | 119.9771 | 137.7973 | 72.6177 | 75.5003 | 125.2386 | 63.9176 | 62.5809 | 119.2497 | 115.3011 | 45.9608 | 78.9872 | 75.3379 | 52.3458 | 86.0367 | 63.6115
TSO | - | 4 | 18 | 2020 | Summer | P, [MW] | 0 | 0 | 39.864 | 37.5255 | 33.6592 | 32.5197 | 34.5244 | 37.9851 | 49.9805 | 54.1352 | 55.1952 | 52.1445 | 47.0253 | 53.7303 | 51.8183 | 52.3517 | 48.9173 | 47.5712 | 46.6752 | 45.9014 | 45.0757 | 50.2766 | 50.9566 | 53.4121 | 45.9676 | 40.3903
TSO | - | 5 | 6 | 2020 | Summer | P, [MW] | 0 | 0 | 5.4711 | 2.4499 | 1.5191 | 0.24234 | 1.3411 | 0.70952 | 6.2952 | 22.8586 | 24.2229 | 25.2884 | 25.1704 | 30.8968 | 29.7121 | 30.7023 | 25.9617 | 22.7549 | 20.9798 | 20.8105 | 23.088 | 24.7726 | 26.0707 | 28.2634 | 28.5275 | 18.7211
TSO | - | 7 | 8 | 2020 | Summer | P, [MW] | 0 | 0 | 27.4647 | 29.6935 | 15.5686 | 13.8908 | 11.7071 | 13.2577 | 29.1795 | 70.2693 | 58.0187 | 46.2803 | 52.2443 | 72.6369 | 69.3398 | 45.513 | 63.4131 | 57.5419 | 41.1714 | 40.5275 | 68.3658 | 78.8624 | 81.5602 | 76.6984 | 79.0678 | 59.3193
TSO | - | 10 | 12 | 2020 | Summer | P, [MW] | 0 | 0 | 10.6779 | 1.9072 | 14.3572 | 5.1762 | 10.7553 | 10.7262 | 16.036 | 5.8178 | 4.4842 | 12.0835 | 5.6314 | 16.8586 | 21.6202 | 33.1012 | 36.1942 | 39.1123 | 23.6018 | 25.0374 | 31.2188 | 13.2805 | 14.4843 | 30.6108 | 12.4622 | 3.7775
TSO | - | 11 | 13 | 2020 | Summer | P, [MW] | 0 | 0 | 8.6198 | 7.8345 | 19.9691 | 6.1853 | 18.6016 | 26.2619 | 13.8387 | 17.6355 | 5.0053 | 2.3013 | 6.5276 | 1.5061 | 4.6173 | 6.145 | 16.6324 | 11.5665 | 7.2607 | 8.41 | 9.3104 | 7.7717 | 6.7189 | 7.8637 | 10.1706 | 9.1239
TSO | - | 12 | 13 | 2020 | Summer | P, [MW] | 0 | 0 | 32.7931 | 63.5699 | 39.9223 | 50.3502 | 44.78 | 57.8584 | 22.4774 | 74.029 | 55.1667 | 51.4732 | 58.2924 | 22.4147 | 7.3964 | 23.1327 | 22.7801 | 53.0542 | 3.7107 | 1.7677 | 24.8105 | 17.7962 | 12.2081 | 20.6444 | 17.501 | 43.8354
TSO | - | 12 | 16 | 2020 | Summer | P, [MW] | 0 | 0 | 18.9075 | 26.7292 | 29.503 | 30.5608 | 31.1408 | 31.8532 | 5.0042 | 20.9122 | 6.5327 | 3.2606 | 4.5532 | 13.257 | 15.1131 | 16.1311 | 7.4634 | 14.1832 | 5.686 | 5.8927 | 31.192 | 18.4109 | 20.7743 | 16.7536 | 3.9288 | 8.3275
TSO | - | 12 | 17 | 2020 | Summer | P, [MW] | 0 | 0 | 40.8955 | 47.1078 | 49.5203 | 48.9946 | 48.8007 | 49.0183 | 25.5987 | 1.1447 | 21.532 | 28.4406 | 26.0322 | 14.8641 | 12.7171 | 15.7172 | 20.2885 | 16.8231 | 23.7177 | 23.348 | 5.5573 | 8.7324 | 3.2927 | 12.9207 | 27.8334 | 34.6395
TSO | - | 14 | 15 | 2020 | Summer | P, [MW] | 0 | 0 | 66.0989 | 67.3767 | 71.2452 | 64.6766 | 69.3511 | 61.9819 | 52.2378 | 45.9494 | 60.9043 | 68.3219 | 73.1691 | 51.8354 | 57.175 | 82.0792 | 68.8071 | 70.3318 | 81.433 | 80.7646 | 38.647 | 52.2903 | 50.6719 | 59.6525 | 73.043 | 64.8508
TSO | - | 18 | 19 | 2020 | Summer | P, [MW] | 0 | 0 | 5.4714 | 6.3824 | 6.8664 | 2.9689 | 3.9592 | 4.8056 | 3.3401 | 3.5114 | 2.1695 | 0.75111 | 0.43358 | 1.419 | 1.3817 | 2.9872 | 5.3756 | 5.0927 | 5.5089 | 5.4193 | 3.2554 | 3.6089 | 3.7891 | 3.8103 | 2.2531 | 2.7646
TSO | - | 19 | 20 | 2020 | Summer | P, [MW] | 0 | 0 | 1.0215 | 1.9303 | 1.3039 | 1.8533 | 1.7343 | 0.81796 | 1.2078 | 1.2882 | 2.1596 | 5.9272 | 7.0546 | 4.1318 | 4.1278 | 6.2481 | 3.1343 | 2.8523 | 5.4517 | 5.3642 | 2.1276 | 2.4791 | 2.6581 | 2.6788 | 5.5314 | 3.8451
TSO | - | 21 | 20 | 2020 | Summer | P, [MW] | 0 | 0 | 1.8984 | 0.79969 | 1.3191 | 0.73822 | 0.9306 | 3.3586 | 4.225 | 2.2678 | 1.5694 | 2.1932 | 3.0148 | 0.44406 | 1.096 | 2.1137 | 0.81803 | 1.0016 | 1.4565 | 1.5804 | 1.3688 | 1.1697 | 1.0249 | 1.1801 | 2.4453 | 1.0361
TSO | - | 21 | 22 | 2020 | Summer | P, [MW] | 0 | 0 | 1.8996 | 0.80082 | 1.3202 | 0.73895 | 0.9312 | 3.361 | 4.2284 | 2.2688 | 1.5703 | 2.1918 | 3.013 | 0.44544 | 1.0946 | 2.111 | 0.81915 | 1.0024 | 1.4556 | 1.5796 | 1.3694 | 1.17 | 1.0252 | 1.1805 | 2.4439 | 1.0355
TSO | - | 22 | 23 | 2020 | Summer | P, [MW] | 0 | 0 | 2.0192 | 2.7165 | 2.619 | 0.95133 | 0.91862 | 0.17508 | 2.073 | 5.9573 | 3.1027 | 3.1931 | 1.0221 | 2.684 | 5.7925 | 8.1102 | 10.9099 | 9.2498 | 7.9442 | 7.8404 | 5.2301 | 2.6326 | 5.322 | 8.5732 | 7.938 | 10.9047
TSO | - | 23 | 24 | 2020 | Summer | P, [MW] | 0 | 0 | 2.6274 | 6.1088 | 6.5568 | 5.2487 | 3.4623 | 4.4773 | 3.5527 | 3.9323 | 0.55838 | 2.0063 | 2.8888 | 0.42584 | 2.036 | 4.4194 | 1.0912 | 1.9522 | 2.5833 | 2.3444 | 0.37181 | 3.2956 | 4.1449 | 2.6554 | 3.3961 | 1.5436
TSO | - | 24 | 25 | 2020 | Summer | P, [MW] | 0 | 0 | 8.1261 | 18.0064 | 14.0232 | 8.882 | 8.6256 | 7.6285 | 6.2533 | 5.4162 | 5.5616 | 9.6033 | 4.8084 | 4.6498 | 3.9704 | 3.7412 | 6.2185 | 4.9297 | 5.6242 | 5.7389 | 7.8911 | 6.9185 | 6.4751 | 5.377 | 6.1903 | 4.9028
TSO | - | 24 | 26 | 2020 | Summer | P, [MW] | 0 | 0 | 5.5247 | 11.9616 | 7.5131 | 3.6682 | 5.1937 | 3.1852 | 2.7369 | 9.3717 | 6.1507 | 7.651 | 7.7279 | 5.1173 | 6.051 | 8.2169 | 7.3617 | 6.9336 | 8.2568 | 8.1341 | 7.5261 | 10.2317 | 10.6447 | 8.0495 | 9.6123 | 6.482
TSO | - | 26 | 27 | 2020 | Summer | P, [MW] | 0 | 0 | 5.5452 | 12.0251 | 7.5412 | 3.6854 | 5.2174 | 3.204 | 2.754 | 9.4111 | 6.1746 | 7.6809 | 7.7582 | 5.1365 | 6.077 | 8.2562 | 7.3899 | 6.9689 | 8.2977 | 8.176 | 7.5504 | 10.2765 | 10.6944 | 8.0774 | 9.6557 | 6.5122
TSO | - | 27 | 28 | 2020 | Summer | P, [MW] | 0 | 0 | 18.3119 | 24.7693 | 19.1549 | 15.9818 | 16.3004 | 15.4837 | 18.1615 | 27.7036 | 24.071 | 26.2755 | 25.1572 | 23.4678 | 24.1137 | 26.7437 | 25.4306 | 23.2258 | 24.878 | 24.5783 | 23.9889 | 27.4133 | 27.4038 | 24.768 | 24.8015 | 21.1767
TSO | - | 28 | 29 | 2020 | Summer | P, [MW] | 0 | 0 | 24.7708 | 30.5514 | 24.465 | 21.1619 | 21.589 | 20.3887 | 24.0625 | 34.927 | 32.0334 | 34.6108 | 34.099 | 32.7258 | 33.2503 | 36.1905 | 34.1958 | 32.0919 | 33.4736 | 33.3699 | 32.2748 | 35.7128 | 35.6884 | 33.5477 | 33.5646 | 28.739
TSO | - | 7 | 29 | 2020 | Summer | P, [MW] | 0 | 0 | 47.3092 | 42.2033 | 41.4026 | 34.1913 | 32.004 | 31.514 | 45.6679 | 78.5804 | 84.5523 | 90.1065 | 91.3458 | 95.1404 | 93.8338 | 100.723 | 94.8504 | 85.8669 | 87.0999 | 86.2213 | 82.717 | 86.145 | 88.5638 | 96.827 | 100.5728 | 76.2397
TSO | - | 25 | 30 | 2020 | Summer | P, [MW] | 0 | 0 | 6.9232 | 5.3585 | 7.6691 | 7.8736 | 7.618 | 6.4308 | 5.4515 | 5.0091 | 4.7614 | 2.1894 | 4.2048 | 3.0661 | 3.1707 | 2.7459 | 2.6751 | 3.9331 | 4.82 | 4.9344 | 5.5047 | 6.501 | 5.668 | 4.9674 | 5.3845 | 4.4952
TSO | - | 30 | 31 | 2020 | Summer | P, [MW] | 0 | 0 | 6.8617 | 5.3171 | 7.5935 | 7.7973 | 7.5468 | 6.3793 | 5.4124 | 4.9736 | 4.7288 | 2.1795 | 4.1754 | 3.0483 | 3.1476 | 2.7262 | 2.6595 | 3.9065 | 4.7813 | 4.8945 | 5.456 | 6.4383 | 5.6189 | 4.9291 | 5.3404 | 4.4635
TSO | - | 31 | 32 | 2020 | Summer | P, [MW] | 0 | 0 | 0.28929 | 4.0994 | 4.0943 | 2.3296 | 1.8135 | 0.95613 | 1.0557 | 3.3092 | 3.8822 | 3.1189 | 4.7358 | 5.0304 | 5.5936 | 5.8442 | 4.112 | 4.0609 | 3.5708 | 3.4457 | 2.0839 | 2.9923 | 3.2161 | 3.8048 | 3.2516 | 2.1576
TSO | - | 32 | 33 | 2020 | Summer | P, [MW] | 0 | 0 | 4.0204 | 3.3571 | 2.8586 | 2.7482 | 2.7481 | 3.2483 | 4.6075 | 5.0931 | 6.1034 | 6.3677 | 6.5318 | 7.0735 | 7.4096 | 7.2189 | 7.1178 | 6.8173 | 6.3942 | 6.3645 | 6.0123 | 6.247 | 6.2682 | 6.5492 | 6.1298 | 4.6641
TSO | - | 34 | 32 | 2020 | Summer | P, [MW] | 0 | 0 | 7.1394 | 10.2571 | 9.5169 | 7.6073 | 7.0595 | 6.8087 | 6.1845 | 4.6256 | 5.195 | 6.2073 | 4.6631 | 4.82 | 4.4019 | 3.9924 | 5.4224 | 5.2322 | 5.3705 | 5.5392 | 6.7968 | 6.4844 | 5.9322 | 5.7592 | 5.7789 | 4.8201
TSO | - | 34 | 35 | 2020 | Summer | P, [MW] | 0 | 0 | 7.1464 | 10.2714 | 9.5288 | 7.6148 | 7.066 | 6.8146 | 6.1897 | 4.6289 | 5.1995 | 6.2143 | 4.6675 | 4.825 | 4.4071 | 3.9972 | 5.4293 | 5.2378 | 5.3766 | 5.5454 | 6.804 | 6.4913 | 5.938 | 5.7648 | 5.7843 | 4.824
TSO | - | 35 | 36 | 2020 | Summer | P, [MW] | 0 | 0 | 15.147 | 17.9217 | 16.7948 | 15.1943 | 14.5707 | 14.3896 | 16.4293 | 16.0208 | 17.2629 | 17.5651 | 15.6812 | 16.6067 | 15.985 | 14.8132 | 15.9111 | 15.3637 | 15.5006 | 15.235 | 16.7322 | 16.9019 | 16.1875 | 16.632 | 15.9504 | 13.5998
TSO | - | 36 | 37 | 2020 | Summer | P, [MW] | 0 | 0 | 20.0812 | 21.4344 | 21.0034 | 19.3975 | 19.1886 | 19.7624 | 22.0315 | 21.6121 | 23.8557 | 23.4714 | 21.4812 | 22.5299 | 21.5407 | 20.0575 | 20.4021 | 19.836 | 20.1638 | 19.9737 | 21.6672 | 22.2433 | 20.9055 | 21.8605 | 20.3649 | 17.2051
TSO | - | 37 | 38 | 2020 | Summer | P, [MW] | 0 | 0 | 25.6245 | 25.7546 | 25.7072 | 24.0591 | 24.1463 | 25.5782 | 28.4005 | 27.9751 | 31.2267 | 30.351 | 28.2494 | 29.5709 | 28.3676 | 26.5502 | 26.2873 | 25.6903 | 25.9852 | 25.8748 | 27.77 | 28.7355 | 26.8895 | 28.31 | 26.0634 | 21.845
TSO | - | 37 | 39 | 2020 | Summer | P, [MW] | 0 | 0 | 5.4043 | 4.1762 | 4.5624 | 4.5403 | 4.8363 | 5.681 | 6.1997 | 6.1819 | 7.1438 | 6.6645 | 6.5791 | 6.8266 | 6.6181 | 6.3066 | 5.713 | 5.7005 | 5.666 | 5.7503 | 5.9297 | 6.3069 | 5.822 | 6.2671 | 5.549 | 4.5383
TSO | - | 36 | 40 | 2020 | Summer | P, [MW] | 0 | 0 | 4.8775 | 3.4429 | 4.1448 | 4.1504 | 4.5673 | 5.3209 | 5.5342 | 5.5178 | 6.5025 | 5.8165 | 5.7241 | 5.8346 | 5.4705 | 5.1683 | 4.417 | 4.4073 | 4.5966 | 4.6756 | 4.8623 | 5.2655 | 4.6506 | 5.1536 | 4.3512 | 3.5618
TSO | - | 22 | 38 | 2020 | Summer | P, [MW] | 0 | 0 | 3.9219 | 3.5223 | 3.9424 | 1.6915 | 1.8511 | 3.1892 | 6.3082 | 3.6837 | 1.524 | 1.0181 | 4.025 | 3.1434 | 4.7118 | 6.0152 | 11.7497 | 10.2681 | 6.5002 | 6.2717 | 6.6033 | 3.805 | 6.3512 | 9.7612 | 5.4996 | 9.879
TSO | - | 11 | 41 | 2020 | Summer | P, [MW] | 0 | 0 | 12.1039 | 11.9824 | 10.1542 | 10.0645 | 9.962 | 10.3857 | 13.5581 | 15.4681 | 16.0243 | 15.8367 | 15.3522 | 16.8599 | 16.8242 | 16.9265 | 16.3094 | 15.6951 | 15.3812 | 15.4399 | 15.5443 | 16.3027 | 16.5515 | 16.9242 | 15.3787 | 12.9461
TSO | - | 41 | 42 | 2020 | Summer | P, [MW] | 0 | 0 | 12.016 | 12.0114 | 9.6523 | 10.1217 | 9.8636 | 10.2126 | 13.3721 | 15.1646 | 15.8762 | 16.4826 | 15.4882 | 16.6938 | 16.5671 | 16.6251 | 15.3099 | 15.0131 | 14.5721 | 14.6303 | 14.7227 | 16.0643 | 15.9379 | 16.712 | 16.038 | 13.1918
TSO | - | 41 | 43 | 2020 | Summer | P, [MW] | 0 | 0 | 15.3013 | 15.1422 | 12.5405 | 13.151 | 12.8316 | 12.8464 | 17.2269 | 20.1301 | 21.2255 | 22.0477 | 21.4095 | 23.2204 | 23.1696 | 22.9503 | 21.2439 | 20.4266 | 20.3689 | 20.4467 | 20.4059 | 21.4112 | 21.7386 | 22.2321 | 20.9105 | 17.3257
TSO | - | 38 | 44 | 2020 | Summer | P, [MW] | 0 | 0 | 21.3913 | 24.5282 | 22.5204 | 18.1894 | 19.5029 | 17.8057 | 18.7401 | 14.847 | 18.7248 | 25.0076 | 22.4326 | 18.7944 | 28.0407 | 32.6191 | 32.4084 | 30.8278 | 30.5735 | 31.5109 | 21.4807 | 22.2996 | 24.4371 | 28.2058 | 30.9601 | 26.1282
TSO | - | 15 | 45 | 2020 | Summer | P, [MW] | 0 | 0 | 37.02 | 39.2436 | 36.606 | 31.994 | 33.7186 | 31.3913 | 34.9187 | 33.3799 | 38.2897 | 45.3563 | 44.3947 | 43.2918 | 44.7839 | 55.205 | 53.905 | 51.6808 | 52.3976 | 52.3277 | 40.0661 | 41.5556 | 43.8232 | 48.9291 | 47.8883 | 41.5457
TSO | - | 14 | 46 | 2020 | Summer | P, [MW] | 0 | 0 | 28.4352 | 29.2805 | 23.5119 | 18.1567 | 22.0759 | 18.123 | 27.9638 | 25.3305 | 27.4573 | 40.7796 | 37.3854 | 43.0922 | 53.2727 | 67.7065 | 68.0979 | 63.4143 | 61.1713 | 61.1748 | 45.6367 | 46.0647 | 55.0631 | 61.8127 | 58.5623 | 54.8459
TSO | - | 46 | 47 | 2020 | Summer | P, [MW] | 0 | 0 | 28.3852 | 29.2277 | 23.4721 | 18.1215 | 22.0327 | 18.0805 | 27.9096 | 25.2924 | 27.4088 | 40.6717 | 37.2933 | 42.9763 | 53.1029 | 67.443 | 67.8352 | 63.187 | 60.9585 | 60.9628 | 45.5157 | 45.9422 | 54.8889 | 61.5941 | 58.3658 | 54.6723
TSO | - | 47 | 48 | 2020 | Summer | P, [MW] | 0 | 0 | 31.2859 | 45.3813 | 42.1503 | 38.4746 | 34.0824 | 40.1029 | 34.9556 | 34.8434 | 39.4348 | 35.191 | 28.5356 | 28.3825 | 15.938 | 7.4744 | 10.4355 | 9.9624 | 11.0268 | 12.4486 | 22.6271 | 18.1298 | 10.7857 | 9.0523 | 5.526 | 2.861
TSO | - | 48 | 49 | 2020 | Summer | P, [MW] | 0 | 0 | 4.8048 | 15.8841 | 12.6622 | 8.9614 | 7.8927 | 9.9327 | 4.1487 | 7.0649 | 8.7261 | 9.1882 | 4.4325 | 1.0591 | 4.9036 | 8.4118 | 9.242 | 9.7453 | 7.0006 | 6.6412 | 2.0784 | 2.4388 | 6.375 | 8.5282 | 6.6206 | 5.4047
TSO | - | 49 | 50 | 2020 | Summer | P, [MW] | 0 | 0 | 22.5724 | 16.8796 | 21.4226 | 24.204 | 24.2341 | 26.3781 | 23.5855 | 29.3434 | 30.0316 | 24.4948 | 28.8884 | 25.268 | 22.583 | 21.151 | 16.4217 | 17.5972 | 20.3035 | 20.8205 | 21.6244 | 24.2915 | 22.1823 | 22.3225 | 21.5589 | 22.6843
TSO | - | 50 | 51 | 2020 | Summer | P, [MW] | 0 | 0 | 7.1872 | 10.74 | 5.5319 | 3.3457 | 3.1689 | 0.71794 | 5.915 | 8.7512 | 11.2335 | 15.3288 | 12.2564 | 17.0843 | 18.3537 | 20.5814 | 21.6071 | 21.4465 | 17.9468 | 18.287 | 17.1487 | 15.3604 | 17.5214 | 18.6392 | 15.8447 | 11.4819
TSO | - | 10 | 51 | 2020 | Summer | P, [MW] | 0 | 0 | 31.6722 | 35.0493 | 27.8855 | 26.8908 | 24.4893 | 24.4185 | 35.3086 | 43.7104 | 46.0434 | 51.6229 | 46.1286 | 52.8006 | 53.3642 | 56.3523 | 56.7581 | 52.8797 | 49.9141 | 49.9002 | 48.6961 | 48.0821 | 49.4717 | 50.7734 | 44.7794 | 39.4215
TSO | - | 13 | 49 | 2020 | Summer | P, [MW] | 0 | 0 | 24.9076 | 33.6026 | 25.6367 | 19.621 | 20.6049 | 20.8808 | 27.0999 | 25.9777 | 25.753 | 37.1789 | 29.6669 | 35.5301 | 39.1224 | 42.9418 | 47.9279 | 42.705 | 39.6693 | 39.8518 | 38.7933 | 35.3523 | 40.236 | 43.0947 | 38.667 | 33.967
TSO | - | 29 | 52 | 2020 | Summer | P, [MW] | 0 | 0 | 13.4948 | 7.9656 | 11.9963 | 8.882 | 9.3134 | 9.2682 | 12.0554 | 22.5059 | 26.0578 | 27.1844 | 28.8909 | 29.2972 | 28.6915 | 31.1839 | 28.9955 | 26.2061 | 26.7955 | 26.5112 | 24.8652 | 25.3543 | 26.0147 | 30.5095 | 32.3304 | 23.4743
TSO | - | 52 | 53 | 2020 | Summer | P, [MW] | 0 | 0 | 6.6321 | 1.9522 | 6.4061 | 3.4145 | 3.7607 | 4.1224 | 5.7994 | 14.7272 | 17.4206 | 18.1445 | 19.1357 | 19.1793 | 18.7365 | 20.8673 | 19.4193 | 16.6168 | 17.5073 | 17.0158 | 15.887 | 16.4028 | 17.0758 | 20.8447 | 22.6353 | 15.2752
TSO | - | 53 | 54 | 2020 | Summer | P, [MW] | 0 | 0 | 3.9457 | 2.2601 | 0.71984 | 1.4026 | 2.559 | 2.027 | 5.564 | 10.273 | 13.4807 | 14.977 | 13.8657 | 18.6817 | 17.7751 | 17.5062 | 17.5327 | 15.5654 | 13.9215 | 13.8231 | 14.1265 | 12.9759 | 14.3849 | 17.4264 | 17.5547 | 12.9075
TSO | - | 54 | 55 | 2020 | Summer | P, [MW] | 0 | 0 | 3.9672 | 2.2684 | 0.70989 | 1.4071 | 2.5486 | 2.0215 | 5.5962 | 10.4035 | 13.7225 | 15.288 | 14.1195 | 19.1525 | 18.1955 | 17.9095 | 17.9026 | 15.8518 | 14.1635 | 14.075 | 14.3272 | 13.1497 | 14.5924 | 17.7367 | 17.8784 | 13.0791
TSO | - | 11 | 43 | 2020 | Summer | P, [MW] | 0 | 0 | 17.9698 | 17.8074 | 15.8749 | 13.8178 | 14.1652 | 16.1806 | 19.8959 | 21.4624 | 21.2255 | 18.0472 | 17.4082 | 19.886 | 19.836 | 20.9502 | 22.5773 | 21.76 | 20.3689 | 20.4467 | 21.0726 | 22.0776 | 22.4051 | 22.8988 | 18.9099 | 16.659
TSO | - | 44 | 45 | 2020 | Summer | P, [MW] | 0 | 0 | 36.8139 | 39.0135 | 36.4076 | 31.8415 | 33.5497 | 31.2423 | 34.7352 | 33.1903 | 38.0528 | 45.0366 | 44.0793 | 43 | 44.475 | 54.7434 | 53.467 | 51.2765 | 51.9797 | 51.912 | 39.8055 | 41.2805 | 43.5222 | 48.5596 | 47.5385 | 41.286
TSO | - | 40 | 56 | 2020 | Summer | P, [MW] | 0 | 0 | 4.8756 | 3.4417 | 4.1433 | 4.1489 | 4.5656 | 5.3187 | 5.5318 | 5.5153 | 6.4991 | 5.8139 | 5.7215 | 5.8319 | 5.4681 | 5.1661 | 4.4154 | 4.4058 | 4.5949 | 4.6739 | 4.8605 | 5.2633 | 4.6489 | 5.1515 | 4.3497 | 3.5608
TSO | - | 56 | 41 | 2020 | Summer | P, [MW] | 0 | 0 | 7.2177 | 7.6138 | 5.7416 | 5.7719 | 5.4067 | 5.3438 | 7.1432 | 8.7993 | 9.3538 | 10.26 | 9.8714 | 10.4772 | 10.6004 | 10.7697 | 10.283 | 9.9035 | 9.6308 | 9.6273 | 9.5859 | 10.5443 | 10.2363 | 10.6048 | 10.3525 | 7.9925
TSO | - | 56 | 42 | 2020 | Summer | P, [MW] | 0 | 0 | 3.0476 | 3.8462 | 2.6554 | 2.4031 | 1.899 | 1.7146 | 1.6876 | 1.6323 | 1.6569 | 2.4287 | 2.8521 | 2.3729 | 2.641 | 2.9348 | 3.6412 | 3.7023 | 3.4643 | 3.5953 | 3.8699 | 4.1232 | 3.9017 | 3.8165 | 4.2768 | 3.1098
TSO | - | 39 | 57 | 2020 | Summer | P, [MW] | 0 | 0 | 5.4025 | 4.1751 | 4.5611 | 4.539 | 4.8348 | 5.6791 | 6.1974 | 6.1795 | 7.1405 | 6.6617 | 6.5763 | 6.8236 | 6.6151 | 6.3038 | 5.7107 | 5.6984 | 5.664 | 5.7482 | 5.9274 | 6.3043 | 5.8198 | 6.2646 | 5.5471 | 4.537
TSO | - | 57 | 56 | 2020 | Summer | P, [MW] | 0 | 0 | 1.7071 | 1.7626 | 0.49171 | 0.3077 | 0.0049912 | 0.033363 | 1.8668 | 2.6804 | 3.5638 | 4.5324 | 4.9474 | 5.6236 | 6.5876 | 6.5905 | 6.8952 | 6.3289 | 5.6383 | 5.5005 | 4.6771 | 4.6988 | 5.2021 | 5.2771 | 5.2253 | 3.6821
TSO | - | 38 | 49 | 2020 | Summer | P, [MW] | 0 | 0 | 3.6443 | 3.6472 | 1.2859 | 1.4182 | 1.3093 | 0.88855 | 5.2738 | 2.3523 | 1.9717 | 0.39254 | 3.3214 | 6.6606 | 9.2322 | 10.4142 | 12.0555 | 12.4206 | 9.9796 | 10.0005 | 8.1801 | 7.3342 | 9.2667 | 10.9399 | 8.0901 | 4.6028
TSO | - | 38 | 48 | 2020 | Summer | P, [MW] | 0 | 0 | 26.3734 | 29.2791 | 29.3065 | 29.3602 | 26.0687 | 30.008 | 30.6671 | 27.6458 | 30.5452 | 25.8697 | 24.0145 | 27.22 | 20.7754 | 15.8208 | 19.6063 | 19.6375 | 17.9519 | 19.0119 | 24.6259 | 20.5136 | 17.1124 | 17.5237 | 12.1144 | 2.5214
TSO | - | 9 | 55 | 2020 | Summer | P, [MW] | 0 | 0 | 12.2503 | 13.2261 | 12.9468 | 13.0807 | 8.3281 | 6.4986 | 10.6236 | 12.3676 | 14.7771 | 14.3023 | 13.5198 | 16.9985 | 15.4641 | 14.3785 | 16.3306 | 15.7411 | 15.6327 | 15.8261 | 18.3368 | 17.224 | 17.4404 | 19.1353 | 20.4094 | 15.7921
TSO | - | 1 | 2 | 2020 | Summer | P, [MW] | Expected | - | 64.8218 | 44.2433 | 74.9292 | 83.4301 | 73.113 | 85.2738 | 60.8658 | 122.33 | 91.4701 | 97.2487 | 109.0723 | 37.6244 | 33.1464 | 69.0375 | 56.8499 | 53.752 | 81.8558 | 66.3919 | 13.4489 | 77.1495 | 73.3743 | 62.4534 | 31.8666 | 46.917
TSO | - | 2 | 3 | 2020 | Summer | P, [MW] | Expected | - | 91.3487 | 84.3095 | 96.3852 | 98.4274 | 95.8615 | 99.1693 | 88.3009 | 13.7152 | 36.4833 | 45.3413 | 29.5268 | 63.2835 | 65.1004 | 51.9182 | 79.2668 | 82.8893 | 59.9775 | 58.6032 | 68.4966 | 65.1142 | 66.6804 | 84.5499 | 63.7538 | 70.7099
TSO | - | 3 | 4 | 2020 | Summer | P, [MW] | Expected | - | 37.7861 | 34.7146 | 34.9732 | 35.724 | 36.9852 | 39.9248 | 46.6308 | 29.5983 | 34.6396 | 31.5883 | 26.6972 | 27.5147 | 26.4178 | 26.3133 | 31.3839 | 31.6176 | 33.6438 | 32.5684 | 25.5821 | 26.3648 | 26.5453 | 32.1096 | 26.4479 | 28.5851
TSO | - | 4 | 5 | 2020 | Summer | P, [MW] | Expected | - | 1.3326 | 0.29021 | 2.1861 | 2.8821 | 2.1429 | 2.0964 | 0.88721 | 6.7198 | 4.1499 | 3.8996 | 3.7792 | 5.7951 | 5.6125 | 5.6801 | 2.0574 | 1.9492 | 0.79376 | 1.0177 | 3.8135 | 5.8207 | 5.7488 | 3.5629 | 2.4703 | 0.63916
TSO | - | 4 | 6 | 2020 | Summer | P, [MW] | Expected | - | 3.4856 | 3.1703 | 0.94066 | 0.25006 | 0.24209 | 0.24177 | 4.3387 | 17.8987 | 16.4997 | 16.7471 | 16.6275 | 20.5096 | 19.8755 | 20.4465 | 15.5668 | 14.0895 | 12.3211 | 12.3944 | 15.748 | 18.1661 | 18.7404 | 17.8219 | 17.1236 | 11.2324
TSO | - | 6 | 7 | 2020 | Summer | P, [MW] | Expected | - | 20.0055 | 12.6603 | 25.993 | 20.452 | 20.4459 | 18.4088 | 16.6498 | 8.5192 | 26.7354 | 44.0404 | 39.3249 | 22.7312 | 24.7146 | 55.4561 | 31.683 | 28.5439 | 46.1593 | 45.9191 | 14.5603 | 7.5263 | 7.262 | 20.3858 | 21.7929 | 17.1481
TSO | - | 6 | 8 | 2020 | Summer | P, [MW] | Expected | - | 0.13512 | 5.0669 | 8.6005 | 6.0703 | 6.9813 | 5.1403 | 2.539 | 24.2804 | 8.541 | 6.5408 | 1.2445 | 16.7871 | 14.2944 | 13.7321 | 7.9313 | 7.34 | 9.7899 | 9.9335 | 19.96 | 28.421 | 29.683 | 19.9985 | 20.2407 | 14.8377
TSO | - | 8 | 9 | 2020 | Summer | P, [MW] | Expected | - | 86.1674 | 66.28 | 111.2336 | 52.0932 | 103.9593 | 105.7009 | 65.0799 | 174.6444 | 171.1682 | 163.7908 | 180.5237 | 173.4362 | 172.8204 | 167.7256 | 158.5997 | 143.9942 | 150.6675 | 148.4257 | 122.5321 | 163.1689 | 157.4874 | 148.955 | 165.6386 | 114.2022
TSO | - | 9 | 10 | 2020 | Summer | P, [MW] | Expected | - | 24.7397 | 41.4735 | 17.1311 | 25.8702 | 16.5261 | 15.1462 | 22.0701 | 55.1973 | 48.4764 | 45.2885 | 49.0081 | 41.1423 | 36.6723 | 33.524 | 25.7102 | 21.299 | 33.6132 | 32.9669 | 22.0704 | 40.9057 | 39.344 | 26.1109 | 40.4166 | 40.0054
TSO | - | 9 | 11 | 2020 | Summer | P, [MW] | Expected | - | 21.499 | 37.7281 | 6.0946 | 17.7334 | 5.5599 | 0.356 | 19.6644 | 54.7797 | 42.4099 | 31.6901 | 39.4138 | 35.3561 | 32.1569 | 31.8353 | 22.3408 | 25.983 | 28.5992 | 27.5817 | 27.3608 | 46.2937 | 45.8137 | 32.0302 | 44.5951 | 38.8411
TSO | - | 9 | 12 | 2020 | Summer | P, [MW] | Expected | - | 9.195 | 23.9036 | 3.359 | 12.1693 | 4.5774 | 3.8225 | 5.4285 | 33.5389 | 26.0091 | 21.128 | 25.7141 | 16.7617 | 12.1972 | 5.5104 | 0.41577 | 4.2168 | 9.5223 | 8.5565 | 1.2029 | 17.131 | 15.7506 | 1.3144 | 17.2054 | 20.6764
TSO | - | 9 | 13 | 2020 | Summer | P, [MW] | Expected | - | 7.566 | 23.8448 | 5.9404 | 6.6654 | 5.5853 | 11.904 | 4.196 | 37.5937 | 25.2296 | 16.0831 | 24.2822 | 18.4279 | 15.2854 | 14.3897 | 4.4255 | 8.7283 | 12.1391 | 11.058 | 10.3495 | 28.4272 | 27.6949 | 13.5219 | 28.6266 | 25.0711
TSO | - | 13 | 14 | 2020 | Summer | P, [MW] | Expected | - | 21.1917 | 22.2895 | 31.9169 | 29.0174 | 31.4674 | 28.7935 | 9.2477 | 5.3169 | 17.5417 | 12.5739 | 16.718 | 6.1915 | 14.8947 | 5.5632 | 18.8447 | 13.3425 | 0.69775 | 1.7153 | 21.9807 | 7.0581 | 17.6749 | 16.1787 | 0.30117 | 8.6881
TSO | - | 13 | 15 | 2020 | Summer | P, [MW] | Expected | - | 51.9568 | 53.2984 | 60.5532 | 54.9763 | 59.128 | 53.1809 | 37.2815 | 31.4257 | 47.1081 | 49.4064 | 54.4139 | 29.6738 | 28.7176 | 49.1215 | 34.002 | 37.6702 | 51.7862 | 50.1648 | 13.0966 | 29.1738 | 22.821 | 29.1669 | 45.5259 | 44.8819
TSO | - | 1 | 15 | 2020 | Summer | P, [MW] | Expected | - | 133.6565 | 126.1558 | 142.9069 | 139.8056 | 140.2146 | 138.9093 | 120.7611 | 21.3159 | 74.3004 | 85.6992 | 76.0854 | 94.8788 | 100.1 | 105.5652 | 134.2417 | 135.1853 | 104.6333 | 106.6643 | 88.0768 | 83.4166 | 83.4389 | 129.8033 | 119.5768 | 118.4949
TSO | - | 1 | 16 | 2020 | Summer | P, [MW] | Expected | - | 77.3247 | 80.4134 | 82.1773 | 81.0688 | 81.1156 | 81.4988 | 68.4154 | 51.6063 | 73.2771 | 78.0688 | 76.5112 | 69.6826 | 68.0465 | 71.0162 | 72.0186 | 67.7247 | 74.5933 | 74.4506 | 45.2869 | 58.1351 | 54.9929 | 65.122 | 74.1038 | 75.723
TSO | - | 1 | 17 | 2020 | Summer | P, [MW] | Expected | - | 94.8635 | 96.376 | 97.9448 | 97.5475 | 98.4595 | 99.378 | 92.6835 | 81.7507 | 99.4862 | 99.7132 | 99.8792 | 98.4916 | 97.3376 | 97.4382 | 98.3266 | 90.9934 | 98.9571 | 99.0193 | 72.6631 | 83.2306 | 84.6337 | 90.7677 | 92.7939 | 94.0216
TSO | - | 3 | 15 | 2020 | Summer | P, [MW] | Expected | - | 47.1714 | 57.3596 | 47.9833 | 33.7207 | 43.956 | 29.4401 | 34.2302 | 130.5504 | 114.7929 | 119.9771 | 137.7973 | 72.6177 | 75.5003 | 125.2386 | 63.9176 | 62.5809 | 119.2497 | 115.3011 | 45.9608 | 78.9872 | 75.3379 | 52.3458 | 86.0367 | 63.6115
TSO | - | 4 | 18 | 2020 | Summer | P, [MW] | Expected | - | 39.864 | 37.5255 | 33.6592 | 32.5197 | 34.5244 | 37.9851 | 49.9805 | 54.1352 | 55.1952 | 52.1445 | 47.0253 | 53.7303 | 51.8183 | 52.3517 | 48.9173 | 47.5712 | 46.6752 | 45.9014 | 45.0757 | 50.2766 | 50.9566 | 53.4121 | 45.9676 | 40.3903
TSO | - | 5 | 6 | 2020 | Summer | P, [MW] | Expected | - | 5.4711 | 2.4499 | 1.5191 | 0.24234 | 1.3411 | 0.70952 | 6.2952 | 22.8586 | 24.2229 | 25.2884 | 25.1704 | 30.8968 | 29.7121 | 30.7023 | 25.9617 | 22.7549 | 20.9798 | 20.8105 | 23.088 | 24.7726 | 26.0707 | 28.2634 | 28.5275 | 18.7211
TSO | - | 7 | 8 | 2020 | Summer | P, [MW] | Expected | - | 27.4647 | 29.6935 | 15.5686 | 13.8908 | 11.7071 | 13.2577 | 29.1795 | 70.2693 | 58.0187 | 46.2803 | 52.2443 | 72.6369 | 69.3398 | 45.513 | 63.4131 | 57.5419 | 41.1714 | 40.5275 | 68.3658 | 78.8624 | 81.5602 | 76.6984 | 79.0678 | 59.3193
TSO | - | 10 | 12 | 2020 | Summer | P, [MW] | Expected | - | 10.6779 | 1.9072 | 14.3572 | 5.1762 | 10.7553 | 10.7262 | 16.036 | 5.8178 | 4.4842 | 12.0835 | 5.6314 | 16.8586 | 21.6202 | 33.1012 | 36.1942 | 39.1123 | 23.6018 | 25.0374 | 31.2188 | 13.2805 | 14.4843 | 30.6108 | 12.4622 | 3.7775
TSO | - | 11 | 13 | 2020 | Summer | P, [MW] | Expected | - | 8.6198 | 7.8345 | 19.9691 | 6.1853 | 18.6016 | 26.2619 | 13.8387 | 17.6355 | 5.0053 | 2.3013 | 6.5276 | 1.5061 | 4.6173 | 6.145 | 16.6324 | 11.5665 | 7.2607 | 8.41 | 9.3104 | 7.7717 | 6.7189 | 7.8637 | 10.1706 | 9.1239
TSO | - | 12 | 13 | 2020 | Summer | P, [MW] | Expected | - | 32.7931 | 63.5699 | 39.9223 | 50.3502 | 44.78 | 57.8584 | 22.4774 | 74.029 | 55.1667 | 51.4732 | 58.2924 | 22.4147 | 7.3964 | 23.1327 | 22.7801 | 53.0542 | 3.7107 | 1.7677 | 24.8105 | 17.7962 | 12.2081 | 20.6444 | 17.501 | 43.8354
TSO | - | 12 | 16 | 2020 | Summer | P, [MW] | Expected | - | 18.9075 | 26.7292 | 29.503 | 30.5608 | 31.1408 | 31.8532 | 5.0042 | 20.9122 | 6.5327 | 3.2606 | 4.5532 | 13.257 | 15.1131 | 16.1311 | 7.4634 | 14.1832 | 5.686 | 5.8927 | 31.192 | 18.4109 | 20.7743 | 16.7536 | 3.9288 | 8.3275
TSO | - | 12 | 17 | 2020 | Summer | P, [MW] | Expected | - | 40.8955 | 47.1078 | 49.5203 | 48.9946 | 48.8007 | 49.0183 | 25.5987 | 1.1447 | 21.532 | 28.4406 | 26.0322 | 14.8641 | 12.7171 | 15.7172 | 20.2885 | 16.8231 | 23.7177 | 23.348 | 5.5573 | 8.7324 | 3.2927 | 12.9207 | 27.8334 | 34.6395
TSO | - | 14 | 15 | 2020 | Summer | P, [MW] | Expected | - | 66.0989 | 67.3767 | 71.2452 | 64.6766 | 69.3511 | 61.9819 | 52.2378 | 45.9494 | 60.9043 | 68.3219 | 73.1691 | 51.8354 | 57.175 | 82.0792 | 68.8071 | 70.3318 | 81.433 | 80.7646 | 38.647 | 52.2903 | 50.6719 | 59.6525 | 73.043 | 64.8508
TSO | - | 18 | 19 | 2020 | Summer | P, [MW] | Expected | - | 5.4714 | 6.3824 | 6.8664 | 2.9689 | 3.9592 | 4.8056 | 3.3401 | 3.5114 | 2.1695 | 0.75111 | 0.43358 | 1.419 | 1.3817 | 2.9872 | 5.3756 | 5.0927 | 5.5089 | 5.4193 | 3.2554 | 3.6089 | 3.7891 | 3.8103 | 2.2531 | 2.7646
TSO | - | 19 | 20 | 2020 | Summer | P, [MW] | Expected | - | 1.0215 | 1.9303 | 1.3039 | 1.8533 | 1.7343 | 0.81796 | 1.2078 | 1.2882 | 2.1596 | 5.9272 | 7.0546 | 4.1318 | 4.1278 | 6.2481 | 3.1343 | 2.8523 | 5.4517 | 5.3642 | 2.1276 | 2.4791 | 2.6581 | 2.6788 | 5.5314 | 3.8451
TSO | - | 21 | 20 | 2020 | Summer | P, [MW] | Expected | - | 1.8984 | 0.79969 | 1.3191 | 0.73822 | 0.9306 | 3.3586 | 4.225 | 2.2678 | 1.5694 | 2.1932 | 3.0148 | 0.44406 | 1.096 | 2.1137 | 0.81803 | 1.0016 | 1.4565 | 1.5804 | 1.3688 | 1.1697 | 1.0249 | 1.1801 | 2.4453 | 1.0361
TSO | - | 21 | 22 | 2020 | Summer | P, [MW] | Expected | - | 1.8996 | 0.80082 | 1.3202 | 0.73895 | 0.9312 | 3.361 | 4.2284 | 2.2688 | 1.5703 | 2.1918 | 3.013 | 0.44544 | 1.0946 | 2.111 | 0.81915 | 1.0024 | 1.4556 | 1.5796 | 1.3694 | 1.17 | 1.0252 | 1.1805 | 2.4439 | 1.0355
TSO | - | 22 | 23 | 2020 | Summer | P, [MW] | Expected | - | 2.0192 | 2.7165 | 2.619 | 0.95133 | 0.91862 | 0.17508 | 2.073 | 5.9573 | 3.1027 | 3.1931 | 1.0221 | 2.684 | 5.7925 | 8.1102 | 10.9099 | 9.2498 | 7.9442 | 7.8404 | 5.2301 | 2.6326 | 5.322 | 8.5732 | 7.938 | 10.9047
TSO | - | 23 | 24 | 2020 | Summer | P, [MW] | Expected | - | 2.6274 | 6.1088 | 6.5568 | 5.2487 | 3.4623 | 4.4773 | 3.5527 | 3.9323 | 0.55838 | 2.0063 | 2.8888 | 0.42584 | 2.036 | 4.4194 | 1.0912 | 1.9522 | 2.5833 | 2.3444 | 0.37181 | 3.2956 | 4.1449 | 2.6554 | 3.3961 | 1.5436
TSO | - | 24 | 25 | 2020 | Summer | P, [MW] | Expected | - | 8.1261 | 18.0064 | 14.0232 | 8.882 | 8.6256 | 7.6285 | 6.2533 | 5.4162 | 5.5616 | 9.6033 | 4.8084 | 4.6498 | 3.9704 | 3.7412 | 6.2185 | 4.9297 | 5.6242 | 5.7389 | 7.8911 | 6.9185 | 6.4751 | 5.377 | 6.1903 | 4.9028
TSO | - | 24 | 26 | 2020 | Summer | P, [MW] | Expected | - | 5.5247 | 11.9616 | 7.5131 | 3.6682 | 5.1937 | 3.1852 | 2.7369 | 9.3717 | 6.1507 | 7.651 | 7.7279 | 5.1173 | 6.051 | 8.2169 | 7.3617 | 6.9336 | 8.2568 | 8.1341 | 7.5261 | 10.2317 | 10.6447 | 8.0495 | 9.6123 | 6.482
TSO | - | 26 | 27 | 2020 | Summer | P, [MW] | Expected | - | 5.5452 | 12.0251 | 7.5412 | 3.6854 | 5.2174 | 3.204 | 2.754 | 9.4111 | 6.1746 | 7.6809 | 7.7582 | 5.1365 | 6.077 | 8.2562 | 7.3899 | 6.9689 | 8.2977 | 8.176 | 7.5504 | 10.2765 | 10.6944 | 8.0774 | 9.6557 | 6.5122
TSO | - | 27 | 28 | 2020 | Summer | P, [MW] | Expected | - | 18.3119 | 24.7693 | 19.1549 | 15.9818 | 16.3004 | 15.4837 | 18.1615 | 27.7036 | 24.071 | 26.2755 | 25.1572 | 23.4678 | 24.1137 | 26.7437 | 25.4306 | 23.2258 | 24.878 | 24.5783 | 23.9889 | 27.4133 | 27.4038 | 24.768 | 24.8015 | 21.1767
TSO | - | 28 | 29 | 2020 | Summer | P, [MW] | Expected | - | 24.7708 | 30.5514 | 24.465 | 21.1619 | 21.589 | 20.3887 | 24.0625 | 34.927 | 32.0334 | 34.6108 | 34.099 | 32.7258 | 33.2503 | 36.1905 | 34.1958 | 32.0919 | 33.4736 | 33.3699 | 32.2748 | 35.7128 | 35.6884 | 33.5477 | 33.5646 | 28.739
TSO | - | 7 | 29 | 2020 | Summer | P, [MW] | Expected | - | 47.3092 | 42.2033 | 41.4026 | 34.1913 | 32.004 | 31.514 | 45.6679 | 78.5804 | 84.5523 | 90.1065 | 91.3458 | 95.1404 | 93.8338 | 100.723 | 94.8504 | 85.8669 | 87.0999 | 86.2213 | 82.717 | 86.145 | 88.5638 | 96.827 | 100.5728 | 76.2397
TSO | - | 25 | 30 | 2020 | Summer | P, [MW] | Expected | - | 6.9232 | 5.3585 | 7.6691 | 7.8736 | 7.618 | 6.4308 | 5.4515 | 5.0091 | 4.7614 | 2.1894 | 4.2048 | 3.0661 | 3.1707 | 2.7459 | 2.6751 | 3.9331 | 4.82 | 4.9344 | 5.5047 | 6.501 | 5.668 | 4.9674 | 5.3845 | 4.4952
TSO | - | 30 | 31 | 2020 | Summer | P, [MW] | Expected | - | 6.8617 | 5.3171 | 7.5935 | 7.7973 | 7.5468 | 6.3793 | 5.4124 | 4.9736 | 4.7288 | 2.1795 | 4.1754 | 3.0483 | 3.1476 | 2.7262 | 2.6595 | 3.9065 | 4.7813 | 4.8945 | 5.456 | 6.4383 | 5.6189 | 4.9291 | 5.3404 | 4.4635
TSO | - | 31 | 32 | 2020 | Summer | P, [MW] | Expected | - | 0.28929 | 4.0994 | 4.0943 | 2.3296 | 1.8135 | 0.95613 | 1.0557 | 3.3092 | 3.8822 | 3.1189 | 4.7358 | 5.0304 | 5.5936 | 5.8442 | 4.112 | 4.0609 | 3.5708 | 3.4457 | 2.0839 | 2.9923 | 3.2161 | 3.8048 | 3.2516 | 2.1576
TSO | - | 32 | 33 | 2020 | Summer | P, [MW] | Expected | - | 4.0204 | 3.3571 | 2.8586 | 2.7482 | 2.7481 | 3.2483 | 4.6075 | 5.0931 | 6.1034 | 6.3677 | 6.5318 | 7.0735 | 7.4096 | 7.2189 | 7.1178 | 6.8173 | 6.3942 | 6.3645 | 6.0123 | 6.247 | 6.2682 | 6.5492 | 6.1298 | 4.6641
TSO | - | 34 | 32 | 2020 | Summer | P, [MW] | Expected | - | 7.1394 | 10.2571 | 9.5169 | 7.6073 | 7.0595 | 6.8087 | 6.1845 | 4.6256 | 5.195 | 6.2073 | 4.6631 | 4.82 | 4.4019 | 3.9924 | 5.4224 | 5.2322 | 5.3705 | 5.5392 | 6.7968 | 6.4844 | 5.9322 | 5.7592 | 5.7789 | 4.8201
TSO | - | 34 | 35 | 2020 | Summer | P, [MW] | Expected | - | 7.1464 | 10.2714 | 9.5288 | 7.6148 | 7.066 | 6.8146 | 6.1897 | 4.6289 | 5.1995 | 6.2143 | 4.6675 | 4.825 | 4.4071 | 3.9972 | 5.4293 | 5.2378 | 5.3766 | 5.5454 | 6.804 | 6.4913 | 5.938 | 5.7648 | 5.7843 | 4.824
TSO | - | 35 | 36 | 2020 | Summer | P, [MW] | Expected | - | 15.147 | 17.9217 | 16.7948 | 15.1943 | 14.5707 | 14.3896 | 16.4293 | 16.0208 | 17.2629 | 17.5651 | 15.6812 | 16.6067 | 15.985 | 14.8132 | 15.9111 | 15.3637 | 15.5006 | 15.235 | 16.7322 | 16.9019 | 16.1875 | 16.632 | 15.9504 | 13.5998
TSO | - | 36 | 37 | 2020 | Summer | P, [MW] | Expected | - | 20.0812 | 21.4344 | 21.0034 | 19.3975 | 19.1886 | 19.7624 | 22.0315 | 21.6121 | 23.8557 | 23.4714 | 21.4812 | 22.5299 | 21.5407 | 20.0575 | 20.4021 | 19.836 | 20.1638 | 19.9737 | 21.6672 | 22.2433 | 20.9055 | 21.8605 | 20.3649 | 17.2051
TSO | - | 37 | 38 | 2020 | Summer | P, [MW] | Expected | - | 25.6245 | 25.7546 | 25.7072 | 24.0591 | 24.1463 | 25.5782 | 28.4005 | 27.9751 | 31.2267 | 30.351 | 28.2494 | 29.5709 | 28.3676 | 26.5502 | 26.2873 | 25.6903 | 25.9852 | 25.8748 | 27.77 | 28.7355 | 26.8895 | 28.31 | 26.0634 | 21.845
TSO | - | 37 | 39 | 2020 | Summer | P, [MW] | Expected | - | 5.4043 | 4.1762 | 4.5624 | 4.5403 | 4.8363 | 5.681 | 6.1997 | 6.1819 | 7.1438 | 6.6645 | 6.5791 | 6.8266 | 6.6181 | 6.3066 | 5.713 | 5.7005 | 5.666 | 5.7503 | 5.9297 | 6.3069 | 5.822 | 6.2671 | 5.549 | 4.5383
TSO | - | 36 | 40 | 2020 | Summer | P, [MW] | Expected | - | 4.8775 | 3.4429 | 4.1448 | 4.1504 | 4.5673 | 5.3209 | 5.5342 | 5.5178 | 6.5025 | 5.8165 | 5.7241 | 5.8346 | 5.4705 | 5.1683 | 4.417 | 4.4073 | 4.5966 | 4.6756 | 4.8623 | 5.2655 | 4.6506 | 5.1536 | 4.3512 | 3.5618
TSO | - | 22 | 38 | 2020 | Summer | P, [MW] | Expected | - | 3.9219 | 3.5223 | 3.9424 | 1.6915 | 1.8511 | 3.1892 | 6.3082 | 3.6837 | 1.524 | 1.0181 | 4.025 | 3.1434 | 4.7118 | 6.0152 | 11.7497 | 10.2681 | 6.5002 | 6.2717 | 6.6033 | 3.805 | 6.3512 | 9.7612 | 5.4996 | 9.879
TSO | - | 11 | 41 | 2020 | Summer | P, [MW] | Expected | - | 12.1039 | 11.9824 | 10.1542 | 10.0645 | 9.962 | 10.3857 | 13.5581 | 15.4681 | 16.0243 | 15.8367 | 15.3522 | 16.8599 | 16.8242 | 16.9265 | 16.3094 | 15.6951 | 15.3812 | 15.4399 | 15.5443 | 16.3027 | 16.5515 | 16.9242 | 15.3787 | 12.9461
TSO | - | 41 | 42 | 2020 | Summer | P, [MW] | Expected | - | 12.016 | 12.0114 | 9.6523 | 10.1217 | 9.8636 | 10.2126 | 13.3721 | 15.1646 | 15.8762 | 16.4826 | 15.4882 | 16.6938 | 16.5671 | 16.6251 | 15.3099 | 15.0131 | 14.5721 | 14.6303 | 14.7227 | 16.0643 | 15.9379 | 16.712 | 16.038 | 13.1918
TSO | - | 41 | 43 | 2020 | Summer | P, [MW] | Expected | - | 15.3013 | 15.1422 | 12.5405 | 13.151 | 12.8316 | 12.8464 | 17.2269 | 20.1301 | 21.2255 | 22.0477 | 21.4095 | 23.2204 | 23.1696 | 22.9503 | 21.2439 | 20.4266 | 20.3689 | 20.4467 | 20.4059 | 21.4112 | 21.7386 | 22.2321 | 20.9105 | 17.3257
TSO | - | 38 | 44 | 2020 | Summer | P, [MW] | Expected | - | 21.3913 | 24.5282 | 22.5204 | 18.1894 | 19.5029 | 17.8057 | 18.7401 | 14.847 | 18.7248 | 25.0076 | 22.4326 | 18.7944 | 28.0407 | 32.6191 | 32.4084 | 30.8278 | 30.5735 | 31.5109 | 21.4807 | 22.2996 | 24.4371 | 28.2058 | 30.9601 | 26.1282
TSO | - | 15 | 45 | 2020 | Summer | P, [MW] | Expected | - | 37.02 | 39.2436 | 36.606 | 31.994 | 33.7186 | 31.3913 | 34.9187 | 33.3799 | 38.2897 | 45.3563 | 44.3947 | 43.2918 | 44.7839 | 55.205 | 53.905 | 51.6808 | 52.3976 | 52.3277 | 40.0661 | 41.5556 | 43.8232 | 48.9291 | 47.8883 | 41.5457
TSO | - | 14 | 46 | 2020 | Summer | P, [MW] | Expected | - | 28.4352 | 29.2805 | 23.5119 | 18.1567 | 22.0759 | 18.123 | 27.9638 | 25.3305 | 27.4573 | 40.7796 | 37.3854 | 43.0922 | 53.2727 | 67.7065 | 68.0979 | 63.4143 | 61.1713 | 61.1748 | 45.6367 | 46.0647 | 55.0631 | 61.8127 | 58.5623 | 54.8459
TSO | - | 46 | 47 | 2020 | Summer | P, [MW] | Expected | - | 28.3852 | 29.2277 | 23.4721 | 18.1215 | 22.0327 | 18.0805 | 27.9096 | 25.2924 | 27.4088 | 40.6717 | 37.2933 | 42.9763 | 53.1029 | 67.443 | 67.8352 | 63.187 | 60.9585 | 60.9628 | 45.5157 | 45.9422 | 54.8889 | 61.5941 | 58.3658 | 54.6723
TSO | - | 47 | 48 | 2020 | Summer | P, [MW] | Expected | - | 31.2859 | 45.3813 | 42.1503 | 38.4746 | 34.0824 | 40.1029 | 34.9556 | 34.8434 | 39.4348 | 35.191 | 28.5356 | 28.3825 | 15.938 | 7.4744 | 10.4355 | 9.9624 | 11.0268 | 12.4486 | 22.6271 | 18.1298 | 10.7857 | 9.0523 | 5.526 | 2.861
TSO | - | 48 | 49 | 2020 | Summer | P, [MW] | Expected | - | 4.8048 | 15.8841 | 12.6622 | 8.9614 | 7.8927 | 9.9327 | 4.1487 | 7.0649 | 8.7261 | 9.1882 | 4.4325 | 1.0591 | 4.9036 | 8.4118 | 9.242 | 9.7453 | 7.0006 | 6.6412 | 2.0784 | 2.4388 | 6.375 | 8.5282 | 6.6206 | 5.4047
TSO | - | 49 | 50 | 2020 | Summer | P, [MW] | Expected | - | 22.5724 | 16.8796 | 21.4226 | 24.204 | 24.2341 | 26.3781 | 23.5855 | 29.3434 | 30.0316 | 24.4948 | 28.8884 | 25.268 | 22.583 | 21.151 | 16.4217 | 17.5972 | 20.3035 | 20.8205 | 21.6244 | 24.2915 | 22.1823 | 22.3225 | 21.5589 | 22.6843
TSO | - | 50 | 51 | 2020 | Summer | P, [MW] | Expected | - | 7.1872 | 10.74 | 5.5319 | 3.3457 | 3.1689 | 0.71794 | 5.915 | 8.7512 | 11.2335 | 15.3288 | 12.2564 | 17.0843 | 18.3537 | 20.5814 | 21.6071 | 21.4465 | 17.9468 | 18.287 | 17.1487 | 15.3604 | 17.5214 | 18.6392 | 15.8447 | 11.4819
TSO | - | 10 | 51 | 2020 | Summer | P, [MW] | Expected | - | 31.6722 | 35.0493 | 27.8855 | 26.8908 | 24.4893 | 24.4185 | 35.3086 | 43.7104 | 46.0434 | 51.6229 | 46.1286 | 52.8006 | 53.3642 | 56.3523 | 56.7581 | 52.8797 | 49.9141 | 49.9002 | 48.6961 | 48.0821 | 49.4717 | 50.7734 | 44.7794 | 39.4215
TSO | - | 13 | 49 | 2020 | Summer | P, [MW] | Expected | - | 24.9076 | 33.6026 | 25.6367 | 19.621 | 20.6049 | 20.8808 | 27.0999 | 25.9777 | 25.753 | 37.1789 | 29.6669 | 35.5301 | 39.1224 | 42.9418 | 47.9279 | 42.705 | 39.6693 | 39.8518 | 38.7933 | 35.3523 | 40.236 | 43.0947 | 38.667 | 33.967
TSO | - | 29 | 52 | 2020 | Summer | P, [MW] | Expected | - | 13.4948 | 7.9656 | 11.9963 | 8.882 | 9.3134 | 9.2682 | 12.0554 | 22.5059 | 26.0578 | 27.1844 | 28.8909 | 29.2972 | 28.6915 | 31.1839 | 28.9955 | 26.2061 | 26.7955 | 26.5112 | 24.8652 | 25.3543 | 26.0147 | 30.5095 | 32.3304 | 23.4743
TSO | - | 52 | 53 | 2020 | Summer | P, [MW] | Expected | - | 6.6321 | 1.9522 | 6.4061 | 3.4145 | 3.7607 | 4.1224 | 5.7994 | 14.7272 | 17.4206 | 18.1445 | 19.1357 | 19.1793 | 18.7365 | 20.8673 | 19.4193 | 16.6168 | 17.5073 | 17.0158 | 15.887 | 16.4028 | 17.0758 | 20.8447 | 22.6353 | 15.2752
TSO | - | 53 | 54 | 2020 | Summer | P, [MW] | Expected | - | 3.9457 | 2.2601 | 0.71984 | 1.4026 | 2.559 | 2.027 | 5.564 | 10.273 | 13.4807 | 14.977 | 13.8657 | 18.6817 | 17.7751 | 17.5062 | 17.5327 | 15.5654 | 13.9215 | 13.8231 | 14.1265 | 12.9759 | 14.3849 | 17.4264 | 17.5547 | 12.9075
TSO | - | 54 | 55 | 2020 | Summer | P, [MW] | Expected | - | 3.9672 | 2.2684 | 0.70989 | 1.4071 | 2.5486 | 2.0215 | 5.5962 | 10.4035 | 13.7225 | 15.288 | 14.1195 | 19.1525 | 18.1955 | 17.9095 | 17.9026 | 15.8518 | 14.1635 | 14.075 | 14.3272 | 13.1497 | 14.5924 | 17.7367 | 17.8784 | 13.0791
TSO | - | 11 | 43 | 2020 | Summer | P, [MW] | Expected | - | 17.9698 | 17.8074 | 15.8749 | 13.8178 | 14.1652 | 16.1806 | 19.8959 | 21.4624 | 21.2255 | 18.0472 | 17.4082 | 19.886 | 19.836 | 20.9502 | 22.5773 | 21.76 | 20.3689 | 20.4467 | 21.0726 | 22.0776 | 22.4051 | 22.8988 | 18.9099 | 16.659
TSO | - | 44 | 45 | 2020 | Summer | P, [MW] | Expected | - | 36.8139 | 39.0135 | 36.4076 | 31.8415 | 33.5497 | 31.2423 | 34.7352 | 33.1903 | 38.0528 | 45.0366 | 44.0793 | 43 | 44.475 | 54.7434 | 53.467 | 51.2765 | 51.9797 | 51.912 | 39.8055 | 41.2805 | 43.5222 | 48.5596 | 47.5385 | 41.286
TSO | - | 40 | 56 | 2020 | Summer | P, [MW] | Expected | - | 4.8756 | 3.4417 | 4.1433 | 4.1489 | 4.5656 | 5.3187 | 5.5318 | 5.5153 | 6.4991 | 5.8139 | 5.7215 | 5.8319 | 5.4681 | 5.1661 | 4.4154 | 4.4058 | 4.5949 | 4.6739 | 4.8605 | 5.2633 | 4.6489 | 5.1515 | 4.3497 | 3.5608
TSO | - | 56 | 41 | 2020 | Summer | P, [MW] | Expected | - | 7.2177 | 7.6138 | 5.7416 | 5.7719 | 5.4067 | 5.3438 | 7.1432 | 8.7993 | 9.3538 | 10.26 | 9.8714 | 10.4772 | 10.6004 | 10.7697 | 10.283 | 9.9035 | 9.6308 | 9.6273 | 9.5859 | 10.5443 | 10.2363 | 10.6048 | 10.3525 | 7.9925
TSO | - | 56 | 42 | 2020 | Summer | P, [MW] | Expected | - | 3.0476 | 3.8462 | 2.6554 | 2.4031 | 1.899 | 1.7146 | 1.6876 | 1.6323 | 1.6569 | 2.4287 | 2.8521 | 2.3729 | 2.641 | 2.9348 | 3.6412 | 3.7023 | 3.4643 | 3.5953 | 3.8699 | 4.1232 | 3.9017 | 3.8165 | 4.2768 | 3.1098
TSO | - | 39 | 57 | 2020 | Summer | P, [MW] | Expected | - | 5.4025 | 4.1751 | 4.5611 | 4.539 | 4.8348 | 5.6791 | 6.1974 | 6.1795 | 7.1405 | 6.6617 | 6.5763 | 6.8236 | 6.6151 | 6.3038 | 5.7107 | 5.6984 | 5.664 | 5.7482 | 5.9274 | 6.3043 | 5.8198 | 6.2646 | 5.5471 | 4.537
TSO | - | 57 | 56 | 2020 | Summer | P, [MW] | Expected | - | 1.7071 | 1.7626 | 0.49171 | 0.3077 | 0.0049912 | 0.033363 | 1.8668 | 2.6804 | 3.5638 | 4.5324 | 4.9474 | 5.6236 | 6.5876 | 6.5905 | 6.8952 | 6.3289 | 5.6383 | 5.5005 | 4.6771 | 4.6988 | 5.2021 | 5.2771 | 5.2253 | 3.6821
TSO | - | 38 | 49 | 2020 | Summer | P, [MW] | Expected | - | 3.6443 | 3.6472 | 1.2859 | 1.4182 | 1.3093 | 0.88855 | 5.2738 | 2.3523 | 1.9717 | 0.39254 | 3.3214 | 6.6606 | 9.2322 | 10.4142 | 12.0555 | 12.4206 | 9.9796 | 10.0005 | 8.1801 | 7.3342 | 9.2667 | 10.9399 | 8.0901 | 4.6028
TSO | - | 38 | 48 | 2020 | Summer | P, [MW] | Expected | - | 26.3734 | 29.2791 | 29.3065 | 29.3602 | 26.0687 | 30.008 | 30.6671 | 27.6458 | 30.5452 | 25.8697 | 24.0145 | 27.22 | 20.7754 | 15.8208 | 19.6063 | 19.6375 | 17.9519 | 19.0119 | 24.6259 | 20.5136 | 17.1124 | 17.5237 | 12.1144 | 2.5214
TSO | - | 9 | 55 | 2020 | Summer | P, [MW] | Expected | - | 12.2503 | 13.2261 | 12.9468 | 13.0807 | 8.3281 | 6.4986 | 10.6236 | 12.3676 | 14.7771 | 14.3023 | 13.5198 | 16.9985 | 15.4641 | 14.3785 | 16.3306 | 15.7411 | 15.6327 | 15.8261 | 18.3368 | 17.224 | 17.4404 | 19.1353 | 20.4094 | 15.7921
DSO | 2 | 1 | 2 | 2020 | Summer | P, [MW] | 0 | 0 | 8.5166 | 7.5665 | 6.9231 | 6.9627 | 7.0175 | 7.1046 | 9.4795 | 11.7085 | 11.524 | 8.0329 | 4.7272 | 4.3316 | 4.5487 | 3.908 | 6.2297 | 7.4218 | 9.2428 | 11.2285 | 10.9716 | 11.5422 | 12.7476 | 12.9311 | 11.343 | 9.2086
DSO | 2 | 2 | 3 | 2020 | Summer | P, [MW] | 0 | 0 | 8.06 | 7.229 | 6.7315 | 6.7261 | 6.8323 | 6.8864 | 9.1611 | 11.2938 | 11.5366 | 8.2524 | 4.901 | 4.2805 | 4.5772 | 3.9541 | 6.2469 | 7.5323 | 9.5376 | 11.6226 | 11.3455 | 12.0627 | 12.9859 | 12.6839 | 10.8047 | 8.8168
DSO | 2 | 3 | 4 | 2020 | Summer | P, [MW] | 0 | 0 | 7.3619 | 6.5741 | 6.2019 | 6.1208 | 6.2161 | 6.2827 | 8.4724 | 10.5407 | 10.7656 | 7.5313 | 4.2048 | 3.5094 | 3.8305 | 3.2012 | 5.498 | 6.7653 | 8.7736 | 10.9393 | 10.5114 | 11.2079 | 12.2011 | 11.8623 | 10.0305 | 8.141
DSO | 2 | 4 | 5 | 2020 | Summer | P, [MW] | 0 | 0 | 5.7823 | 5.1472 | 4.8593 | 4.7817 | 4.8777 | 4.9425 | 6.7809 | 8.3209 | 8.2915 | 5.6263 | 2.9687 | 2.5062 | 2.7456 | 2.2694 | 3.921 | 5.0268 | 6.6257 | 8.2244 | 7.772 | 8.4632 | 9.4518 | 9.1279 | 7.6514 | 6.1445
DSO | 2 | 5 | 6 | 2020 | Summer | P, [MW] | 0 | 0 | 2.4505 | 2.2069 | 2.1692 | 2.1564 | 2.183 | 2.1759 | 2.3214 | 2.9669 | 2.5667 | 0.043172 | 1.582 | 2.8347 | 2.5497 | 2.9398 | 1.3454 | 0.085009 | 1.4262 | 3.0115 | 3.069 | 3.3595 | 3.9317 | 4.0656 | 3.5499 | 2.7083
DSO | 2 | 6 | 7 | 2020 | Summer | P, [MW] | 0 | 0 | 1.7715 | 1.5773 | 1.5107 | 1.5274 | 1.5152 | 1.547 | 1.7 | 1.9415 | 1.589 | 0.054286 | 1.0559 | 1.8343 | 1.6012 | 1.8742 | 0.86137 | 0.16032 | 0.84146 | 1.8905 | 1.9785 | 2.1065 | 2.3916 | 2.4464 | 2.2242 | 1.8621
DSO | 2 | 7 | 8 | 2020 | Summer | P, [MW] | 0 | 0 | 1.5456 | 1.3895 | 1.3235 | 1.3401 | 1.328 | 1.3595 | 1.4661 | 1.5739 | 1.1798 | 0.45603 | 1.4295 | 2.2107 | 1.9777 | 2.2546 | 1.2192 | 0.45493 | 0.54499 | 1.5893 | 1.6771 | 1.734 | 1.9795 | 2.0342 | 1.8822 | 1.5594
DSO | 2 | 2 | 9 | 2020 | Summer | P, [MW] | 0 | 0 | 0.09236 | 0.0019357 | 0.082545 | 0.07538 | 0.13243 | 0.093374 | 0.043053 | 0.0089757 | 0.43179 | 0.60522 | 0.53876 | 0.35384 | 0.42283 | 0.44217 | 0.41064 | 0.51524 | 0.70251 | 0.76712 | 0.82054 | 0.98021 | 0.66911 | 0.20165 | 0.12278 | 0.03465
DSO | 2 | 1 | 20 | 2020 | Summer | P, [MW] | 0 | 0 | 5.6886 | 5.6379 | 4.8255 | 5.1537 | 4.9282 | 4.9883 | 5.6021 | 6.4348 | 4.9559 | 1.7782 | 5.7128 | 7.8668 | 6.523 | 7.7144 | 4.4937 | 1.5914 | 2.6866 | 6.6922 | 6.8819 | 7.224 | 7.6152 | 7.4302 | 6.7745 | 6.2596
DSO | 2 | 20 | 21 | 2020 | Summer | P, [MW] | 0 | 0 | 4.1668 | 4.2662 | 3.5134 | 3.824 | 3.6124 | 3.6482 | 4.2173 | 4.9384 | 3.2595 | 3.5868 | 7.7591 | 10.0373 | 8.686 | 9.6886 | 6.2307 | 3.2375 | 1.0529 | 5.0443 | 5.2109 | 5.4949 | 5.6305 | 5.3879 | 4.9143 | 4.7231
DSO | 2 | 21 | 22 | 2020 | Summer | P, [MW] | 0 | 0 | 0.228 | 0.2039 | 0.19065 | 0.19039 | 0.19453 | 0.19864 | 0.24199 | 0.30087 | 0.25334 | 1.874 | 2.8875 | 3.543 | 3.2437 | 3.4604 | 2.4385 | 1.7087 | 0.77522 | 0.25547 | 0.31583 | 0.31444 | 0.31186 | 0.31363 | 0.29558 | 0.25343
DSO | 2 | 21 | 23 | 2020 | Summer | P, [MW] | 0 | 0 | 3.5276 | 3.6976 | 2.9828 | 3.3129 | 3.0991 | 3.125 | 3.575 | 4.1358 | 2.9592 | 2.2731 | 5.5007 | 7.234 | 6.1521 | 6.9593 | 4.4041 | 2.0748 | 1.2893 | 4.2173 | 4.3067 | 4.56 | 4.6796 | 4.4336 | 4.0381 | 3.9691
DSO | 2 | 23 | 24 | 2020 | Summer | P, [MW] | 0 | 0 | 0.7989 | 0.7916 | 0.76465 | 0.7492 | 0.74493 | 0.75659 | 0.75024 | 0.90457 | 0.42024 | 1.3501 | 2.379 | 3.0446 | 2.7043 | 2.9555 | 1.9962 | 1.2193 | 0.18941 | 0.82968 | 0.86014 | 0.84862 | 0.84703 | 0.83983 | 0.77795 | 0.75348
DSO | 2 | 23 | 25 | 2020 | Summer | P, [MW] | 0 | 0 | 1.6419 | 1.547 | 1.4859 | 1.3767 | 1.3311 | 1.3916 | 1.5352 | 1.973 | 1.0684 | 2.3877 | 4.4951 | 5.7118 | 5.0386 | 5.5728 | 3.8976 | 2.3817 | 0.18127 | 1.8506 | 2.0738 | 2.1878 | 2.2891 | 2.1321 | 1.8435 | 1.6784
DSO | 2 | 25 | 26 | 2020 | Summer | P, [MW] | 0 | 0 | 0.22825 | 0.21446 | 0.19579 | 0.20543 | 0.20155 | 0.20593 | 0.29445 | 0.37209 | 0.80362 | 4.2494 | 6.3858 | 7.7963 | 7.16 | 7.6539 | 5.5148 | 3.9718 | 1.9733 | 0.16679 | 0.31161 | 0.3393 | 0.35487 | 0.33167 | 0.29196 | 0.2433
DSO | 2 | 50 | 1 | 2020 | Summer | P, [MW] | 0 | 0 | 15.4626 | 14.53 | 13.1592 | 13.4684 | 13.3423 | 13.5889 | 16.4943 | 19.2217 | 17.3978 | 7.0373 | 0.33663 | 3.0214 | 1.4174 | 3.2989 | 2.4986 | 6.7126 | 12.9217 | 18.8839 | 18.8338 | 19.5362 | 20.9591 | 21.0371 | 19.0909 | 16.6243
DSO | 2 | 50 | 51 | 2020 | Summer | P, [MW] | 0 | 0 | 15.4942 | 14.6095 | 13.3112 | 13.5954 | 13.4804 | 13.7256 | 16.4812 | 19.1435 | 17.3715 | 7.3651 | 0.42995 | 2.1798 | 0.67183 | 2.4297 | 3.1158 | 7.1001 | 13.0344 | 18.8233 | 18.7724 | 19.4975 | 20.934 | 20.9988 | 19.036 | 16.6123
DSO | 2 | 1 | 2 | 2020 | Summer | P, [MW] | Expected | - | 8.5166 | 7.5665 | 6.9231 | 6.9627 | 7.0175 | 7.1046 | 9.4795 | 11.7085 | 11.524 | 8.0329 | 4.7272 | 4.3316 | 4.5487 | 3.908 | 6.2297 | 7.4218 | 9.2428 | 11.2285 | 10.9716 | 11.5422 | 12.7476 | 12.9311 | 11.343 | 9.2086
DSO | 2 | 2 | 3 | 2020 | Summer | P, [MW] | Expected | - | 8.06 | 7.229 | 6.7315 | 6.7261 | 6.8323 | 6.8864 | 9.1611 | 11.2938 | 11.5366 | 8.2524 | 4.901 | 4.2805 | 4.5772 | 3.9541 | 6.2469 | 7.5323 | 9.5376 | 11.6226 | 11.3455 | 12.0627 | 12.9859 | 12.6839 | 10.8047 | 8.8168
DSO | 2 | 3 | 4 | 2020 | Summer | P, [MW] | Expected | - | 7.3619 | 6.5741 | 6.2019 | 6.1208 | 6.2161 | 6.2827 | 8.4724 | 10.5407 | 10.7656 | 7.5313 | 4.2048 | 3.5094 | 3.8305 | 3.2012 | 5.498 | 6.7653 | 8.7736 | 10.9393 | 10.5114 | 11.2079 | 12.2011 | 11.8623 | 10.0305 | 8.141
DSO | 2 | 4 | 5 | 2020 | Summer | P, [MW] | Expected | - | 5.7823 | 5.1472 | 4.8593 | 4.7817 | 4.8777 | 4.9425 | 6.7809 | 8.3209 | 8.2915 | 5.6263 | 2.9687 | 2.5062 | 2.7456 | 2.2694 | 3.921 | 5.0268 | 6.6257 | 8.2244 | 7.772 | 8.4632 | 9.4518 | 9.1279 | 7.6514 | 6.1445
DSO | 2 | 5 | 6 | 2020 | Summer | P, [MW] | Expected | - | 2.4505 | 2.2069 | 2.1692 | 2.1564 | 2.183 | 2.1759 | 2.3214 | 2.9669 | 2.5667 | 0.043172 | 1.582 | 2.8347 | 2.5497 | 2.9398 | 1.3454 | 0.085009 | 1.4262 | 3.0115 | 3.069 | 3.3595 | 3.9317 | 4.0656 | 3.5499 | 2.7083
DSO | 2 | 6 | 7 | 2020 | Summer | P, [MW] | Expected | - | 1.7715 | 1.5773 | 1.5107 | 1.5274 | 1.5152 | 1.547 | 1.7 | 1.9415 | 1.589 | 0.054286 | 1.0559 | 1.8343 | 1.6012 | 1.8742 | 0.86137 | 0.16032 | 0.84146 | 1.8905 | 1.9785 | 2.1065 | 2.3916 | 2.4464 | 2.2242 | 1.8621
DSO | 2 | 7 | 8 | 2020 | Summer | P, [MW] | Expected | - | 1.5456 | 1.3895 | 1.3235 | 1.3401 | 1.328 | 1.3595 | 1.4661 | 1.5739 | 1.1798 | 0.45603 | 1.4295 | 2.2107 | 1.9777 | 2.2546 | 1.2192 | 0.45493 | 0.54499 | 1.5893 | 1.6771 | 1.734 | 1.9795 | 2.0342 | 1.8822 | 1.5594
DSO | 2 | 2 | 9 | 2020 | Summer | P, [MW] | Expected | - | 0.09236 | 0.0019357 | 0.082545 | 0.07538 | 0.13243 | 0.093374 | 0.043053 | 0.0089757 | 0.43179 | 0.60522 | 0.53876 | 0.35384 | 0.42283 | 0.44217 | 0.41064 | 0.51524 | 0.70251 | 0.76712 | 0.82054 | 0.98021 | 0.66911 | 0.20165 | 0.12278 | 0.03465
DSO | 2 | 1 | 20 | 2020 | Summer | P, [MW] | Expected | - | 5.6886 | 5.6379 | 4.8255 | 5.1537 | 4.9282 | 4.9883 | 5.6021 | 6.4348 | 4.9559 | 1.7782 | 5.7128 | 7.8668 | 6.523 | 7.7144 | 4.4937 | 1.5914 | 2.6866 | 6.6922 | 6.8819 | 7.224 | 7.6152 | 7.4302 | 6.7745 | 6.2596
DSO | 2 | 20 | 21 | 2020 | Summer | P, [MW] | Expected | - | 4.1668 | 4.2662 | 3.5134 | 3.824 | 3.6124 | 3.6482 | 4.2173 | 4.9384 | 3.2595 | 3.5868 | 7.7591 | 10.0373 | 8.686 | 9.6886 | 6.2307 | 3.2375 | 1.0529 | 5.0443 | 5.2109 | 5.4949 | 5.6305 | 5.3879 | 4.9143 | 4.7231
DSO | 2 | 21 | 22 | 2020 | Summer | P, [MW] | Expected | - | 0.228 | 0.2039 | 0.19065 | 0.19039 | 0.19453 | 0.19864 | 0.24199 | 0.30087 | 0.25334 | 1.874 | 2.8875 | 3.543 | 3.2437 | 3.4604 | 2.4385 | 1.7087 | 0.77522 | 0.25547 | 0.31583 | 0.31444 | 0.31186 | 0.31363 | 0.29558 | 0.25343
DSO | 2 | 21 | 23 | 2020 | Summer | P, [MW] | Expected | - | 3.5276 | 3.6976 | 2.9828 | 3.3129 | 3.0991 | 3.125 | 3.575 | 4.1358 | 2.9592 | 2.2731 | 5.5007 | 7.234 | 6.1521 | 6.9593 | 4.4041 | 2.0748 | 1.2893 | 4.2173 | 4.3067 | 4.56 | 4.6796 | 4.4336 | 4.0381 | 3.9691
DSO | 2 | 23 | 24 | 2020 | Summer | P, [MW] | Expected | - | 0.7989 | 0.7916 | 0.76465 | 0.7492 | 0.74493 | 0.75659 | 0.75024 | 0.90457 | 0.42024 | 1.3501 | 2.379 | 3.0446 | 2.7043 | 2.9555 | 1.9962 | 1.2193 | 0.18941 | 0.82968 | 0.86014 | 0.84862 | 0.84703 | 0.83983 | 0.77795 | 0.75348
DSO | 2 | 23 | 25 | 2020 | Summer | P, [MW] | Expected | - | 1.6419 | 1.547 | 1.4859 | 1.3767 | 1.3311 | 1.3916 | 1.5352 | 1.973 | 1.0684 | 2.3877 | 4.4951 | 5.7118 | 5.0386 | 5.5728 | 3.8976 | 2.3817 | 0.18127 | 1.8506 | 2.0738 | 2.1878 | 2.2891 | 2.1321 | 1.8435 | 1.6784
DSO | 2 | 25 | 26 | 2020 | Summer | P, [MW] | Expected | - | 0.22825 | 0.21446 | 0.19579 | 0.20543 | 0.20155 | 0.20593 | 0.29445 | 0.37209 | 0.80362 | 4.2494 | 6.3858 | 7.7963 | 7.16 | 7.6539 | 5.5148 | 3.9718 | 1.9733 | 0.16679 | 0.31161 | 0.3393 | 0.35487 | 0.33167 | 0.29196 | 0.2433
DSO | 2 | 50 | 1 | 2020 | Summer | P, [MW] | Expected | - | 15.4626 | 14.53 | 13.1592 | 13.4684 | 13.3423 | 13.5889 | 16.4943 | 19.2217 | 17.3978 | 7.0373 | 0.33663 | 3.0214 | 1.4174 | 3.2989 | 2.4986 | 6.7126 | 12.9217 | 18.8839 | 18.8338 | 19.5362 | 20.9591 | 21.0371 | 19.0909 | 16.6243
DSO | 2 | 50 | 51 | 2020 | Summer | P, [MW] | Expected | - | 15.4942 | 14.6095 | 13.3112 | 13.5954 | 13.4804 | 13.7256 | 16.4812 | 19.1435 | 17.3715 | 7.3651 | 0.42995 | 2.1798 | 0.67183 | 2.4297 | 3.1158 | 7.1001 | 13.0344 | 18.8233 | 18.7724 | 19.4975 | 20.934 | 20.9988 | 19.036 | 16.6123

## Transformer Ratio
Operator | Connection Node ID | From Node ID | To Node ID | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
DSO | 2 | 50 | 1 | 2020 | Summer | Ratio | 0 | 0 | 0.95862 | 0.95484 | 0.94875 | 0.95158 | 0.94958 | 0.94652 | 0.95493 | 0.96964 | 0.9724 | 0.96285 | 0.95169 | 0.95453 | 0.9559 | 0.95396 | 0.95351 | 0.95665 | 0.9637 | 0.97289 | 0.97233 | 0.97984 | 0.98619 | 0.98386 | 0.97304 | 0.96388
DSO | 2 | 50 | 1 | 2020 | Summer | Ratio | Expected | - | 0.95862 | 0.95484 | 0.94875 | 0.95158 | 0.94958 | 0.94652 | 0.95493 | 0.96964 | 0.9724 | 0.96285 | 0.95169 | 0.95453 | 0.9559 | 0.95396 | 0.95351 | 0.95665 | 0.9637 | 0.97289 | 0.97233 | 0.97984 | 0.98619 | 0.98386 | 0.97304 | 0.96388

## Current
Operator | Connection Node ID | From Node ID | To Node ID | Year | Day | Quantity | Market Scenario | Operation Scenario | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
TSO | - | 1 | 2 | 2020 | Summer | I, [%] | 0 | 0 | 45.45% | 60% | 69.37% | 64.46% | 61.96% | 76.83% | 45.81% | 67.42% | 80.22% | 59.09% | 76.7% | 71.69% | 67.58% | 68.71% | 27.47% | 33.42% | 49.47% | 61.04% | 42.14% | 40.61% | 40.69% | 32.34% | 22.82% | 23.75%
TSO | - | 2 | 3 | 2020 | Summer | I, [%] | 0 | 0 | 88.21% | 81.53% | 92.15% | 94.3% | 91.77% | 94.72% | 88.51% | 33.96% | 35.75% | 44% | 30.7% | 62.61% | 65.05% | 52.68% | 77.36% | 80.82% | 58.27% | 58.93% | 72.64% | 63.22% | 64.72% | 81.88% | 61.99% | 68.43%
TSO | - | 3 | 4 | 2020 | Summer | I, [%] | 0 | 0 | 37.81% | 34.25% | 34.11% | 35.19% | 36.65% | 39.62% | 48.26% | 34.69% | 41.29% | 39.84% | 34% | 34.55% | 34.97% | 34.14% | 40.15% | 38.62% | 39.03% | 37.35% | 29.9% | 30.16% | 30.11% | 34.59% | 29.35% | 30.34%
TSO | - | 4 | 5 | 2020 | Summer | I, [%] | 0 | 0 | 95.82% | 95.66% | 96.95% | 97.29% | 97.18% | 97.48% | 95.43% | 89.12% | 87.27% | 85.84% | 86.86% | 81.91% | 81.6% | 82.68% | 89.57% | 89.25% | 90.94% | 90.51% | 83.61% | 87.07% | 87.54% | 82.82% | 88.8% | 94.25%
TSO | - | 4 | 6 | 2020 | Summer | I, [%] | 0 | 0 | 13.85% | 14.3% | 14.08% | 14.53% | 14.78% | 15.64% | 14.43% | 18.18% | 17.88% | 17.93% | 17.9% | 20.51% | 19.95% | 20.44% | 17.56% | 16.96% | 16.09% | 15.92% | 17.26% | 18.71% | 19.42% | 18.8% | 18.75% | 15.77%
TSO | - | 6 | 7 | 2020 | Summer | I, [%] | 0 | 0 | 41.79% | 38.29% | 44.18% | 40.63% | 40.2% | 37.23% | 39.03% | 26.65% | 38.46% | 51.94% | 49.55% | 30.11% | 33% | 59.09% | 44.47% | 41.62% | 55.34% | 55.05% | 30.38% | 25.25% | 24.01% | 33.26% | 36.91% | 39.43%
TSO | - | 6 | 8 | 2020 | Summer | I, [%] | 0 | 0 | 92.15% | 91.96% | 95.71% | 96.75% | 96.83% | 97.31% | 93.14% | 76.34% | 61.52% | 56.32% | 59.1% | 49.93% | 49.33% | 48.82% | 65.06% | 68.58% | 73.41% | 71.81% | 70.19% | 82.16% | 84.97% | 67.89% | 76.06% | 89.17%
TSO | - | 8 | 9 | 2020 | Summer | I, [%] | 0 | 0 | 48.02% | 39.08% | 59.78% | 37.26% | 57.74% | 62.6% | 43.83% | 87.11% | 92.81% | 92.25% | 93.16% | 94.04% | 93.3% | 90.04% | 86.91% | 84.97% | 89.98% | 89.63% | 61.23% | 80.97% | 78.28% | 74.41% | 82.58% | 58.93%
TSO | - | 9 | 10 | 2020 | Summer | I, [%] | 0 | 0 | 25.74% | 42.43% | 18.08% | 26.42% | 17.08% | 15.73% | 23.18% | 58.72% | 49.42% | 48.72% | 49.32% | 44.21% | 41.63% | 38.45% | 34.82% | 28.98% | 41.14% | 40.34% | 27.91% | 44.12% | 41.75% | 30.11% | 43.16% | 41.21%
TSO | - | 9 | 11 | 2020 | Summer | I, [%] | 0 | 0 | 25.17% | 39.41% | 13.42% | 23.05% | 15.29% | 14.52% | 24.01% | 55.08% | 45.07% | 35.3% | 41.2% | 37.48% | 35.03% | 34.04% | 26.95% | 31.7% | 34.81% | 33.73% | 27.57% | 46.25% | 45.85% | 32.16% | 44.91% | 40.73%
TSO | - | 9 | 12 | 2020 | Summer | I, [%] | 0 | 0 | 33.09% | 51.74% | 31.42% | 36.48% | 30.38% | 30.29% | 28.46% | 64.95% | 48.58% | 51.49% | 45.11% | 47.94% | 47.36% | 41.81% | 33.22% | 30.93% | 43.29% | 43.11% | 35.46% | 44.8% | 41.26% | 35.8% | 44.03% | 46.38%
TSO | - | 9 | 13 | 2020 | Summer | I, [%] | 0 | 0 | 10.33% | 24.43% | 7.568% | 10.08% | 9.078% | 13.66% | 10.3% | 37.84% | 30.65% | 24.71% | 27.93% | 25.15% | 24.58% | 22.35% | 18.66% | 20.99% | 24.54% | 23.68% | 10.79% | 28.47% | 27.73% | 13.83% | 28.79% | 26.3%
TSO | - | 13 | 14 | 2020 | Summer | I, [%] | 0 | 0 | 48.9% | 50.51% | 53.6% | 54.11% | 54.72% | 53.14% | 50.73% | 36.88% | 17.5% | 18.73% | 16.89% | 18.82% | 23.3% | 19.86% | 19.87% | 13.4% | 16.18% | 16.51% | 43.24% | 34.37% | 38.39% | 40.69% | 38.11% | 46.89%
TSO | - | 13 | 15 | 2020 | Summer | I, [%] | 0 | 0 | 65.07% | 66.33% | 69.88% | 64.79% | 68.22% | 61.35% | 54.42% | 51.12% | 46.73% | 49.19% | 54.45% | 32.67% | 31.41% | 50.33% | 33.3% | 36.98% | 51.19% | 49.78% | 45.44% | 48.47% | 44.31% | 49.87% | 60.07% | 60.79%
TSO | - | 1 | 15 | 2020 | Summer | I, [%] | 0 | 0 | 65.63% | 61.47% | 69.2% | 67.66% | 67.85% | 67.18% | 60.01% | 30.58% | 40.11% | 41.97% | 39.45% | 46.79% | 49.01% | 51.48% | 64.92% | 66.09% | 50.96% | 52.01% | 46.02% | 43.88% | 45.12% | 64.37% | 59.94% | 59.02%
TSO | - | 1 | 16 | 2020 | Summer | I, [%] | 0 | 0 | 42.9% | 43.88% | 43.82% | 43.27% | 43.23% | 42.73% | 39.47% | 35.16% | 35.86% | 38.14% | 37.61% | 34.3% | 33.7% | 35.13% | 35.22% | 32.81% | 36.48% | 36.43% | 30.89% | 35.23% | 34.12% | 37.77% | 41.91% | 42.9%
TSO | - | 1 | 17 | 2020 | Summer | I, [%] | 0 | 0 | 96.89% | 97.81% | 97.89% | 97.46% | 98.18% | 98.3% | 96.78% | 90.97% | 96.45% | 97.46% | 96.8% | 96.72% | 95.54% | 95.86% | 96.01% | 88.27% | 96.72% | 96.59% | 81.12% | 87.77% | 89.91% | 94.8% | 95.9% | 97.37%
TSO | - | 3 | 15 | 2020 | Summer | I, [%] | 0 | 0 | 26.85% | 32.48% | 28.69% | 21.63% | 25.84% | 18.8% | 18.18% | 64.24% | 58.36% | 60.73% | 67.4% | 43.72% | 43.26% | 64.37% | 31.28% | 32.97% | 59.81% | 58.48% | 30.19% | 41.4% | 38.27% | 31.92% | 44.43% | 32.86%
TSO | - | 4 | 18 | 2020 | Summer | I, [%] | 0 | 0 | 19.51% | 18.43% | 16.74% | 16.08% | 16.93% | 18.54% | 24.55% | 28.08% | 28.71% | 27.46% | 24.4% | 28.79% | 28.14% | 27.98% | 25.59% | 24.54% | 23.53% | 23.06% | 22.65% | 25.34% | 25.66% | 26.49% | 22.66% | 19.72%
TSO | - | 5 | 6 | 2020 | Summer | I, [%] | 0 | 0 | 11.71% | 11.58% | 11.08% | 11.9% | 12.15% | 14.02% | 13.04% | 22.76% | 24.59% | 25.38% | 25.25% | 30.61% | 29.43% | 30.27% | 26.13% | 23.78% | 22.23% | 21.87% | 23.53% | 24.78% | 26.28% | 28.21% | 28.6% | 20.3%
TSO | - | 7 | 8 | 2020 | Summer | I, [%] | 0 | 0 | 46.04% | 47.14% | 42.02% | 44.52% | 44.28% | 48.95% | 49.49% | 70.48% | 60.64% | 47.79% | 53.81% | 72.43% | 69.15% | 45.36% | 65% | 61.7% | 47.28% | 46.06% | 68.48% | 78.09% | 81.29% | 76.21% | 79.53% | 65.71%
TSO | - | 10 | 12 | 2020 | Summer | I, [%] | 0 | 0 | 34.78% | 34.93% | 38.9% | 36.17% | 37.56% | 37.54% | 34.05% | 20.73% | 18.99% | 29.8% | 13.49% | 35.16% | 38.43% | 44.18% | 37.86% | 41.33% | 33.2% | 35.02% | 41.92% | 29.9% | 30.44% | 43.74% | 30.42% | 32.41%
TSO | - | 11 | 13 | 2020 | Summer | I, [%] | 0 | 0 | 21.66% | 20.12% | 50.69% | 15.51% | 46.43% | 65.29% | 36.64% | 44.97% | 51.43% | 55.11% | 42.72% | 53.8% | 62.5% | 56.88% | 66.71% | 57.52% | 59.49% | 59.58% | 24.43% | 20.28% | 16.92% | 21.46% | 25.72% | 23.94%
TSO | - | 12 | 13 | 2020 | Summer | I, [%] | 0 | 0 | 53.61% | 59.57% | 55.51% | 58.44% | 57.22% | 60.12% | 52.95% | 55.84% | 31.01% | 43.3% | 30% | 39.71% | 40.03% | 39.76% | 26.96% | 31.49% | 32.86% | 33.74% | 50.43% | 45.49% | 43.71% | 50.16% | 48.41% | 55.34%
TSO | - | 12 | 16 | 2020 | Summer | I, [%] | 0 | 0 | 48.14% | 50.29% | 49.03% | 49.61% | 50.12% | 47.94% | 45.81% | 55.81% | 10.83% | 12.4% | 11.76% | 19.45% | 21.65% | 22.85% | 13.84% | 13.96% | 12.11% | 12.77% | 55.6% | 46.72% | 49.09% | 45.24% | 44.23% | 46.55%
TSO | - | 12 | 17 | 2020 | Summer | I, [%] | 0 | 0 | 62.65% | 65.62% | 65.24% | 64.72% | 64.63% | 62.51% | 53.24% | 52.58% | 23.3% | 28.98% | 28.96% | 18.5% | 19.11% | 21% | 21.82% | 16.29% | 24.61% | 24.87% | 46.24% | 46.92% | 46.14% | 45.9% | 55.12% | 60.15%
TSO | - | 14 | 15 | 2020 | Summer | I, [%] | 0 | 0 | 70.97% | 71.86% | 73.61% | 66.41% | 70.97% | 62.39% | 56.74% | 57.57% | 60.33% | 66.86% | 73.06% | 51.66% | 56.48% | 80.78% | 67.07% | 69.1% | 79.64% | 79.03% | 54.9% | 62.37% | 60.21% | 68.43% | 79.21% | 70.32%
TSO | - | 18 | 19 | 2020 | Summer | I, [%] | 0 | 0 | 28.62% | 32.92% | 34.14% | 16.09% | 20.46% | 23.3% | 17.49% | 18.99% | 11.86% | 6.07% | 7.856% | 7.691% | 7.21% | 15.09% | 27.14% | 25.67% | 27.83% | 27.24% | 21.28% | 21.42% | 21.51% | 22.68% | 15.08% | 14.93%
TSO | - | 19 | 20 | 2020 | Summer | I, [%] | 0 | 0 | 7.615% | 11.88% | 8.84% | 9.918% | 9.283% | 4.002% | 6.014% | 7.049% | 10.98% | 29.86% | 35.57% | 21.22% | 21.38% | 32.27% | 15.99% | 15.53% | 27.58% | 27.2% | 13.64% | 14.07% | 14.16% | 15.11% | 27.99% | 19.02%
TSO | - | 21 | 20 | 2020 | Summer | I, [%] | 0 | 0 | 12.75% | 12.42% | 12.53% | 9.973% | 9.081% | 18.11% | 21.57% | 11.53% | 11.19% | 13.74% | 15.34% | 13.71% | 13.52% | 19.41% | 12.36% | 10.58% | 11.35% | 10.79% | 8.819% | 6.589% | 5.272% | 7.829% | 13.82% | 8.967%
TSO | - | 21 | 22 | 2020 | Summer | I, [%] | 0 | 0 | 25.5% | 24.84% | 25.05% | 19.95% | 18.16% | 36.22% | 43.15% | 23.07% | 22.37% | 27.47% | 30.68% | 27.41% | 27.04% | 38.82% | 24.73% | 21.16% | 22.71% | 21.58% | 17.64% | 13.18% | 10.54% | 15.66% | 27.63% | 17.93%
TSO | - | 22 | 23 | 2020 | Summer | I, [%] | 0 | 0 | 26.77% | 41.85% | 28.81% | 17.12% | 17.56% | 14.78% | 26.47% | 40.85% | 46.82% | 68.18% | 50.19% | 56.4% | 59.58% | 62.14% | 74.44% | 64.91% | 58.84% | 57.95% | 30.83% | 25.64% | 34.05% | 46.09% | 45.77% | 61.13%
TSO | - | 23 | 24 | 2020 | Summer | I, [%] | 0 | 0 | 39.6% | 62.07% | 53.03% | 45.85% | 42.8% | 45.23% | 46.74% | 37.44% | 43.03% | 57.01% | 43.01% | 50.05% | 51.86% | 58.24% | 55.94% | 55.84% | 54.52% | 55.31% | 20.15% | 32.61% | 38.59% | 32% | 39.48% | 46.3%
TSO | - | 24 | 25 | 2020 | Summer | I, [%] | 0 | 0 | 22.81% | 51.04% | 38.11% | 23.4% | 22.85% | 20.08% | 18.23% | 18.87% | 19.13% | 32.79% | 18.47% | 19.92% | 18% | 18.87% | 26.42% | 19.27% | 20.83% | 20.72% | 24.1% | 22.66% | 21.53% | 19.91% | 19.72% | 16.65%
TSO | - | 24 | 26 | 2020 | Summer | I, [%] | 0 | 0 | 35.26% | 62.04% | 41.28% | 32.29% | 37.93% | 33.75% | 32.26% | 48.88% | 38.04% | 42.55% | 42.88% | 34.16% | 39.72% | 48.78% | 41.34% | 46.28% | 49.81% | 50.4% | 38.44% | 52.13% | 54.9% | 41.17% | 51.32% | 42.77%
TSO | - | 26 | 27 | 2020 | Summer | I, [%] | 0 | 0 | 35.26% | 62.04% | 41.28% | 32.29% | 37.93% | 33.75% | 32.26% | 48.88% | 38.04% | 42.55% | 42.88% | 34.16% | 39.72% | 48.78% | 41.34% | 46.28% | 49.81% | 50.4% | 38.44% | 52.13% | 54.9% | 41.17% | 51.32% | 42.77%
TSO | - | 27 | 28 | 2020 | Summer | I, [%] | 0 | 0 | 19.12% | 25.07% | 19.6% | 17.11% | 17.48% | 16.77% | 19.32% | 28.05% | 24.79% | 26.84% | 25.67% | 24.12% | 24.84% | 27.41% | 26.05% | 24.35% | 25.74% | 25.58% | 24.2% | 27.54% | 27.66% | 24.98% | 25.25% | 22.22%
TSO | - | 28 | 29 | 2020 | Summer | I, [%] | 0 | 0 | 25.41% | 30.69% | 24.85% | 22.18% | 22.62% | 21.9% | 25.19% | 35.06% | 32.54% | 34.97% | 34.39% | 33.12% | 33.61% | 36.46% | 34.44% | 32.71% | 33.91% | 33.86% | 32.38% | 35.63% | 35.69% | 33.6% | 33.7% | 29.37%
TSO | - | 7 | 29 | 2020 | Summer | I, [%] | 0 | 0 | 23.83% | 21.11% | 20.61% | 17.08% | 16.02% | 16.44% | 23.06% | 40.26% | 43.22% | 46.15% | 46.82% | 49.21% | 48.41% | 51.52% | 48.4% | 43.83% | 44.12% | 43.82% | 42.23% | 43.66% | 44.74% | 49.27% | 51.03% | 38.61%
TSO | - | 25 | 30 | 2020 | Summer | I, [%] | 0 | 0 | 38.3% | 28.79% | 40.14% | 40.84% | 40.31% | 33.26% | 30.84% | 31.47% | 30.37% | 20.31% | 31.01% | 25.87% | 29.96% | 28.63% | 25.38% | 30.06% | 35.04% | 35.36% | 38.35% | 41.88% | 38% | 34.2% | 36.23% | 31.8%
TSO | - | 30 | 31 | 2020 | Summer | I, [%] | 0 | 0 | 71.48% | 60.86% | 81.31% | 81.26% | 77.8% | 67% | 56.76% | 52.21% | 49.67% | 23.06% | 44.92% | 32.72% | 36.65% | 32.58% | 29.07% | 41.99% | 52.08% | 53.2% | 59.46% | 69.2% | 60.32% | 52.62% | 56.91% | 47.05%
TSO | - | 31 | 32 | 2020 | Summer | I, [%] | 0 | 0 | 49.05% | 67.51% | 63.42% | 51.18% | 50.32% | 52.89% | 51.15% | 49.89% | 52.92% | 52.57% | 61.09% | 64.01% | 67.17% | 70.53% | 59.04% | 63.15% | 59.01% | 61.02% | 46.64% | 53.86% | 56.29% | 56.53% | 56.67% | 56.54%
TSO | - | 32 | 33 | 2020 | Summer | I, [%] | 0 | 0 | 46.17% | 42.35% | 38.72% | 38.37% | 37.6% | 49.25% | 55.27% | 55.63% | 64.41% | 67.03% | 69.03% | 74.55% | 79.04% | 77% | 75.66% | 71.71% | 67.24% | 66.92% | 64.07% | 66.53% | 66.56% | 69.23% | 64.91% | 50.64%
TSO | - | 34 | 32 | 2020 | Summer | I, [%] | 0 | 0 | 37.03% | 52.66% | 48.06% | 37.98% | 35.42% | 33.56% | 31.66% | 25.49% | 30.21% | 37.54% | 29.85% | 31.79% | 32.55% | 31.56% | 37.67% | 33.52% | 35.26% | 35.58% | 37.53% | 37.03% | 34.16% | 33.39% | 32.91% | 28.05%
TSO | - | 34 | 35 | 2020 | Summer | I, [%] | 0 | 0 | 36.72% | 52.41% | 47.89% | 37.86% | 35.25% | 33.57% | 31.47% | 25.03% | 29.55% | 36.75% | 28.98% | 30.85% | 31.47% | 30.4% | 36.65% | 32.62% | 34.32% | 34.66% | 37.03% | 36.41% | 33.51% | 32.72% | 32.28% | 27.31%
TSO | - | 35 | 36 | 2020 | Summer | I, [%] | 0 | 0 | 15.27% | 18.03% | 16.76% | 15.07% | 14.46% | 14.25% | 16.7% | 17.43% | 19.17% | 19.56% | 17.78% | 19.46% | 19.09% | 18.07% | 18.21% | 16.95% | 17.17% | 16.57% | 17.72% | 17.95% | 17.09% | 17.89% | 16.66% | 13.86%
TSO | - | 36 | 37 | 2020 | Summer | I, [%] | 0 | 0 | 20.23% | 21.57% | 21.04% | 19.3% | 19.09% | 19.64% | 22.2% | 22.99% | 25.58% | 25.16% | 23.27% | 24.95% | 24.5% | 23.1% | 22.53% | 21.19% | 21.43% | 20.97% | 22.58% | 23.22% | 21.76% | 23.01% | 20.99% | 17.39%
TSO | - | 37 | 38 | 2020 | Summer | I, [%] | 0 | 0 | 25.71% | 25.89% | 25.75% | 23.92% | 23.98% | 25.38% | 28.4% | 29.36% | 32.93% | 31.97% | 30.05% | 31.96% | 31.57% | 29.81% | 28.61% | 27.06% | 27.16% | 26.8% | 28.68% | 29.72% | 27.77% | 29.48% | 26.66% | 21.96%
TSO | - | 37 | 39 | 2020 | Summer | I, [%] | 0 | 0 | 27.39% | 21.87% | 23.79% | 23.08% | 24.46% | 28.55% | 31.12% | 32.18% | 37.19% | 34.54% | 34.37% | 35.75% | 35.92% | 34.22% | 30.8% | 29.73% | 29.15% | 29.48% | 30.69% | 32.67% | 30.22% | 32.61% | 28.52% | 22.9%
TSO | - | 36 | 40 | 2020 | Summer | I, [%] | 0 | 0 | 25.41% | 19.77% | 22.76% | 21.66% | 23.53% | 26.97% | 27.96% | 28.6% | 33.54% | 29.76% | 29.49% | 29.94% | 28.59% | 26.97% | 22.8% | 22.52% | 23.51% | 23.91% | 25.02% | 27.07% | 23.9% | 26.5% | 22.27% | 17.98%
TSO | - | 22 | 38 | 2020 | Summer | I, [%] | 0 | 0 | 25.44% | 32.9% | 24.61% | 10.98% | 12.88% | 17.05% | 37.01% | 33.13% | 52.57% | 74.66% | 55.63% | 70.07% | 68.54% | 69.97% | 85.57% | 75.08% | 61.29% | 58.9% | 35% | 27.06% | 37.81% | 50.46% | 31.97% | 53.37%
TSO | - | 11 | 41 | 2020 | Summer | I, [%] | 0 | 0 | 9.206% | 9.147% | 8.151% | 8.097% | 8.022% | 8.392% | 9.95% | 11.23% | 11.62% | 11.41% | 11.06% | 12.21% | 12.37% | 12.37% | 11.75% | 11.2% | 10.95% | 10.99% | 11.18% | 11.68% | 11.88% | 12.14% | 11.07% | 9.515%
TSO | - | 41 | 42 | 2020 | Summer | I, [%] | 0 | 0 | 12.37% | 12.44% | 10.4% | 10.76% | 10.45% | 10.83% | 13.57% | 16.1% | 16.9% | 17.73% | 16.51% | 18.3% | 18.5% | 18.44% | 16.53% | 15.69% | 15.07% | 14.99% | 15.09% | 16.56% | 16.34% | 17.05% | 16.19% | 13.27%
TSO | - | 41 | 43 | 2020 | Summer | I, [%] | 0 | 0 | 16.55% | 16.45% | 14.43% | 15.01% | 14.73% | 14.89% | 17.87% | 20.44% | 21.5% | 22.13% | 21.54% | 23.41% | 23.68% | 23.35% | 21.37% | 20.39% | 20.26% | 20.34% | 20.54% | 21.48% | 21.86% | 22.35% | 21.14% | 17.96%
TSO | - | 38 | 44 | 2020 | Summer | I, [%] | 0 | 0 | 21.37% | 24.51% | 22.2% | 17.89% | 19.2% | 17.61% | 18.6% | 17.98% | 19.92% | 25.67% | 24.21% | 19.26% | 28.33% | 32.69% | 32.39% | 30.94% | 30.82% | 31.78% | 23.38% | 23.63% | 25.23% | 28.82% | 31.31% | 26.01%
TSO | - | 15 | 45 | 2020 | Summer | I, [%] | 0 | 0 | 36.34% | 38.39% | 35.67% | 31.31% | 32.95% | 30.98% | 34.31% | 34.73% | 38.87% | 45.19% | 44.87% | 43.18% | 44.43% | 54.35% | 52.94% | 50.87% | 51.7% | 51.57% | 40.77% | 41.91% | 43.86% | 48.62% | 47.33% | 40.82%
TSO | - | 14 | 46 | 2020 | Summer | I, [%] | 0 | 0 | 29.6% | 30.41% | 26.47% | 24.95% | 27.62% | 27.42% | 30.84% | 25.69% | 28.93% | 43.19% | 39.92% | 44.8% | 54.26% | 67.63% | 67.54% | 62.85% | 60.78% | 60.68% | 45.84% | 46.12% | 55.03% | 61.66% | 58.48% | 55%
TSO | - | 46 | 47 | 2020 | Summer | I, [%] | 0 | 0 | 29.5% | 30.31% | 26.32% | 24.72% | 27.42% | 27.17% | 30.69% | 25.74% | 29.04% | 43.32% | 40.03% | 44.91% | 54.34% | 67.69% | 67.59% | 62.88% | 60.82% | 60.72% | 45.87% | 46.15% | 55.04% | 61.66% | 58.47% | 54.95%
TSO | - | 47 | 48 | 2020 | Summer | I, [%] | 0 | 0 | 31.03% | 44.91% | 41.38% | 37.58% | 33.41% | 38.88% | 34.64% | 35.44% | 39.71% | 35.03% | 28.67% | 28.65% | 17.84% | 16.01% | 14.59% | 14.74% | 17.71% | 19.51% | 23.32% | 19.16% | 14.2% | 13.29% | 9.425% | 7.537%
TSO | - | 48 | 49 | 2020 | Summer | I, [%] | 0 | 0 | 6.559% | 16.87% | 13.37% | 10.53% | 9.497% | 11.19% | 7.622% | 8.291% | 8.782% | 10.41% | 4.904% | 3.519% | 5.847% | 8.448% | 9.433% | 9.713% | 7.631% | 6.789% | 5.601% | 4.639% | 8.318% | 10.55% | 8.785% | 9.601%
TSO | - | 49 | 50 | 2020 | Summer | I, [%] | 0 | 0 | 22.64% | 17.87% | 22.05% | 24.05% | 24.09% | 26.33% | 23.62% | 31.91% | 32.39% | 24.56% | 31.02% | 26.59% | 24.36% | 23.14% | 16.53% | 17.98% | 20.31% | 21.68% | 27.55% | 26.62% | 24.81% | 24.28% | 23.47% | 24%
TSO | - | 50 | 51 | 2020 | Summer | I, [%] | 0 | 0 | 11.39% | 14.63% | 11.23% | 10.91% | 10.83% | 12.15% | 13.62% | 9.048% | 15.85% | 19.04% | 15.93% | 21.62% | 21.96% | 23.31% | 22.01% | 21.5% | 19.18% | 20.7% | 17.59% | 15.75% | 18.1% | 19.58% | 17.4% | 14.14%
TSO | - | 10 | 51 | 2020 | Summer | I, [%] | 0 | 0 | 35.93% | 39.18% | 34.15% | 33.66% | 32.27% | 32.05% | 38.22% | 45.52% | 49.67% | 53.75% | 48.92% | 56.61% | 56.19% | 58.69% | 55.23% | 52.41% | 49.85% | 50.17% | 49.54% | 48.86% | 50.36% | 51.92% | 46.94% | 42.68%
TSO | - | 13 | 49 | 2020 | Summer | I, [%] | 0 | 0 | 25.8% | 33.64% | 26.22% | 22.64% | 23.58% | 24.62% | 28.54% | 27.29% | 30.66% | 43.44% | 34.05% | 41.31% | 43.48% | 46.61% | 49.47% | 43.67% | 41.76% | 42.36% | 39.82% | 35.96% | 40.72% | 43.43% | 38.93% | 34.69%
TSO | - | 29 | 52 | 2020 | Summer | I, [%] | 0 | 0 | 15.14% | 9.405% | 12.65% | 9.39% | 9.609% | 9.349% | 13.05% | 26.21% | 28.72% | 30.11% | 32.31% | 33.78% | 33.02% | 34.9% | 32.46% | 28.75% | 28.64% | 28.74% | 28.1% | 28.45% | 28.71% | 34.16% | 36.12% | 26.56%
TSO | - | 52 | 53 | 2020 | Summer | I, [%] | 0 | 0 | 9.585% | 5.787% | 8.005% | 5.142% | 4.912% | 4.11% | 7.972% | 19.23% | 20.4% | 20.54% | 22.23% | 22.89% | 22.13% | 23.95% | 22.7% | 18.91% | 19.21% | 18.99% | 19.66% | 19.97% | 20.35% | 24.94% | 27.06% | 19.19%
TSO | - | 53 | 54 | 2020 | Summer | I, [%] | 0 | 0 | 4.171% | 2.286% | 1.739% | 1.455% | 2.601% | 2.52% | 5.716% | 11.41% | 15.7% | 17.87% | 16.12% | 22.18% | 20.92% | 20.49% | 19.68% | 17.27% | 15.75% | 16.03% | 14.65% | 13.53% | 14.91% | 18.26% | 18.61% | 13.5%
TSO | - | 54 | 55 | 2020 | Summer | I, [%] | 0 | 0 | 5.558% | 3.69% | 4.438% | 2.842% | 4.08% | 2.409% | 6.232% | 12.66% | 17.07% | 19.29% | 17.45% | 23.53% | 22.27% | 21.82% | 20.84% | 18.38% | 17.02% | 17.4% | 15.19% | 14.24% | 15.43% | 18.84% | 19.29% | 14.1%
TSO | - | 11 | 43 | 2020 | Summer | I, [%] | 0 | 0 | 18.63% | 18.5% | 17.12% | 15.11% | 15.39% | 17.52% | 20.17% | 21.94% | 21.77% | 18.7% | 17.91% | 20.74% | 21.17% | 22% | 23% | 21.91% | 20.53% | 20.62% | 21.35% | 22.24% | 22.61% | 23.09% | 19.01% | 16.92%
TSO | - | 44 | 45 | 2020 | Summer | I, [%] | 0 | 0 | 36.35% | 38.41% | 35.66% | 31.26% | 32.91% | 30.9% | 34.29% | 34.85% | 38.96% | 45.27% | 44.96% | 43.25% | 44.49% | 54.4% | 52.99% | 50.91% | 51.76% | 51.62% | 40.87% | 42% | 43.93% | 48.67% | 47.36% | 40.8%
TSO | - | 40 | 56 | 2020 | Summer | I, [%] | 0 | 0 | 25.41% | 19.77% | 22.76% | 21.66% | 23.53% | 26.97% | 27.96% | 28.6% | 33.54% | 29.76% | 29.49% | 29.94% | 28.59% | 26.97% | 22.8% | 22.52% | 23.51% | 23.91% | 25.02% | 27.07% | 23.9% | 26.5% | 22.27% | 17.98%
TSO | - | 56 | 41 | 2020 | Summer | I, [%] | 0 | 0 | 40.1% | 41.8% | 33.01% | 34.02% | 32.1% | 33.4% | 40.94% | 45.67% | 47.84% | 51.79% | 50.24% | 52.97% | 53.88% | 54.69% | 51.92% | 50.33% | 48.54% | 48.69% | 49.87% | 54.24% | 53.17% | 54.97% | 53.98% | 43.27%
TSO | - | 56 | 42 | 2020 | Summer | I, [%] | 0 | 0 | 15.2% | 19.37% | 13.47% | 11.78% | 9.352% | 9.515% | 11.78% | 14.35% | 11.64% | 14.34% | 15.45% | 13.84% | 15.74% | 16.68% | 19.62% | 20.14% | 17.63% | 18.36% | 20.63% | 21.72% | 21.02% | 19.78% | 22.06% | 16.15%
TSO | - | 39 | 57 | 2020 | Summer | I, [%] | 0 | 0 | 27.39% | 21.87% | 23.79% | 23.08% | 24.46% | 28.55% | 31.12% | 32.18% | 37.19% | 34.54% | 34.37% | 35.75% | 35.92% | 34.22% | 30.8% | 29.73% | 29.15% | 29.48% | 30.69% | 32.67% | 30.22% | 32.61% | 28.52% | 22.9%
TSO | - | 57 | 56 | 2020 | Summer | I, [%] | 0 | 0 | 10.52% | 10.49% | 5.902% | 7.823% | 7.248% | 12% | 16.34% | 17.95% | 19.65% | 23.95% | 25.95% | 29.54% | 34.51% | 34.48% | 35.67% | 33.2% | 28.99% | 28.42% | 25.53% | 25.71% | 28.11% | 28.32% | 27.92% | 20.91%
TSO | - | 38 | 49 | 2020 | Summer | I, [%] | 0 | 0 | 5.638% | 6.419% | 4.74% | 5.446% | 4.784% | 5.095% | 7.693% | 3.753% | 2.615% | 5.148% | 3.951% | 8.185% | 10.75% | 11.58% | 13.04% | 12.85% | 12.18% | 11.53% | 9.089% | 7.733% | 9.739% | 11.54% | 8.887% | 7.499%
TSO | - | 38 | 48 | 2020 | Summer | I, [%] | 0 | 0 | 26.52% | 29.32% | 29.18% | 29.01% | 25.65% | 29.38% | 30.62% | 28.02% | 31.14% | 26.47% | 24.32% | 28.53% | 23.9% | 22.33% | 23.45% | 22.81% | 25.06% | 25.57% | 24.88% | 20.83% | 17.81% | 18.11% | 12.41% | 2.564%
TSO | - | 9 | 55 | 2020 | Summer | I, [%] | 0 | 0 | 14.99% | 14.56% | 14.92% | 14.24% | 10.94% | 8.223% | 12.86% | 16.52% | 20.08% | 21.43% | 20.12% | 24.79% | 23.56% | 22.72% | 22.55% | 21.77% | 22.13% | 23.12% | 21.33% | 20.71% | 20.54% | 22.16% | 24.14% | 19.65%
TSO | - | 1 | 2 | 2020 | Summer | I, [%] | Expected | - | 45.45% | 60% | 69.37% | 64.46% | 61.96% | 76.83% | 45.81% | 67.42% | 80.22% | 59.09% | 76.7% | 71.69% | 67.58% | 68.71% | 27.47% | 33.42% | 49.47% | 61.04% | 42.14% | 40.61% | 40.69% | 32.34% | 22.82% | 23.75%
TSO | - | 2 | 3 | 2020 | Summer | I, [%] | Expected | - | 88.21% | 81.53% | 92.15% | 94.3% | 91.77% | 94.72% | 88.51% | 33.96% | 35.75% | 44% | 30.7% | 62.61% | 65.05% | 52.68% | 77.36% | 80.82% | 58.27% | 58.93% | 72.64% | 63.22% | 64.72% | 81.88% | 61.99% | 68.43%
TSO | - | 3 | 4 | 2020 | Summer | I, [%] | Expected | - | 37.81% | 34.25% | 34.11% | 35.19% | 36.65% | 39.62% | 48.26% | 34.69% | 41.29% | 39.84% | 34% | 34.55% | 34.97% | 34.14% | 40.15% | 38.62% | 39.03% | 37.35% | 29.9% | 30.16% | 30.11% | 34.59% | 29.35% | 30.34%
TSO | - | 4 | 5 | 2020 | Summer | I, [%] | Expected | - | 95.82% | 95.66% | 96.95% | 97.29% | 97.18% | 97.48% | 95.43% | 89.12% | 87.27% | 85.84% | 86.86% | 81.91% | 81.6% | 82.68% | 89.57% | 89.25% | 90.94% | 90.51% | 83.61% | 87.07% | 87.54% | 82.82% | 88.8% | 94.25%
TSO | - | 4 | 6 | 2020 | Summer | I, [%] | Expected | - | 13.85% | 14.3% | 14.08% | 14.53% | 14.78% | 15.64% | 14.43% | 18.18% | 17.88% | 17.93% | 17.9% | 20.51% | 19.95% | 20.44% | 17.56% | 16.96% | 16.09% | 15.92% | 17.26% | 18.71% | 19.42% | 18.8% | 18.75% | 15.77%
TSO | - | 6 | 7 | 2020 | Summer | I, [%] | Expected | - | 41.79% | 38.29% | 44.18% | 40.63% | 40.2% | 37.23% | 39.03% | 26.65% | 38.46% | 51.94% | 49.55% | 30.11% | 33% | 59.09% | 44.47% | 41.62% | 55.34% | 55.05% | 30.38% | 25.25% | 24.01% | 33.26% | 36.91% | 39.43%
TSO | - | 6 | 8 | 2020 | Summer | I, [%] | Expected | - | 92.15% | 91.96% | 95.71% | 96.75% | 96.83% | 97.31% | 93.14% | 76.34% | 61.52% | 56.32% | 59.1% | 49.93% | 49.33% | 48.82% | 65.06% | 68.58% | 73.41% | 71.81% | 70.19% | 82.16% | 84.97% | 67.89% | 76.06% | 89.17%
TSO | - | 8 | 9 | 2020 | Summer | I, [%] | Expected | - | 48.02% | 39.08% | 59.78% | 37.26% | 57.74% | 62.6% | 43.83% | 87.11% | 92.81% | 92.25% | 93.16% | 94.04% | 93.3% | 90.04% | 86.91% | 84.97% | 89.98% | 89.63% | 61.23% | 80.97% | 78.28% | 74.41% | 82.58% | 58.93%
TSO | - | 9 | 10 | 2020 | Summer | I, [%] | Expected | - | 25.74% | 42.43% | 18.08% | 26.42% | 17.08% | 15.73% | 23.18% | 58.72% | 49.42% | 48.72% | 49.32% | 44.21% | 41.63% | 38.45% | 34.82% | 28.98% | 41.14% | 40.34% | 27.91% | 44.12% | 41.75% | 30.11% | 43.16% | 41.21%
TSO | - | 9 | 11 | 2020 | Summer | I, [%] | Expected | - | 25.17% | 39.41% | 13.42% | 23.05% | 15.29% | 14.52% | 24.01% | 55.08% | 45.07% | 35.3% | 41.2% | 37.48% | 35.03% | 34.04% | 26.95% | 31.7% | 34.81% | 33.73% | 27.57% | 46.25% | 45.85% | 32.16% | 44.91% | 40.73%
TSO | - | 9 | 12 | 2020 | Summer | I, [%] | Expected | - | 33.09% | 51.74% | 31.42% | 36.48% | 30.38% | 30.29% | 28.46% | 64.95% | 48.58% | 51.49% | 45.11% | 47.94% | 47.36% | 41.81% | 33.22% | 30.93% | 43.29% | 43.11% | 35.46% | 44.8% | 41.26% | 35.8% | 44.03% | 46.38%
TSO | - | 9 | 13 | 2020 | Summer | I, [%] | Expected | - | 10.33% | 24.43% | 7.568% | 10.08% | 9.078% | 13.66% | 10.3% | 37.84% | 30.65% | 24.71% | 27.93% | 25.15% | 24.58% | 22.35% | 18.66% | 20.99% | 24.54% | 23.68% | 10.79% | 28.47% | 27.73% | 13.83% | 28.79% | 26.3%
TSO | - | 13 | 14 | 2020 | Summer | I, [%] | Expected | - | 48.9% | 50.51% | 53.6% | 54.11% | 54.72% | 53.14% | 50.73% | 36.88% | 17.5% | 18.73% | 16.89% | 18.82% | 23.3% | 19.86% | 19.87% | 13.4% | 16.18% | 16.51% | 43.24% | 34.37% | 38.39% | 40.69% | 38.11% | 46.89%
TSO | - | 13 | 15 | 2020 | Summer | I, [%] | Expected | - | 65.07% | 66.33% | 69.88% | 64.79% | 68.22% | 61.35% | 54.42% | 51.12% | 46.73% | 49.19% | 54.45% | 32.67% | 31.41% | 50.33% | 33.3% | 36.98% | 51.19% | 49.78% | 45.44% | 48.47% | 44.31% | 49.87% | 60.07% | 60.79%
TSO | - | 1 | 15 | 2020 | Summer | I, [%] | Expected | - | 65.63% | 61.47% | 69.2% | 67.66% | 67.85% | 67.18% | 60.01% | 30.58% | 40.11% | 41.97% | 39.45% | 46.79% | 49.01% | 51.48% | 64.92% | 66.09% | 50.96% | 52.01% | 46.02% | 43.88% | 45.12% | 64.37% | 59.94% | 59.02%
TSO | - | 1 | 16 | 2020 | Summer | I, [%] | Expected | - | 42.9% | 43.88% | 43.82% | 43.27% | 43.23% | 42.73% | 39.47% | 35.16% | 35.86% | 38.14% | 37.61% | 34.3% | 33.7% | 35.13% | 35.22% | 32.81% | 36.48% | 36.43% | 30.89% | 35.23% | 34.12% | 37.77% | 41.91% | 42.9%
TSO | - | 1 | 17 | 2020 | Summer | I, [%] | Expected | - | 96.89% | 97.81% | 97.89% | 97.46% | 98.18% | 98.3% | 96.78% | 90.97% | 96.45% | 97.46% | 96.8% | 96.72% | 95.54% | 95.86% | 96.01% | 88.27% | 96.72% | 96.59% | 81.12% | 87.77% | 89.91% | 94.8% | 95.9% | 97.37%
TSO | - | 3 | 15 | 2020 | Summer | I, [%] | Expected | - | 26.85% | 32.48% | 28.69% | 21.63% | 25.84% | 18.8% | 18.18% | 64.24% | 58.36% | 60.73% | 67.4% | 43.72% | 43.26% | 64.37% | 31.28% | 32.97% | 59.81% | 58.48% | 30.19% | 41.4% | 38.27% | 31.92% | 44.43% | 32.86%
TSO | - | 4 | 18 | 2020 | Summer | I, [%] | Expected | - | 19.51% | 18.43% | 16.74% | 16.08% | 16.93% | 18.54% | 24.55% | 28.08% | 28.71% | 27.46% | 24.4% | 28.79% | 28.14% | 27.98% | 25.59% | 24.54% | 23.53% | 23.06% | 22.65% | 25.34% | 25.66% | 26.49% | 22.66% | 19.72%
TSO | - | 5 | 6 | 2020 | Summer | I, [%] | Expected | - | 11.71% | 11.58% | 11.08% | 11.9% | 12.15% | 14.02% | 13.04% | 22.76% | 24.59% | 25.38% | 25.25% | 30.61% | 29.43% | 30.27% | 26.13% | 23.78% | 22.23% | 21.87% | 23.53% | 24.78% | 26.28% | 28.21% | 28.6% | 20.3%
TSO | - | 7 | 8 | 2020 | Summer | I, [%] | Expected | - | 46.04% | 47.14% | 42.02% | 44.52% | 44.28% | 48.95% | 49.49% | 70.48% | 60.64% | 47.79% | 53.81% | 72.43% | 69.15% | 45.36% | 65% | 61.7% | 47.28% | 46.06% | 68.48% | 78.09% | 81.29% | 76.21% | 79.53% | 65.71%
TSO | - | 10 | 12 | 2020 | Summer | I, [%] | Expected | - | 34.78% | 34.93% | 38.9% | 36.17% | 37.56% | 37.54% | 34.05% | 20.73% | 18.99% | 29.8% | 13.49% | 35.16% | 38.43% | 44.18% | 37.86% | 41.33% | 33.2% | 35.02% | 41.92% | 29.9% | 30.44% | 43.74% | 30.42% | 32.41%
TSO | - | 11 | 13 | 2020 | Summer | I, [%] | Expected | - | 21.66% | 20.12% | 50.69% | 15.51% | 46.43% | 65.29% | 36.64% | 44.97% | 51.43% | 55.11% | 42.72% | 53.8% | 62.5% | 56.88% | 66.71% | 57.52% | 59.49% | 59.58% | 24.43% | 20.28% | 16.92% | 21.46% | 25.72% | 23.94%
TSO | - | 12 | 13 | 2020 | Summer | I, [%] | Expected | - | 53.61% | 59.57% | 55.51% | 58.44% | 57.22% | 60.12% | 52.95% | 55.84% | 31.01% | 43.3% | 30% | 39.71% | 40.03% | 39.76% | 26.96% | 31.49% | 32.86% | 33.74% | 50.43% | 45.49% | 43.71% | 50.16% | 48.41% | 55.34%
TSO | - | 12 | 16 | 2020 | Summer | I, [%] | Expected | - | 48.14% | 50.29% | 49.03% | 49.61% | 50.12% | 47.94% | 45.81% | 55.81% | 10.83% | 12.4% | 11.76% | 19.45% | 21.65% | 22.85% | 13.84% | 13.96% | 12.11% | 12.77% | 55.6% | 46.72% | 49.09% | 45.24% | 44.23% | 46.55%
TSO | - | 12 | 17 | 2020 | Summer | I, [%] | Expected | - | 62.65% | 65.62% | 65.24% | 64.72% | 64.63% | 62.51% | 53.24% | 52.58% | 23.3% | 28.98% | 28.96% | 18.5% | 19.11% | 21% | 21.82% | 16.29% | 24.61% | 24.87% | 46.24% | 46.92% | 46.14% | 45.9% | 55.12% | 60.15%
TSO | - | 14 | 15 | 2020 | Summer | I, [%] | Expected | - | 70.97% | 71.86% | 73.61% | 66.41% | 70.97% | 62.39% | 56.74% | 57.57% | 60.33% | 66.86% | 73.06% | 51.66% | 56.48% | 80.78% | 67.07% | 69.1% | 79.64% | 79.03% | 54.9% | 62.37% | 60.21% | 68.43% | 79.21% | 70.32%
TSO | - | 18 | 19 | 2020 | Summer | I, [%] | Expected | - | 28.62% | 32.92% | 34.14% | 16.09% | 20.46% | 23.3% | 17.49% | 18.99% | 11.86% | 6.07% | 7.856% | 7.691% | 7.21% | 15.09% | 27.14% | 25.67% | 27.83% | 27.24% | 21.28% | 21.42% | 21.51% | 22.68% | 15.08% | 14.93%
TSO | - | 19 | 20 | 2020 | Summer | I, [%] | Expected | - | 7.615% | 11.88% | 8.84% | 9.918% | 9.283% | 4.002% | 6.014% | 7.049% | 10.98% | 29.86% | 35.57% | 21.22% | 21.38% | 32.27% | 15.99% | 15.53% | 27.58% | 27.2% | 13.64% | 14.07% | 14.16% | 15.11% | 27.99% | 19.02%
TSO | - | 21 | 20 | 2020 | Summer | I, [%] | Expected | - | 12.75% | 12.42% | 12.53% | 9.973% | 9.081% | 18.11% | 21.57% | 11.53% | 11.19% | 13.74% | 15.34% | 13.71% | 13.52% | 19.41% | 12.36% | 10.58% | 11.35% | 10.79% | 8.819% | 6.589% | 5.272% | 7.829% | 13.82% | 8.967%
TSO | - | 21 | 22 | 2020 | Summer | I, [%] | Expected | - | 25.5% | 24.84% | 25.05% | 19.95% | 18.16% | 36.22% | 43.15% | 23.07% | 22.37% | 27.47% | 30.68% | 27.41% | 27.04% | 38.82% | 24.73% | 21.16% | 22.71% | 21.58% | 17.64% | 13.18% | 10.54% | 15.66% | 27.63% | 17.93%
TSO | - | 22 | 23 | 2020 | Summer | I, [%] | Expected | - | 26.77% | 41.85% | 28.81% | 17.12% | 17.56% | 14.78% | 26.47% | 40.85% | 46.82% | 68.18% | 50.19% | 56.4% | 59.58% | 62.14% | 74.44% | 64.91% | 58.84% | 57.95% | 30.83% | 25.64% | 34.05% | 46.09% | 45.77% | 61.13%
TSO | - | 23 | 24 | 2020 | Summer | I, [%] | Expected | - | 39.6% | 62.07% | 53.03% | 45.85% | 42.8% | 45.23% | 46.74% | 37.44% | 43.03% | 57.01% | 43.01% | 50.05% | 51.86% | 58.24% | 55.94% | 55.84% | 54.52% | 55.31% | 20.15% | 32.61% | 38.59% | 32% | 39.48% | 46.3%
TSO | - | 24 | 25 | 2020 | Summer | I, [%] | Expected | - | 22.81% | 51.04% | 38.11% | 23.4% | 22.85% | 20.08% | 18.23% | 18.87% | 19.13% | 32.79% | 18.47% | 19.92% | 18% | 18.87% | 26.42% | 19.27% | 20.83% | 20.72% | 24.1% | 22.66% | 21.53% | 19.91% | 19.72% | 16.65%
TSO | - | 24 | 26 | 2020 | Summer | I, [%] | Expected | - | 35.26% | 62.04% | 41.28% | 32.29% | 37.93% | 33.75% | 32.26% | 48.88% | 38.04% | 42.55% | 42.88% | 34.16% | 39.72% | 48.78% | 41.34% | 46.28% | 49.81% | 50.4% | 38.44% | 52.13% | 54.9% | 41.17% | 51.32% | 42.77%
TSO | - | 26 | 27 | 2020 | Summer | I, [%] | Expected | - | 35.26% | 62.04% | 41.28% | 32.29% | 37.93% | 33.75% | 32.26% | 48.88% | 38.04% | 42.55% | 42.88% | 34.16% | 39.72% | 48.78% | 41.34% | 46.28% | 49.81% | 50.4% | 38.44% | 52.13% | 54.9% | 41.17% | 51.32% | 42.77%
TSO | - | 27 | 28 | 2020 | Summer | I, [%] | Expected | - | 19.12% | 25.07% | 19.6% | 17.11% | 17.48% | 16.77% | 19.32% | 28.05% | 24.79% | 26.84% | 25.67% | 24.12% | 24.84% | 27.41% | 26.05% | 24.35% | 25.74% | 25.58% | 24.2% | 27.54% | 27.66% | 24.98% | 25.25% | 22.22%
TSO | - | 28 | 29 | 2020 | Summer | I, [%] | Expected | - | 25.41% | 30.69% | 24.85% | 22.18% | 22.62% | 21.9% | 25.19% | 35.06% | 32.54% | 34.97% | 34.39% | 33.12% | 33.61% | 36.46% | 34.44% | 32.71% | 33.91% | 33.86% | 32.38% | 35.63% | 35.69% | 33.6% | 33.7% | 29.37%
TSO | - | 7 | 29 | 2020 | Summer | I, [%] | Expected | - | 23.83% | 21.11% | 20.61% | 17.08% | 16.02% | 16.44% | 23.06% | 40.26% | 43.22% | 46.15% | 46.82% | 49.21% | 48.41% | 51.52% | 48.4% | 43.83% | 44.12% | 43.82% | 42.23% | 43.66% | 44.74% | 49.27% | 51.03% | 38.61%
TSO | - | 25 | 30 | 2020 | Summer | I, [%] | Expected | - | 38.3% | 28.79% | 40.14% | 40.84% | 40.31% | 33.26% | 30.84% | 31.47% | 30.37% | 20.31% | 31.01% | 25.87% | 29.96% | 28.63% | 25.38% | 30.06% | 35.04% | 35.36% | 38.35% | 41.88% | 38% | 34.2% | 36.23% | 31.8%
TSO | - | 30 | 31 | 2020 | Summer | I, [%] | Expected | - | 71.48% | 60.86% | 81.31% | 81.26% | 77.8% | 67% | 56.76% | 52.21% | 49.67% | 23.06% | 44.92% | 32.72% | 36.65% | 32.58% | 29.07% | 41.99% | 52.08% | 53.2% | 59.46% | 69.2% | 60.32% | 52.62% | 56.91% | 47.05%
TSO | - | 31 | 32 | 2020 | Summer | I, [%] | Expected | - | 49.05% | 67.51% | 63.42% | 51.18% | 50.32% | 52.89% | 51.15% | 49.89% | 52.92% | 52.57% | 61.09% | 64.01% | 67.17% | 70.53% | 59.04% | 63.15% | 59.01% | 61.02% | 46.64% | 53.86% | 56.29% | 56.53% | 56.67% | 56.54%
TSO | - | 32 | 33 | 2020 | Summer | I, [%] | Expected | - | 46.17% | 42.35% | 38.72% | 38.37% | 37.6% | 49.25% | 55.27% | 55.63% | 64.41% | 67.03% | 69.03% | 74.55% | 79.04% | 77% | 75.66% | 71.71% | 67.24% | 66.92% | 64.07% | 66.53% | 66.56% | 69.23% | 64.91% | 50.64%
TSO | - | 34 | 32 | 2020 | Summer | I, [%] | Expected | - | 37.03% | 52.66% | 48.06% | 37.98% | 35.42% | 33.56% | 31.66% | 25.49% | 30.21% | 37.54% | 29.85% | 31.79% | 32.55% | 31.56% | 37.67% | 33.52% | 35.26% | 35.58% | 37.53% | 37.03% | 34.16% | 33.39% | 32.91% | 28.05%
TSO | - | 34 | 35 | 2020 | Summer | I, [%] | Expected | - | 36.72% | 52.41% | 47.89% | 37.86% | 35.25% | 33.57% | 31.47% | 25.03% | 29.55% | 36.75% | 28.98% | 30.85% | 31.47% | 30.4% | 36.65% | 32.62% | 34.32% | 34.66% | 37.03% | 36.41% | 33.51% | 32.72% | 32.28% | 27.31%
TSO | - | 35 | 36 | 2020 | Summer | I, [%] | Expected | - | 15.27% | 18.03% | 16.76% | 15.07% | 14.46% | 14.25% | 16.7% | 17.43% | 19.17% | 19.56% | 17.78% | 19.46% | 19.09% | 18.07% | 18.21% | 16.95% | 17.17% | 16.57% | 17.72% | 17.95% | 17.09% | 17.89% | 16.66% | 13.86%
TSO | - | 36 | 37 | 2020 | Summer | I, [%] | Expected | - | 20.23% | 21.57% | 21.04% | 19.3% | 19.09% | 19.64% | 22.2% | 22.99% | 25.58% | 25.16% | 23.27% | 24.95% | 24.5% | 23.1% | 22.53% | 21.19% | 21.43% | 20.97% | 22.58% | 23.22% | 21.76% | 23.01% | 20.99% | 17.39%
TSO | - | 37 | 38 | 2020 | Summer | I, [%] | Expected | - | 25.71% | 25.89% | 25.75% | 23.92% | 23.98% | 25.38% | 28.4% | 29.36% | 32.93% | 31.97% | 30.05% | 31.96% | 31.57% | 29.81% | 28.61% | 27.06% | 27.16% | 26.8% | 28.68% | 29.72% | 27.77% | 29.48% | 26.66% | 21.96%
TSO | - | 37 | 39 | 2020 | Summer | I, [%] | Expected | - | 27.39% | 21.87% | 23.79% | 23.08% | 24.46% | 28.55% | 31.12% | 32.18% | 37.19% | 34.54% | 34.37% | 35.75% | 35.92% | 34.22% | 30.8% | 29.73% | 29.15% | 29.48% | 30.69% | 32.67% | 30.22% | 32.61% | 28.52% | 22.9%
TSO | - | 36 | 40 | 2020 | Summer | I, [%] | Expected | - | 25.41% | 19.77% | 22.76% | 21.66% | 23.53% | 26.97% | 27.96% | 28.6% | 33.54% | 29.76% | 29.49% | 29.94% | 28.59% | 26.97% | 22.8% | 22.52% | 23.51% | 23.91% | 25.02% | 27.07% | 23.9% | 26.5% | 22.27% | 17.98%
TSO | - | 22 | 38 | 2020 | Summer | I, [%] | Expected | - | 25.44% | 32.9% | 24.61% | 10.98% | 12.88% | 17.05% | 37.01% | 33.13% | 52.57% | 74.66% | 55.63% | 70.07% | 68.54% | 69.97% | 85.57% | 75.08% | 61.29% | 58.9% | 35% | 27.06% | 37.81% | 50.46% | 31.97% | 53.37%
TSO | - | 11 | 41 | 2020 | Summer | I, [%] | Expected | - | 9.206% | 9.147% | 8.151% | 8.097% | 8.022% | 8.392% | 9.95% | 11.23% | 11.62% | 11.41% | 11.06% | 12.21% | 12.37% | 12.37% | 11.75% | 11.2% | 10.95% | 10.99% | 11.18% | 11.68% | 11.88% | 12.14% | 11.07% | 9.515%
TSO | - | 41 | 42 | 2020 | Summer | I, [%] | Expected | - | 12.37% | 12.44% | 10.4% | 10.76% | 10.45% | 10.83% | 13.57% | 16.1% | 16.9% | 17.73% | 16.51% | 18.3% | 18.5% | 18.44% | 16.53% | 15.69% | 15.07% | 14.99% | 15.09% | 16.56% | 16.34% | 17.05% | 16.19% | 13.27%
TSO | - | 41 | 43 | 2020 | Summer | I, [%] | Expected | - | 16.55% | 16.45% | 14.43% | 15.01% | 14.73% | 14.89% | 17.87% | 20.44% | 21.5% | 22.13% | 21.54% | 23.41% | 23.68% | 23.35% | 21.37% | 20.39% | 20.26% | 20.34% | 20.54% | 21.48% | 21.86% | 22.35% | 21.14% | 17.96%
TSO | - | 38 | 44 | 2020 | Summer | I, [%] | Expected | - | 21.37% | 24.51% | 22.2% | 17.89% | 19.2% | 17.61% | 18.6% | 17.98% | 19.92% | 25.67% | 24.21% | 19.26% | 28.33% | 32.69% | 32.39% | 30.94% | 30.82% | 31.78% | 23.38% | 23.63% | 25.23% | 28.82% | 31.31% | 26.01%
TSO | - | 15 | 45 | 2020 | Summer | I, [%] | Expected | - | 36.34% | 38.39% | 35.67% | 31.31% | 32.95% | 30.98% | 34.31% | 34.73% | 38.87% | 45.19% | 44.87% | 43.18% | 44.43% | 54.35% | 52.94% | 50.87% | 51.7% | 51.57% | 40.77% | 41.91% | 43.86% | 48.62% | 47.33% | 40.82%
TSO | - | 14 | 46 | 2020 | Summer | I, [%] | Expected | - | 29.6% | 30.41% | 26.47% | 24.95% | 27.62% | 27.42% | 30.84% | 25.69% | 28.93% | 43.19% | 39.92% | 44.8% | 54.26% | 67.63% | 67.54% | 62.85% | 60.78% | 60.68% | 45.84% | 46.12% | 55.03% | 61.66% | 58.48% | 55%
TSO | - | 46 | 47 | 2020 | Summer | I, [%] | Expected | - | 29.5% | 30.31% | 26.32% | 24.72% | 27.42% | 27.17% | 30.69% | 25.74% | 29.04% | 43.32% | 40.03% | 44.91% | 54.34% | 67.69% | 67.59% | 62.88% | 60.82% | 60.72% | 45.87% | 46.15% | 55.04% | 61.66% | 58.47% | 54.95%
TSO | - | 47 | 48 | 2020 | Summer | I, [%] | Expected | - | 31.03% | 44.91% | 41.38% | 37.58% | 33.41% | 38.88% | 34.64% | 35.44% | 39.71% | 35.03% | 28.67% | 28.65% | 17.84% | 16.01% | 14.59% | 14.74% | 17.71% | 19.51% | 23.32% | 19.16% | 14.2% | 13.29% | 9.425% | 7.537%
TSO | - | 48 | 49 | 2020 | Summer | I, [%] | Expected | - | 6.559% | 16.87% | 13.37% | 10.53% | 9.497% | 11.19% | 7.622% | 8.291% | 8.782% | 10.41% | 4.904% | 3.519% | 5.847% | 8.448% | 9.433% | 9.713% | 7.631% | 6.789% | 5.601% | 4.639% | 8.318% | 10.55% | 8.785% | 9.601%
TSO | - | 49 | 50 | 2020 | Summer | I, [%] | Expected | - | 22.64% | 17.87% | 22.05% | 24.05% | 24.09% | 26.33% | 23.62% | 31.91% | 32.39% | 24.56% | 31.02% | 26.59% | 24.36% | 23.14% | 16.53% | 17.98% | 20.31% | 21.68% | 27.55% | 26.62% | 24.81% | 24.28% | 23.47% | 24%
TSO | - | 50 | 51 | 2020 | Summer | I, [%] | Expected | - | 11.39% | 14.63% | 11.23% | 10.91% | 10.83% | 12.15% | 13.62% | 9.048% | 15.85% | 19.04% | 15.93% | 21.62% | 21.96% | 23.31% | 22.01% | 21.5% | 19.18% | 20.7% | 17.59% | 15.75% | 18.1% | 19.58% | 17.4% | 14.14%
TSO | - | 10 | 51 | 2020 | Summer | I, [%] | Expected | - | 35.93% | 39.18% | 34.15% | 33.66% | 32.27% | 32.05% | 38.22% | 45.52% | 49.67% | 53.75% | 48.92% | 56.61% | 56.19% | 58.69% | 55.23% | 52.41% | 49.85% | 50.17% | 49.54% | 48.86% | 50.36% | 51.92% | 46.94% | 42.68%
TSO | - | 13 | 49 | 2020 | Summer | I, [%] | Expected | - | 25.8% | 33.64% | 26.22% | 22.64% | 23.58% | 24.62% | 28.54% | 27.29% | 30.66% | 43.44% | 34.05% | 41.31% | 43.48% | 46.61% | 49.47% | 43.67% | 41.76% | 42.36% | 39.82% | 35.96% | 40.72% | 43.43% | 38.93% | 34.69%
TSO | - | 29 | 52 | 2020 | Summer | I, [%] | Expected | - | 15.14% | 9.405% | 12.65% | 9.39% | 9.609% | 9.349% | 13.05% | 26.21% | 28.72% | 30.11% | 32.31% | 33.78% | 33.02% | 34.9% | 32.46% | 28.75% | 28.64% | 28.74% | 28.1% | 28.45% | 28.71% | 34.16% | 36.12% | 26.56%
TSO | - | 52 | 53 | 2020 | Summer | I, [%] | Expected | - | 9.585% | 5.787% | 8.005% | 5.142% | 4.912% | 4.11% | 7.972% | 19.23% | 20.4% | 20.54% | 22.23% | 22.89% | 22.13% | 23.95% | 22.7% | 18.91% | 19.21% | 18.99% | 19.66% | 19.97% | 20.35% | 24.94% | 27.06% | 19.19%
TSO | - | 53 | 54 | 2020 | Summer | I, [%] | Expected | - | 4.171% | 2.286% | 1.739% | 1.455% | 2.601% | 2.52% | 5.716% | 11.41% | 15.7% | 17.87% | 16.12% | 22.18% | 20.92% | 20.49% | 19.68% | 17.27% | 15.75% | 16.03% | 14.65% | 13.53% | 14.91% | 18.26% | 18.61% | 13.5%
TSO | - | 54 | 55 | 2020 | Summer | I, [%] | Expected | - | 5.558% | 3.69% | 4.438% | 2.842% | 4.08% | 2.409% | 6.232% | 12.66% | 17.07% | 19.29% | 17.45% | 23.53% | 22.27% | 21.82% | 20.84% | 18.38% | 17.02% | 17.4% | 15.19% | 14.24% | 15.43% | 18.84% | 19.29% | 14.1%
TSO | - | 11 | 43 | 2020 | Summer | I, [%] | Expected | - | 18.63% | 18.5% | 17.12% | 15.11% | 15.39% | 17.52% | 20.17% | 21.94% | 21.77% | 18.7% | 17.91% | 20.74% | 21.17% | 22% | 23% | 21.91% | 20.53% | 20.62% | 21.35% | 22.24% | 22.61% | 23.09% | 19.01% | 16.92%
TSO | - | 44 | 45 | 2020 | Summer | I, [%] | Expected | - | 36.35% | 38.41% | 35.66% | 31.26% | 32.91% | 30.9% | 34.29% | 34.85% | 38.96% | 45.27% | 44.96% | 43.25% | 44.49% | 54.4% | 52.99% | 50.91% | 51.76% | 51.62% | 40.87% | 42% | 43.93% | 48.67% | 47.36% | 40.8%
TSO | - | 40 | 56 | 2020 | Summer | I, [%] | Expected | - | 25.41% | 19.77% | 22.76% | 21.66% | 23.53% | 26.97% | 27.96% | 28.6% | 33.54% | 29.76% | 29.49% | 29.94% | 28.59% | 26.97% | 22.8% | 22.52% | 23.51% | 23.91% | 25.02% | 27.07% | 23.9% | 26.5% | 22.27% | 17.98%
TSO | - | 56 | 41 | 2020 | Summer | I, [%] | Expected | - | 40.1% | 41.8% | 33.01% | 34.02% | 32.1% | 33.4% | 40.94% | 45.67% | 47.84% | 51.79% | 50.24% | 52.97% | 53.88% | 54.69% | 51.92% | 50.33% | 48.54% | 48.69% | 49.87% | 54.24% | 53.17% | 54.97% | 53.98% | 43.27%
TSO | - | 56 | 42 | 2020 | Summer | I, [%] | Expected | - | 15.2% | 19.37% | 13.47% | 11.78% | 9.352% | 9.515% | 11.78% | 14.35% | 11.64% | 14.34% | 15.45% | 13.84% | 15.74% | 16.68% | 19.62% | 20.14% | 17.63% | 18.36% | 20.63% | 21.72% | 21.02% | 19.78% | 22.06% | 16.15%
TSO | - | 39 | 57 | 2020 | Summer | I, [%] | Expected | - | 27.39% | 21.87% | 23.79% | 23.08% | 24.46% | 28.55% | 31.12% | 32.18% | 37.19% | 34.54% | 34.37% | 35.75% | 35.92% | 34.22% | 30.8% | 29.73% | 29.15% | 29.48% | 30.69% | 32.67% | 30.22% | 32.61% | 28.52% | 22.9%
TSO | - | 57 | 56 | 2020 | Summer | I, [%] | Expected | - | 10.52% | 10.49% | 5.902% | 7.823% | 7.248% | 12% | 16.34% | 17.95% | 19.65% | 23.95% | 25.95% | 29.54% | 34.51% | 34.48% | 35.67% | 33.2% | 28.99% | 28.42% | 25.53% | 25.71% | 28.11% | 28.32% | 27.92% | 20.91%
TSO | - | 38 | 49 | 2020 | Summer | I, [%] | Expected | - | 5.638% | 6.419% | 4.74% | 5.446% | 4.784% | 5.095% | 7.693% | 3.753% | 2.615% | 5.148% | 3.951% | 8.185% | 10.75% | 11.58% | 13.04% | 12.85% | 12.18% | 11.53% | 9.089% | 7.733% | 9.739% | 11.54% | 8.887% | 7.499%
TSO | - | 38 | 48 | 2020 | Summer | I, [%] | Expected | - | 26.52% | 29.32% | 29.18% | 29.01% | 25.65% | 29.38% | 30.62% | 28.02% | 31.14% | 26.47% | 24.32% | 28.53% | 23.9% | 22.33% | 23.45% | 22.81% | 25.06% | 25.57% | 24.88% | 20.83% | 17.81% | 18.11% | 12.41% | 2.564%
TSO | - | 9 | 55 | 2020 | Summer | I, [%] | Expected | - | 14.99% | 14.56% | 14.92% | 14.24% | 10.94% | 8.223% | 12.86% | 16.52% | 20.08% | 21.43% | 20.12% | 24.79% | 23.56% | 22.72% | 22.55% | 21.77% | 22.13% | 23.12% | 21.33% | 20.71% | 20.54% | 22.16% | 24.14% | 19.65%
DSO | 2 | 1 | 2 | 2020 | Summer | I, [%] | 0 | 0 | 0.0516% | 0.04579% | 0.04019% | 0.04017% | 0.04073% | 0.04108% | 0.05519% | 0.07207% | 0.07587% | 0.06375% | 0.05051% | 0.05394% | 0.05471% | 0.05204% | 0.05455% | 0.05848% | 0.06472% | 0.07248% | 0.07046% | 0.07329% | 0.08047% | 0.08073% | 0.07043% | 0.05821%
DSO | 2 | 2 | 3 | 2020 | Summer | I, [%] | 0 | 0 | 0.05058% | 0.04527% | 0.04019% | 0.03989% | 0.04061% | 0.04083% | 0.05496% | 0.0713% | 0.07676% | 0.06481% | 0.05151% | 0.0543% | 0.05529% | 0.05251% | 0.05575% | 0.05986% | 0.06686% | 0.0752% | 0.07296% | 0.07653% | 0.08251% | 0.08038% | 0.06888% | 0.05733%
DSO | 2 | 3 | 4 | 2020 | Summer | I, [%] | 0 | 0 | 0.04645% | 0.0414% | 0.03706% | 0.0363% | 0.03695% | 0.03725% | 0.05091% | 0.06692% | 0.07225% | 0.06065% | 0.04772% | 0.05033% | 0.05137% | 0.04867% | 0.05154% | 0.05539% | 0.06238% | 0.07125% | 0.06806% | 0.07159% | 0.07805% | 0.07569% | 0.06439% | 0.05336%
DSO | 2 | 4 | 5 | 2020 | Summer | I, [%] | 0 | 0 | 0.03668% | 0.03234% | 0.03059% | 0.0301% | 0.03076% | 0.03107% | 0.04282% | 0.05327% | 0.0563% | 0.04649% | 0.03571% | 0.03886% | 0.03973% | 0.03743% | 0.03861% | 0.04178% | 0.04735% | 0.05387% | 0.05058% | 0.05434% | 0.06082% | 0.05855% | 0.04875% | 0.03923%
DSO | 2 | 5 | 6 | 2020 | Summer | I, [%] | 0 | 0 | 0.01507% | 0.01345% | 0.01324% | 0.01317% | 0.01335% | 0.01326% | 0.0142% | 0.01847% | 0.01796% | 0.01189% | 0.01499% | 0.01975% | 0.01834% | 0.01968% | 0.01269% | 0.01061% | 0.01287% | 0.01926% | 0.01939% | 0.02095% | 0.02461% | 0.02539% | 0.02203% | 0.0168%
DSO | 2 | 6 | 7 | 2020 | Summer | I, [%] | 0 | 0 | 0.01089% | 0.009601% | 0.009215% | 0.009321% | 0.009259% | 0.009421% | 0.01037% | 0.01205% | 0.01114% | 0.007564% | 0.00994% | 0.01298% | 0.01207% | 0.01287% | 0.008376% | 0.006689% | 0.007848% | 0.01208% | 0.01249% | 0.01313% | 0.01497% | 0.01528% | 0.01379% | 0.01154%
DSO | 2 | 7 | 8 | 2020 | Summer | I, [%] | 0 | 0 | 0.009537% | 0.008487% | 0.008102% | 0.008207% | 0.008144% | 0.008308% | 0.008969% | 0.009797% | 0.008598% | 0.006727% | 0.0104% | 0.01399% | 0.01293% | 0.01395% | 0.008781% | 0.006192% | 0.006198% | 0.01022% | 0.01063% | 0.01086% | 0.01246% | 0.01278% | 0.01173% | 0.009702%
DSO | 2 | 2 | 9 | 2020 | Summer | I, [%] | 0 | 0 | 0.002612% | 0.002451% | 0.002416% | 0.002437% | 0.002351% | 0.002311% | 0.003204% | 0.002549% | 0.003097% | 0.003434% | 0.003305% | 0.00253% | 0.002815% | 0.002829% | 0.003273% | 0.003583% | 0.00437% | 0.004664% | 0.004919% | 0.005699% | 0.004204% | 0.00215% | 0.002132% | 0.002076%
DSO | 2 | 1 | 20 | 2020 | Summer | I, [%] | 0 | 0 | 0.02935% | 0.02886% | 0.02475% | 0.02661% | 0.02534% | 0.0258% | 0.02898% | 0.03341% | 0.02614% | 0.01025% | 0.03047% | 0.04239% | 0.03519% | 0.04142% | 0.02354% | 0.008495% | 0.01404% | 0.03505% | 0.03605% | 0.0377% | 0.0399% | 0.03867% | 0.03499% | 0.03249%
DSO | 2 | 20 | 21 | 2020 | Summer | I, [%] | 0 | 0 | 0.02257% | 0.02245% | 0.01859% | 0.02109% | 0.01931% | 0.01882% | 0.0221% | 0.02631% | 0.01831% | 0.01992% | 0.04127% | 0.05365% | 0.0466% | 0.05162% | 0.03292% | 0.01802% | 0.007609% | 0.02728% | 0.02828% | 0.03056% | 0.03159% | 0.02955% | 0.0264% | 0.0253%
DSO | 2 | 21 | 22 | 2020 | Summer | I, [%] | 0 | 0 | 0.001348% | 0.001229% | 0.001171% | 0.001176% | 0.001192% | 0.001144% | 0.00135% | 0.001782% | 0.001645% | 0.009833% | 0.0151% | 0.01858% | 0.01704% | 0.01809% | 0.01266% | 0.009022% | 0.00417% | 0.001587% | 0.001865% | 0.001824% | 0.001809% | 0.001812% | 0.001712% | 0.00152%
DSO | 2 | 21 | 23 | 2020 | Summer | I, [%] | 0 | 0 | 0.01898% | 0.01939% | 0.01566% | 0.01816% | 0.01643% | 0.01621% | 0.01873% | 0.02197% | 0.01611% | 0.01239% | 0.02877% | 0.03797% | 0.03245% | 0.03642% | 0.02288% | 0.01126% | 0.007303% | 0.02272% | 0.0233% | 0.02538% | 0.02632% | 0.02426% | 0.0216% | 0.02117%
DSO | 2 | 23 | 24 | 2020 | Summer | I, [%] | 0 | 0 | 0.005033% | 0.004874% | 0.004502% | 0.004615% | 0.004603% | 0.004595% | 0.004765% | 0.005618% | 0.00373% | 0.00756% | 0.01261% | 0.01604% | 0.01435% | 0.01554% | 0.01065% | 0.007039% | 0.003126% | 0.005175% | 0.005664% | 0.005605% | 0.005418% | 0.005448% | 0.005084% | 0.004802%
DSO | 2 | 23 | 25 | 2020 | Summer | I, [%] | 0 | 0 | 17.8% | 18.49% | 16.13% | 14.57% | 15.04% | 19.26% | 19.47% | 23.28% | 14.79% | 26.15% | 47.18% | 59.31% | 52.64% | 57.8% | 41.18% | 26.88% | 11.2% | 22.1% | 23.87% | 23.38% | 24.5% | 22.81% | 20.74% | 20.23%
DSO | 2 | 25 | 26 | 2020 | Summer | I, [%] | 0 | 0 | 0.001223% | 0.001134% | 0.001623% | 0.001082% | 0.001057% | 0.001072% | 0.001592% | 0.002141% | 0.004395% | 0.02197% | 0.03265% | 0.03979% | 0.03672% | 0.03896% | 0.02803% | 0.02059% | 0.01037% | 0.0009797% | 0.001707% | 0.00182% | 0.001914% | 0.001768% | 0.001547% | 0.00134%
DSO | 2 | 50 | 1 | 2020 | Summer | I, [%] | 0 | 0 | 0.1216% | 0.1197% | 0.1185% | 0.1178% | 0.1188% | 0.1203% | 0.1251% | 0.1306% | 0.1275% | 0.1145% | 0.1207% | 0.1245% | 0.1214% | 0.1248% | 0.1168% | 0.116% | 0.1194% | 0.1298% | 0.1295% | 0.1277% | 0.1308% | 0.1319% | 0.1286% | 0.1244%
DSO | 2 | 50 | 51 | 2020 | Summer | I, [%] | 0 | 0 | 0.1726% | 0.1773% | 0.1857% | 0.1806% | 0.1845% | 0.1903% | 0.1799% | 0.1636% | 0.1583% | 0.1655% | 0.1879% | 0.1866% | 0.1822% | 0.1878% | 0.1823% | 0.1756% | 0.1656% | 0.1589% | 0.1593% | 0.1485% | 0.1439% | 0.1476% | 0.158% | 0.1671%
DSO | 2 | 1 | 2 | 2020 | Summer | I, [%] | Expected | - | 0.0516% | 0.04579% | 0.04019% | 0.04017% | 0.04073% | 0.04108% | 0.05519% | 0.07207% | 0.07587% | 0.06375% | 0.05051% | 0.05394% | 0.05471% | 0.05204% | 0.05455% | 0.05848% | 0.06472% | 0.07248% | 0.07046% | 0.07329% | 0.08047% | 0.08073% | 0.07043% | 0.05821%
DSO | 2 | 2 | 3 | 2020 | Summer | I, [%] | Expected | - | 0.05058% | 0.04527% | 0.04019% | 0.03989% | 0.04061% | 0.04083% | 0.05496% | 0.0713% | 0.07676% | 0.06481% | 0.05151% | 0.0543% | 0.05529% | 0.05251% | 0.05575% | 0.05986% | 0.06686% | 0.0752% | 0.07296% | 0.07653% | 0.08251% | 0.08038% | 0.06888% | 0.05733%
DSO | 2 | 3 | 4 | 2020 | Summer | I, [%] | Expected | - | 0.04645% | 0.0414% | 0.03706% | 0.0363% | 0.03695% | 0.03725% | 0.05091% | 0.06692% | 0.07225% | 0.06065% | 0.04772% | 0.05033% | 0.05137% | 0.04867% | 0.05154% | 0.05539% | 0.06238% | 0.07125% | 0.06806% | 0.07159% | 0.07805% | 0.07569% | 0.06439% | 0.05336%
DSO | 2 | 4 | 5 | 2020 | Summer | I, [%] | Expected | - | 0.03668% | 0.03234% | 0.03059% | 0.0301% | 0.03076% | 0.03107% | 0.04282% | 0.05327% | 0.0563% | 0.04649% | 0.03571% | 0.03886% | 0.03973% | 0.03743% | 0.03861% | 0.04178% | 0.04735% | 0.05387% | 0.05058% | 0.05434% | 0.06082% | 0.05855% | 0.04875% | 0.03923%
DSO | 2 | 5 | 6 | 2020 | Summer | I, [%] | Expected | - | 0.01507% | 0.01345% | 0.01324% | 0.01317% | 0.01335% | 0.01326% | 0.0142% | 0.01847% | 0.01796% | 0.01189% | 0.01499% | 0.01975% | 0.01834% | 0.01968% | 0.01269% | 0.01061% | 0.01287% | 0.01926% | 0.01939% | 0.02095% | 0.02461% | 0.02539% | 0.02203% | 0.0168%
DSO | 2 | 6 | 7 | 2020 | Summer | I, [%] | Expected | - | 0.01089% | 0.009601% | 0.009215% | 0.009321% | 0.009259% | 0.009421% | 0.01037% | 0.01205% | 0.01114% | 0.007564% | 0.00994% | 0.01298% | 0.01207% | 0.01287% | 0.008376% | 0.006689% | 0.007848% | 0.01208% | 0.01249% | 0.01313% | 0.01497% | 0.01528% | 0.01379% | 0.01154%
DSO | 2 | 7 | 8 | 2020 | Summer | I, [%] | Expected | - | 0.009537% | 0.008487% | 0.008102% | 0.008207% | 0.008144% | 0.008308% | 0.008969% | 0.009797% | 0.008598% | 0.006727% | 0.0104% | 0.01399% | 0.01293% | 0.01395% | 0.008781% | 0.006192% | 0.006198% | 0.01022% | 0.01063% | 0.01086% | 0.01246% | 0.01278% | 0.01173% | 0.009702%
DSO | 2 | 2 | 9 | 2020 | Summer | I, [%] | Expected | - | 0.002612% | 0.002451% | 0.002416% | 0.002437% | 0.002351% | 0.002311% | 0.003204% | 0.002549% | 0.003097% | 0.003434% | 0.003305% | 0.00253% | 0.002815% | 0.002829% | 0.003273% | 0.003583% | 0.00437% | 0.004664% | 0.004919% | 0.005699% | 0.004204% | 0.00215% | 0.002132% | 0.002076%
DSO | 2 | 1 | 20 | 2020 | Summer | I, [%] | Expected | - | 0.02935% | 0.02886% | 0.02475% | 0.02661% | 0.02534% | 0.0258% | 0.02898% | 0.03341% | 0.02614% | 0.01025% | 0.03047% | 0.04239% | 0.03519% | 0.04142% | 0.02354% | 0.008495% | 0.01404% | 0.03505% | 0.03605% | 0.0377% | 0.0399% | 0.03867% | 0.03499% | 0.03249%
DSO | 2 | 20 | 21 | 2020 | Summer | I, [%] | Expected | - | 0.02257% | 0.02245% | 0.01859% | 0.02109% | 0.01931% | 0.01882% | 0.0221% | 0.02631% | 0.01831% | 0.01992% | 0.04127% | 0.05365% | 0.0466% | 0.05162% | 0.03292% | 0.01802% | 0.007609% | 0.02728% | 0.02828% | 0.03056% | 0.03159% | 0.02955% | 0.0264% | 0.0253%
DSO | 2 | 21 | 22 | 2020 | Summer | I, [%] | Expected | - | 0.001348% | 0.001229% | 0.001171% | 0.001176% | 0.001192% | 0.001144% | 0.00135% | 0.001782% | 0.001645% | 0.009833% | 0.0151% | 0.01858% | 0.01704% | 0.01809% | 0.01266% | 0.009022% | 0.00417% | 0.001587% | 0.001865% | 0.001824% | 0.001809% | 0.001812% | 0.001712% | 0.00152%
DSO | 2 | 21 | 23 | 2020 | Summer | I, [%] | Expected | - | 0.01898% | 0.01939% | 0.01566% | 0.01816% | 0.01643% | 0.01621% | 0.01873% | 0.02197% | 0.01611% | 0.01239% | 0.02877% | 0.03797% | 0.03245% | 0.03642% | 0.02288% | 0.01126% | 0.007303% | 0.02272% | 0.0233% | 0.02538% | 0.02632% | 0.02426% | 0.0216% | 0.02117%
DSO | 2 | 23 | 24 | 2020 | Summer | I, [%] | Expected | - | 0.005033% | 0.004874% | 0.004502% | 0.004615% | 0.004603% | 0.004595% | 0.004765% | 0.005618% | 0.00373% | 0.00756% | 0.01261% | 0.01604% | 0.01435% | 0.01554% | 0.01065% | 0.007039% | 0.003126% | 0.005175% | 0.005664% | 0.005605% | 0.005418% | 0.005448% | 0.005084% | 0.004802%
DSO | 2 | 23 | 25 | 2020 | Summer | I, [%] | Expected | - | 17.8% | 18.49% | 16.13% | 14.57% | 15.04% | 19.26% | 19.47% | 23.28% | 14.79% | 26.15% | 47.18% | 59.31% | 52.64% | 57.8% | 41.18% | 26.88% | 11.2% | 22.1% | 23.87% | 23.38% | 24.5% | 22.81% | 20.74% | 20.23%
DSO | 2 | 25 | 26 | 2020 | Summer | I, [%] | Expected | - | 0.001223% | 0.001134% | 0.001623% | 0.001082% | 0.001057% | 0.001072% | 0.001592% | 0.002141% | 0.004395% | 0.02197% | 0.03265% | 0.03979% | 0.03672% | 0.03896% | 0.02803% | 0.02059% | 0.01037% | 0.0009797% | 0.001707% | 0.00182% | 0.001914% | 0.001768% | 0.001547% | 0.00134%
DSO | 2 | 50 | 1 | 2020 | Summer | I, [%] | Expected | - | 0.1216% | 0.1197% | 0.1185% | 0.1178% | 0.1188% | 0.1203% | 0.1251% | 0.1306% | 0.1275% | 0.1145% | 0.1207% | 0.1245% | 0.1214% | 0.1248% | 0.1168% | 0.116% | 0.1194% | 0.1298% | 0.1295% | 0.1277% | 0.1308% | 0.1319% | 0.1286% | 0.1244%
DSO | 2 | 50 | 51 | 2020 | Summer | I, [%] | Expected | - | 0.1726% | 0.1773% | 0.1857% | 0.1806% | 0.1845% | 0.1903% | 0.1799% | 0.1636% | 0.1583% | 0.1655% | 0.1879% | 0.1866% | 0.1822% | 0.1878% | 0.1823% | 0.1756% | 0.1656% | 0.1589% | 0.1593% | 0.1485% | 0.1439% | 0.1476% | 0.158% | 0.1671%